## Hierarchy
Sr.No. | Plant | Section | Location | Main Equipment | Sub Equipment | Department | History card Tag Nos. | History card Location
26 | SUGAR | MILL HOUSE | MILL DCS CONTROL ROOM | MILL UPS | MILL UPS 1 | INSTRUMENT | ZIL/GSM/UPS-1-MILL | UPS FOR SUGAR PLANT MILL HOUSE
483 | SUGAR | REFINERY HOUSE | RAW HOUSE DCS CONTROL MAIN ROOM | RAW HOUSE UPS | RAW HOUSE UPS 1 | INSTRUMENT | ZIL/GSM/UPS-1-RAW | UPS FOR SUGAR PLANT RAW HOUSE
494 | SUGAR | REFINERY HOUSE | REFINERY HOUSE DCS CONTROL ROOM | REFINERY HOUSE UPS | REFINERY HOUSE UPS 1 | INSTRUMENT | ZIL/GSM/UPS-1-REFINERY | UPS FOR SUGAR PLANT REFINERY HOUSE
27 | SUGAR | MILL HOUSE | MILL DCS CONTROL ROOM | MILL UPS | MILL UPS 2 | INSTRUMENT | ZIL/GSM/UPS-2-MILL | UPS FOR SUGAR PLANT MILL HOUSE
484 | SUGAR | REFINERY HOUSE | RAW HOUSE DCS CONTROL MAIN ROOM | RAW HOUSE UPS | RAW HOUSE UPS 2 | INSTRUMENT | ZIL/GSM/UPS-2-RAW | UPS FOR SUGAR PLANT RAW HOUSE
495 | SUGAR | REFINERY HOUSE | REFINERY HOUSE DCS CONTROL ROOM | REFINERY HOUSE UPS | REFINERY HOUSE UPS 2 | INSTRUMENT | ZIL/GSM/UPS-2-REFINERY | UPS FOR SUGAR PLANT REFINERY HOUSE
3099 | SUGAR | REFINERY HOUSE | RAW PAN BOILING | RAW PAN | RAW PAN N.2 & CONDENSER FLD INST | INSTRUMENT | ZIL/SUG./001 (022 XV 023B01) | Cooling condenser Main valve RAW. Pan.no.2 (Refinery)
3106 | SUGAR | REFINERY HOUSE | RAW PAN BOILING | RAW PAN | RAW PAN N.3 & CONDENSER FLD INST | INSTRUMENT | ZIL/SUG./001 (022XV020B01) | Cooling condenser Spray valve Raw. Pan.no.3
3106 | SUGAR | REFINERY HOUSE | RAW PAN BOILING | RAW PAN | RAW PAN N.3 & CONDENSER FLD INST | INSTRUMENT | ZIL/SUG./001 (022XV020B02) | Cooling condenser Spray valve Raw. Pan.no.3
3106 | SUGAR | REFINERY HOUSE | RAW PAN BOILING | RAW PAN | RAW PAN N.3 & CONDENSER FLD INST | INSTRUMENT | ZIL/SUG./001 (022XV020B03) | Cooling condenser Spray valve Raw. Pan.no.3
3106 | SUGAR | REFINERY HOUSE | RAW PAN BOILING | RAW PAN | RAW PAN N.3 & CONDENSER FLD INST | INSTRUMENT | ZIL/SUG./001 (022XV020B05) | Cooling condenser Main valve Raw. Pan.no.3
3634 | SUGAR | REFINERY HOUSE | REFINED MASSECUITE BOILING | REFINERY PAN | REFINERY PAN 2 & PAN CONDENSER FLD INST | INSTRUMENT | ZIL/SUG./001 (17 BCV 020B01) | Refinary PAN No 2 Auto feed Valve
3629 | SUGAR | REFINERY HOUSE | REFINED MASSECUITE BOILING | REFINERY PAN | REFINERY PAN 1 & PAN CONDENSER FLD INST | INSTRUMENT | ZIL/SUG./001 (17 BCV.010B01) | Refinary PAN No 1 Auto feed Valve
3639 | SUGAR | REFINERY HOUSE | REFINED MASSECUITE BOILING | REFINERY PAN | REFINERY PAN 3 & PAN CONDENSER FLD INST | INSTRUMENT | ZIL/SUG./001 (17 BCV.030 B01) | Refinary PAN No 3 Auto feed Valve
1131 | SUGAR | REFINERY HOUSE | REFINED MASSECUITE BOILING | DEEP BED FILTER | DEEP BED FILTER FLD INST | INSTRUMENT | ZIL/SUG./001 (40FCV201) | DBF 2 Flow control valve ( MCS Refinery)
1241 | SUGAR | REFINERY HOUSE | MELT DECOLORISATION & BRS UNIT | BRS IIND STAGE | BRS IIND STAGE FLD INST | INSTRUMENT | ZIL/SUG./001 (FCV 201) | B.R.S Brine II Stage Control valve (Refinery)
3369 | SUGAR | REFINERY HOUSE | C MASSECUITE CURING | B/ C MASSECUITE COOLING & REHEATING SYS | B/C MASSECUITE COLD WATER CIRCPUMP2 INST | INSTRUMENT | ZIL/SUG./001 TWC_CMD | Cold water tank level control.
2621 | SUGAR | DS HOUSE | MASSECUITE CURING SECTION | B-HEAVY MOLASSES | WEIGHMENT SYRUP TRANS PUMP1 FLD INST | INSTRUMENT | ZIL/SUG./001/SY_B_MOL_CV2 | DS Syrup to weighing scale
330 | SUGAR | MILL HOUSE | MILLING | SECONDARY JUICE ROTARY SCREEN-2 | SECONDARY JUICE ROTARY SCREEN 2 FLD INST | INSTRUMENT | ZIL/SUG./006 (XV_RJ2_SOV2) | Rotary screen Valve 02(A)
330 | SUGAR | MILL HOUSE | MILLING | SECONDARY JUICE ROTARY SCREEN-2 | SECONDARY JUICE ROTARY SCREEN 2 FLD INST | INSTRUMENT | ZIL/SUG./007 (XV_RJ2_SOV2) | Rotary screen Valve 02(B)
330 | SUGAR | MILL HOUSE | MILLING | SECONDARY JUICE ROTARY SCREEN-2 | SECONDARY JUICE ROTARY SCREEN 2 FLD INST | INSTRUMENT | ZIL/SUG./008 (XV_RJ2_SOV3) | Rotary screen Valve 03(A)
330 | SUGAR | MILL HOUSE | MILLING | SECONDARY JUICE ROTARY SCREEN-2 | SECONDARY JUICE ROTARY SCREEN 2 FLD INST | INSTRUMENT | ZIL/SUG./009 (XV_RJ2_SOV3) | Rotary screen Valve 03(B)
1266 | SUGAR | REFINERY HOUSE | MELT CONCENTRATION UNIT | MELT CONCENTRATOR | MELT CONCENTRATOR BODY FLD INST | INSTRUMENT | ZIL/SUG./01/16.FT.075.B01 | Raw Quad Meltconcentrator O/L
751 | SUGAR | REFINERY HOUSE | RAW PAN BOILING | RAW PAN | RAW PAN N.1 & CONDENSER FLD INST | INSTRUMENT | ZIL/SUG./01/22FT220B01 | Raw Pan Hot Water Line
3629 | SUGAR | REFINERY HOUSE | REFINED MASSECUITE BOILING | REFINERY PAN | REFINERY PAN 1 & PAN CONDENSER FLD INST | INSTRUMENT | ZIL/SUG./01/22FT230B01 | Refinery Pan Hot water flow
4532 | SUGAR | 36-BLOCK | TUBEWELL | TUBEWELL NO-3 36 BLOCK | TUBEWELL NO-3 36 BLOCK FLD INST | INSTRUMENT | ZIL/SUG./01/36-BLOCK-TWL | 36 Block Tube-well
4532 | SUGAR | DS HOUSE | TUBEWELL | TUBEWELL NO-4 DISTERLY | TUBEWELL NO-4 DISTERLY WATER LINE FLD INST | INSTRUMENT | ZIL/SUG./01/DIST.-TWFM-2 | Distillery Tubewell Water line
1603 | SUGAR | DS HOUSE | JUICE HEATING & CLARIFICATION | RAW JUICE HEATER | EXHAUST COND. PUMP FLD INST | INSTRUMENT | ZIL/SUG./01/DS/FT-201 | Exhaust Condensate Flow
1905 | SUGAR | DS HOUSE | EVAPORATION SYSTEM | IST / 2ND EFFECT EVAPORATOR | VAPOUR CELL-2500 M2 FLD INST | INSTRUMENT | ZIL/SUG./01/DS/FT-203 | I/II2500 Robert body
1896 | SUGAR | DS HOUSE | EVAPORATION SYSTEM | IST EFFECT EVAPORATOR | SEMI KESTNER-2500 M2 FLD INST | INSTRUMENT | ZIL/SUG./01/DS_EX_FLOW | DS Exhaust Flow
4016 | SUGAR | ETP | ETP-INSTRUMENT | Instrument Panel & HMI | Instrument Panel , HMI & Fld Inst. | INSTRUMENT | ZIL/SUG./01/ETP-DECANTER-FM | ETP Dicanter Flow meter
1215 | SUGAR | REFINERY HOUSE | MELT DECOLORISATION & BRS UNIT | BRS IST STAGE | BRS IST STAGE FLD INST | INSTRUMENT | ZIL/SUG./01/FT-201 | Refinery BRS 1st Stage Permit Tank
1215 | SUGAR | REFINERY HOUSE | MELT DECOLORISATION & BRS UNIT | BRS IST STAGE | BRS IST STAGE FLD INST | INSTRUMENT | ZIL/SUG./01/FT-203 | Refinery BRS 1st Stage Recycle
574 | SUGAR | REFINERY HOUSE | JUICE HEATING AND CLARIFICATION | ROTARY VACCUM FILTER FOR MUDDY JUICE | FILTRATE TRANS PUMP 1 FLD INST | INSTRUMENT | ZIL/SUG./01/FT-FILTRATE | Filtrate Flow (muddy Juice)
2605 | SUGAR | DS HOUSE | MASSECUITE CURING SECTION | FINAL MOLASSES | FINAL MOLASSES RUN OFF TANK | INSTRUMENT | ZIL/SUG./01/FT-FINAL | Final Molasses O/L Flow
1116 | SUGAR | REFINERY HOUSE | RAW MELT CLARIFICATION SYSTEM | SCUM HOLDING TANK | SCUM TRANS PUMP2 FLD INST | INSTRUMENT | ZIL/SUG./01/FT-SCUM-DE-SWEET | Scum D-scutning (hot Water)
729 | SUGAR | REFINERY HOUSE | SYRUP CLARIFICATION SYSTEM | TREATED SYRUP | TREATED SYRUP PUMP1 FLD INST | INSTRUMENT | ZIL/SUG./01/FT-SYRUP | Syrup Feed Pump Discharge Flow
697 | SUGAR | REFINERY HOUSE | SYRUP CLARIFICATION SYSTEM | SYRUP CLARIFIER | SYRUP REACTION TANK FLD INST | INSTRUMENT | ZIL/SUG./01/SCUM-FM | SCS Scum to DS
1824 | SUGAR | DS HOUSE | JUICE HEATING & CLARIFICATION | ROTARY VACCUM FILTER | VACUUM PUMP1 FLD INST | INSTRUMENT | ZIL/SUG./01/Vacuum-FM-01 | Water flow vacuum filter
174 | SUGAR | MILL HOUSE | CANE PREPRATORY-CAP | SHREDDER | SHREDDER FIELD INST 1 | INSTRUMENT | ZIL/SUG./016 (VIB103,VIB104,VIB105) | Shreder RHS Side
543 | SUGAR | REFINERY HOUSE | JUICE HEATING AND CLARIFICATION | SHORT RETENTION CALRIFIER | SRT FLD INST | INSTRUMENT | ZIL/SUG./016/01/D_SWEET | D Sweetnnig Water Line
141 | SUGAR | MILL HOUSE | CANE HANDLING-CAH | MAIN CANE CARRIER | MAIN CANE CARRIER FLD INST | INSTRUMENT | ZIL/SUG./017 ( PI_502) | Main Cane Carrier
3105 | SUGAR | REFINERY HOUSE | RAW PAN BOILING | RAW PAN | RAW PAN 3 AUTO FEED CONTROL INSTRUMENT | INSTRUMENT | ZIL/SUG./028 (11.BCV.030.B01) | RAW PAN No 03 Auto feed Valve
866 | SUGAR | REFINERY HOUSE | B MASSECUITE PAN BOILING | B CONTINUES PAN | B CONTINUES PAN AUTO FEED CONTROL INST | INSTRUMENT | ZIL/SUG./B.COMP-CT-05 | B Conti.Compartment No 05
866 | SUGAR | REFINERY HOUSE | B MASSECUITE PAN BOILING | B CONTINUES PAN | B CONTINUES PAN AUTO FEED CONTROL INST | INSTRUMENT | ZIL/SUG./B.COMP-CT-06 | B Conti.Compartment No 06
3954 | SUGAR | DS HOUSE | JUICE HEATING & CLARIFICATION | Mud Removal system | MUD REMOVAL SYSTEM FLD INST | INSTRUMENT | ZIL/SUG./DECANTER-2/CV-1 | Decanter-2 Mud I/L Valve
4020 | SUGAR | POWER HOUSE | STEAM TG SET | OLD POWER STEAM TURBINE GENERATOR SET | OLD POWER STEAM TURBINE | MECHANICAL | ZIL/SUG/01 | 3 MW OLD POWER TURBINE
4035 | SUGAR | POWER HOUSE | STEAM TG SET | NEW POWER STEAM TURBINE (NEW-STG) | NEW POWER STEAM TURBINE | MECHANICAL | ZIL/SUG/02 | 3 MW NEW POWER TURBINE
226 | SUGAR | MILL HOUSE | MILLING | MILL NO 1 | MILL NO 1 STEAM TURBINE | MECHANICAL | ZIL/SUG/03 | Mill Turbine -01
244 | SUGAR | MILL HOUSE | MILLING | MILL NO 2 | MILL NO 2 STEAM TURBINE | MECHANICAL | ZIL/SUG/04 | Mill Turbine -02
262 | SUGAR | MILL HOUSE | MILLING | MILL NO 3 | MILL NO 3 STEAM TURBINE | MECHANICAL | ZIL/SUG/05 | Mill Turbine -03

## Sheet Map
source file | sheet name | id | EQUIPMENT TAG NO | Sub Equipment
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | TURBINE :: POWER TURBINE | ee2949ed1129 | ZIL/SUG/01 | OLD POWER STEAM TURBINE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | TURBINE :: POWER TURBINE | 4a14e1694ed7 | ZIL/SUG/02 | NEW POWER STEAM TURBINE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | TURBINE :: Mill turbine-01 | e686217c3a8a | ZIL/SUG/03 | MILL NO 1 STEAM TURBINE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | TURBINE :: Mill turbine-02 | 5794dba376d9 | ZIL/SUG/04 | MILL NO 2 STEAM TURBINE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | TURBINE :: Mill turbine-03 | 543ec787bb43 | ZIL/SUG/05 | MILL NO 3 STEAM TURBINE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Mill-16 :: Control valve | 0338168a0c42 | ZIL/SUG./006 (XV_RJ2_SOV2) | SECONDARY JUICE ROTARY SCREEN 2 FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Mill-16 :: Control valve | 333534806482 | ZIL/SUG./007 (XV_RJ2_SOV2) | SECONDARY JUICE ROTARY SCREEN 2 FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Mill-16 :: Control valve | a73aa53887f2 | ZIL/SUG./008 (XV_RJ2_SOV3) | SECONDARY JUICE ROTARY SCREEN 2 FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Mill-16 :: Control valve | 819ff4051ef6 | ZIL/SUG./009 (XV_RJ2_SOV3) | SECONDARY JUICE ROTARY SCREEN 2 FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Mill-16 :: Shreder -2 | 7bb58a2ff37f | ZIL/SUG./016 (VIB103,VIB104,VIB105) | SHREDDER FIELD INST 1
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Mill-16 :: Cane Carrier Pressure transmitter | c8c7f86779b1 | ZIL/SUG./017 ( PI_502) | MAIN CANE CARRIER FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | RJH-21-27 :: Control valve | 323dbc8cf2bf | ZIL/SUG./016/01/D_SWEET | SRT FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | B COUNTI.PAN 27-65 :: Control valve | 24c2390b4b9d | ZIL/SUG./B.COMP-CT-05 | B CONTINUES PAN AUTO FEED CONTROL INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | B COUNTI.PAN 27-65 :: Control valve | 7960222b9717 | ZIL/SUG./B.COMP-CT-06 | B CONTINUES PAN AUTO FEED CONTROL INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | RAW FEED VALVE-33 :: Control valve | 3535ab959303 | ZIL/SUG./028 (11.BCV.030.B01) | RAW PAN 3 AUTO FEED CONTROL INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | FLOW METER :: Flow Meter | f8589e108b99 | ZIL/SUG./01/22FT220B01 | RAW PAN N.1 & CONDENSER FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | FLOW METER :: Flow meter | 4584773fa72a | ZIL/SUG./01/16.FT.075.B01 | MELT CONCENTRATOR BODY FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | FLOW METER :: Flow meter | 009b63c1200e | ZIL/SUG./01/36-BLOCK-TWL | TUBEWELL NO-3 36 BLOCK FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | FLOW METER :: Flow meter | 8df8daf03ecf | ZIL/SUG./01/SCUM-FM | SYRUP REACTION TANK FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | FLOW METER :: Flow meter | 4847377faae6 | ZIL/SUG./01/FT-FINAL | FINAL MOLASSES RUN OFF TANK
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | FLOW METER :: Flow meter | 257f64ce90fa | ZIL/SUG./01/FT-SYRUP | TREATED SYRUP PUMP1 FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | FLOW METER :: Flow meter | 1c07114f164e | ZIL/SUG./01/FT-FILTRATE | FILTRATE TRANS PUMP 1 FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | FLOW METER :: Flow meter | 24df327cc482 | ZIL/SUG./01/FT-SCUM-DE-SWEET | SCUM TRANS PUMP2 FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | VRL 24-53 :: Control valve | 03f504a9eecf | ZIL/SUG./001/SY_B_MOL_CV2 | WEIGHMENT SYRUP TRANS PUMP1 FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Weingh-54-65 :: Control valve | 8279d1c2b53d | ZIL/SUG./DECANTER-2/CV-1 | MUD REMOVAL SYSTEM FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | DS Flow Meter-31 :: Flow Meter | e6137a7f74de | ZIL/SUG./01/DS_EX_FLOW | SEMI KESTNER-2500 M2 FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | DS Flow Meter-31 :: Flow Meter | 34eaba65875f | ZIL/SUG./01/DS/FT-201 | EXHAUST COND. PUMP FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | DS Flow Meter-31 :: Flow Meter | 517a5ea87f25 | ZIL/SUG./01/DS/FT-203 | VAPOUR CELL-2500 M2 FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | DS Flow Meter-31 :: Flow Meter | 4e7972449bf4 | ZIL/SUG./01/Vacuum-FM-01 | VACUUM PUMP1 FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | DS Flow Meter-31 :: Flow Meter | 48c0393cc9b3 | ZIL/SUG./01/DIST.-TWFM-2 | TUBEWELL NO-4 DISTERLY WATER LINE FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | DS Flow Meter-31 :: Flow Meter | c3e9937b8485 | ZIL/SUG./01/ETP-DECANTER-FM | Instrument Panel , HMI & Fld Inst.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | D.B.F 14 :: Control valve | 7950b69d04a3 | ZIL/SUG./001 (40FCV201) | DEEP BED FILTER FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Ground floor 19 :: Control valve | a57da8dfe7d0 | ZIL/SUG./001 (FCV 201) | BRS IIND STAGE FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Ground floor 19 :: Control valve | 1e06c2215910 | ZIL/SUG./001 TWC_CMD | B/C MASSECUITE COLD WATER CIRCPUMP2 INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Pan Feed Valve 3 :: Control valve | 904dbc43d424 | ZIL/SUG./001 (17 BCV.030 B01) | REFINERY PAN 3 & PAN CONDENSER FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Pan Feed Valve 3 :: Control valve | 0dc553592aaf | ZIL/SUG./001 (17 BCV 020B01) | REFINERY PAN 2 & PAN CONDENSER FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Pan Feed Valve 3 :: Control valve | 9047c11458f6 | ZIL/SUG./001 (17 BCV.010B01) | REFINERY PAN 1 & PAN CONDENSER FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Ref. Condensor 57 :: Control valve | cb921432e0d1 | ZIL/SUG./001 (022 XV 023B01) | RAW PAN N.2 & CONDENSER FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Ref. Condensor 57 :: Control valve | 2ffb61c28344 | ZIL/SUG./001 (022XV020B05) | RAW PAN N.3 & CONDENSER FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Ref. Condensor 57 :: Control valve | 79b8f75b04d0 | ZIL/SUG./001 (022XV020B01) | RAW PAN N.3 & CONDENSER FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Ref. Condensor 57 :: Control valve | 03ffdf69e4f6 | ZIL/SUG./001 (022XV020B02) | RAW PAN N.3 & CONDENSER FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Ref. Condensor 57 :: Control valve | 98591a067f85 | ZIL/SUG./001 (022XV020B03) | RAW PAN N.3 & CONDENSER FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Ref Flow Meter h :: FLOW METER | 9886032b2344 | ZIL/SUG./01/22FT230B01 | REFINERY PAN 1 & PAN CONDENSER FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Ref Flow Meter h :: Flow Meter | 1b40caeb3a99 | ZIL/SUG./01/FT-201 | BRS IST STAGE FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | Ref Flow Meter h :: Flow Meter | b3fe6af92e53 | ZIL/SUG./01/FT-203 | BRS IST STAGE FLD INST
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | 823aa812ca08 | ZIL/GSM/UPS-1-RAW | RAW HOUSE UPS 1
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | a5d4824f484a | ZIL/GSM/UPS-2-RAW | RAW HOUSE UPS 2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | 2cd136de0dc0 | ZIL/GSM/UPS-1-REFINERY | REFINERY HOUSE UPS 1
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | 436cc6ac16a2 | ZIL/GSM/UPS-2-REFINERY | REFINERY HOUSE UPS 2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | eb7ce6a60f04 | ZIL/GSM/UPS-1-MILL | MILL UPS 1
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | a78b376fc91d | ZIL/GSM/UPS-2-MILL | MILL UPS 2

## EQUIPMENT LIFE HISTORY CARD
source file | sheet id | sheet name | EQUIPMENT TAG NO | NAME OF EQUIPMENT | LOCATION | DATE OF COMMISSIONING | Main Equipment | Sub Equipment | Department
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | POWER TURBINE | SUGAR PLANT-3 MW OLD POWER TURBINE | 1996-06-06 | OLD POWER STEAM TURBINE GENERATOR SET | OLD POWER STEAM TURBINE | MECHANICAL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | POWER TURBINE | SUGAR PLANT-3 MW NEW POWER TURBINE | 1996-06-06 | NEW POWER STEAM TURBINE (NEW-STG) | NEW POWER STEAM TURBINE | MECHANICAL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Mill turbine-01 | SUGAR PLANT-Mill turbine-01 | 1996-06-06 | MILL NO 1 | MILL NO 1 STEAM TURBINE | MECHANICAL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Mill turbine-02 | SUGAR PLANT-Mill turbine-02 | 1997-06-06 | MILL NO 2 | MILL NO 2 STEAM TURBINE | MECHANICAL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Mill turbine-03 | SUGAR PLANT-Mill turbine-03 | 1997-06-06 | MILL NO 3 | MILL NO 3 STEAM TURBINE | MECHANICAL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | Control valve | SUGAR UNIT - Rotary screen Valve 02(A) | 2015 | SECONDARY JUICE ROTARY SCREEN-2 | SECONDARY JUICE ROTARY SCREEN 2 FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | Control valve | SUGAR UNIT - Rotary screen Valve 02(B) | 2015 | SECONDARY JUICE ROTARY SCREEN-2 | SECONDARY JUICE ROTARY SCREEN 2 FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | Control valve | SUGAR UNIT - Rotary screen Valve 03(A) | 2015 | SECONDARY JUICE ROTARY SCREEN-2 | SECONDARY JUICE ROTARY SCREEN 2 FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | Control valve | SUGAR UNIT - Rotary screen Valve 03(B) | 2015 | SECONDARY JUICE ROTARY SCREEN-2 | SECONDARY JUICE ROTARY SCREEN 2 FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | Shreder -2 | SUGAR UNIT - Shreder RHS Side | 2015 | SHREDDER | SHREDDER FIELD INST 1 | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | Cane Carrier Pressure transmitter | SUGAR UNIT -Main Cane Carrier | 2025 | MAIN CANE CARRIER | MAIN CANE CARRIER FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | Control valve | SUGAR UNIT - D Sweetnnig Water Line | 2015 | SHORT RETENTION CALRIFIER | SRT FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | Control valve | SUGAR UNIT - B Conti.Compartment No 05 | 2015 | B CONTINUES PAN | B CONTINUES PAN AUTO FEED CONTROL INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | Control valve | SUGAR UNIT - B Conti.Compartment No 06 | 2015 | B CONTINUES PAN | B CONTINUES PAN AUTO FEED CONTROL INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | Control valve | SUGAR UNIT - RAW PAN No 03 Auto feed Valve | 2015 | RAW PAN | RAW PAN 3 AUTO FEED CONTROL INSTRUMENT | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | Flow Meter | SUGAR UNIT - Raw Pan Hot Water Line | 2016 | RAW PAN | RAW PAN N.1 & CONDENSER FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | Flow meter | SUGAR UNIT - Raw Quad Meltconcentrator O/L | 2016 | MELT CONCENTRATOR | MELT CONCENTRATOR BODY FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | Flow meter | SUGAR UNIT - 36 Block Tube-well | 2016 | TUBEWELL NO-3 36 BLOCK | TUBEWELL NO-3 36 BLOCK FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | Flow meter | SUGAR UNIT - SCS Scum to DS | 2016 | SYRUP CLARIFIER | SYRUP REACTION TANK FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | Flow meter | SUGAR UNIT - Final Molasses O/L Flow | 2016 | FINAL MOLASSES | FINAL MOLASSES RUN OFF TANK | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | Flow meter | SUGAR UNIT - Syrup Feed Pump Discharge Flow | 2016 | TREATED SYRUP | TREATED SYRUP PUMP1 FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | Flow meter | SUGAR UNIT - Filtrate Flow (muddy Juice) | 2016 | ROTARY VACCUM FILTER FOR MUDDY JUICE | FILTRATE TRANS PUMP 1 FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | Flow meter | SUGAR UNIT - Scum D-scutning (hot Water) | 2016 | SCUM HOLDING TANK | SCUM TRANS PUMP2 FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve | SUGAR UNIT -DS Syrup to weighing scale |  | B-HEAVY MOLASSES | WEIGHMENT SYRUP TRANS PUMP1 FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | Control valve | SUGAR UNIT - Decanter-02 Mud I/L Valve | 2025 | Mud Removal system | MUD REMOVAL SYSTEM FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | Flow Meter | SUGAR UNIT - DS Exhaust Flow | 2020 | IST EFFECT EVAPORATOR | SEMI KESTNER-2500 M2 FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | Flow Meter | SUGAR UNIT - Exhaust Condensate Flow | 2016 | RAW JUICE HEATER | EXHAUST COND. PUMP FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | Flow Meter | SUGAR UNIT - I/II2500 Robert body | 2016 | IST / 2ND EFFECT EVAPORATOR | VAPOUR CELL-2500 M2 FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter | SUGAR UNIT - Water flow vacuum filter | 2016 | ROTARY VACCUM FILTER | VACUUM PUMP1 FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter | SUGAR UNIT - Distillery Tubewell Water line |  | TUBEWELL NO-4 DISTERLY | TUBEWELL NO-4 DISTERLY WATER LINE FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter | SUGAR UNIT - ETP Dicanter Flow meter | 2025 | Instrument Panel & HMI | Instrument Panel , HMI & Fld Inst. | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) | Control valve | SUGAR UNIT - :DBF 2 Flow control valve ( MCS Refinery) | 2015 | DEEP BED FILTER | DEEP BED FILTER FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) | Control valve | SUGAR UNIT - B.R.S Brine II Stage Control valve (Refinery) | 2015 | BRS IIND STAGE | BRS IIND STAGE FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD | Control valve | SUGAR UNIT -Cold water tank level control. | 2015 | B/ C MASSECUITE COOLING & REHEATING SYS | B/C MASSECUITE COLD WATER CIRCPUMP2 INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | Control valve | SUGAR UNIT - Refinary PAN No 3 Auto feed Valve | 2015 | REFINERY PAN | REFINERY PAN 3 & PAN CONDENSER FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | Control valve | SUGAR UNIT - Refinary PAN No 2 Auto feed Valve | 2015 | REFINERY PAN | REFINERY PAN 2 & PAN CONDENSER FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | Control valve | SUGAR UNIT - Refinary PAN No 1 Auto feed Valve | 2015 | REFINERY PAN | REFINERY PAN 1 & PAN CONDENSER FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | Control valve | SUGAR UNIT -Cooling condenser Main valve RAW. Pan.no.2 (Refinery) | 2015 | RAW PAN | RAW PAN N.2 & CONDENSER FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | Control valve | SUGAR UNIT -Cooling condenser Main valve Raw. Pan.no.3 | 2015 | RAW PAN | RAW PAN N.3 & CONDENSER FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Raw. Pan.no.3 | 2015 | RAW PAN | RAW PAN N.3 & CONDENSER FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | Control valve | SUGAR UNIT -Cooling condenser Spray valve RAW. Pan.no.3 | 2015 | RAW PAN | RAW PAN N.3 & CONDENSER FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Raw. Pan.no.3 | 2015 | RAW PAN | RAW PAN N.3 & CONDENSER FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | FLOW METER | SUGAR UNIT - Refinery Pan Hot water flow | 2016 | REFINERY PAN | REFINERY PAN 1 & PAN CONDENSER FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | Flow Meter | SUGAR UNIT - Refinery BRS 1st Stage Permit Tank | 2016 | BRS IST STAGE | BRS IST STAGE FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | Flow Meter | SUGAR UNIT - Refinery BRS 1st Stage Recycle | 2016 | BRS IST STAGE | BRS IST STAGE FLD INST | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | UNINTERRUPTIBLE POWER SUPPLY (UPS) | UPS FOR SUGAR PLANT RAW HOUSE | 2016 | RAW HOUSE UPS | RAW HOUSE UPS 1 | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | UNINTERRUPTIBLE POWER SUPPLY (UPS) | UPS FOR SUGAR PLANT RAW HOUSE | 2016 | RAW HOUSE UPS | RAW HOUSE UPS 2 | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | UNINTERRUPTIBLE POWER SUPPLY (UPS) | UPS FOR SUGAR PLANT REFINERY HOUSE | 2016 | REFINERY HOUSE UPS | REFINERY HOUSE UPS 1 | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | UNINTERRUPTIBLE POWER SUPPLY (UPS) | UPS FOR SUGAR PLANT REFINERY HOUSE | 2016 | REFINERY HOUSE UPS | REFINERY HOUSE UPS 2 | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | UNINTERRUPTIBLE POWER SUPPLY (UPS) | UPS FOR SUGAR PLANT MILL HOUSE | 2016 | MILL UPS | MILL UPS 1 | INSTRUMENT
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | UNINTERRUPTIBLE POWER SUPPLY (UPS) | UPS FOR SUGAR PLANT MILL HOUSE | 2016 | MILL UPS | MILL UPS 2 | INSTRUMENT

## EQUIPMENT SPECIFICATION
source file | sheet id | sheet name | EQUIPMENT TAG NO | section | sub_section | Parameter label | Parameter value
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  |  | Make | Triveni Engineering Works Naini Allahabad
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  |  | Type | FR14M
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  |  | Power | 3000 K.W.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  |  | S.L No | 140M077
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  |  | Rotor /Gear Speed | 2300/1500 Revs/Min.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  |  | Steam temp. | 415ᵒc
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  |  | Trip Speed | 9158/9574 Revs/Min.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  |  | Exhaust temp. | 150ᵒc
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  |  | Steam Pressure | 42 kg/cm2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  |  | Exhaust Pressure | 1.2 kg/cm2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  |  | Governor | Woodward
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  |  | Part no./Serial no. | 8516-050 /203758212400RPM CW
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 |  |  | Make | Triveni Engineering Works Naini Allahabad
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 |  |  | Type | FR14M
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 |  |  | Power | 3000 K.W.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 |  |  | S.L No | 1000M75
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 |  |  | Rotor /Gear Speed | 2300/1500 Revs/Min.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 |  |  | Steam temp. | 415ᵒc
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 |  |  | Trip Speed | 9158/9574 Revs/Min.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 |  |  | Exhaust temp. | 150ᵒc
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 |  |  | Steam Pressure | 42 kg/cm2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 |  |  | Exhaust Pressure | 1.2 kg/cm2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 |  |  | Governor | Woodward
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 |  |  | Part no./Serial no. | 8516-050 /203758212400RPM CW
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 |  |  | Make | Triveni Engineering Works Naini Allahabad
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 |  |  | Type | 525 MM Turbine
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 |  |  | Power | 1250 BHP KW/HP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 |  |  | S.L No- | 525142
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 |  |  | Rotor /Gear Speed | 6400/800 Revs/Min.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 |  |  | Steam temp. | 415ᵒc
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 |  |  | Trip Speed | 8800/9200 Revs/Min.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 |  |  | Exhaust temp. | 150ᵒc
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 |  |  | Steam Pressure | 45 kg/cm2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 |  |  | Exhaust Pressure | 1.2 Kg/cm2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 |  |  | Make | Triveni Engineering Works Naini Allahabad
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 |  |  | Type | 525 MM Turbine
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 |  |  | Power | 1250 BHP KW/HP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 |  |  | S.L No- | 525145
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 |  |  | Rotor /Gear Speed | 6400/800 Revs/Min.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 |  |  | Steam Pressure | 42 kg/cm2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 |  |  | Trip Speed | 8800/9200 Revs/Min.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 |  |  | Steam temp. | 415ᵒc
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 |  |  | Critical Speed | 14000 RPM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 |  |  | Exhaust temp. | 150ᵒc
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 |  |  | Exhaust Pressure | 1.2 Kg/cm2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 |  |  | Make | Triveni Engineering Works Naini Allahabad
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 |  |  | Type | 525 MM Turbine
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 |  |  | Power | 1250 BHP KW/HP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 |  |  | S.L No- | 525144
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 |  |  | Rotor /Gear Speed | 6400/800 Revs/Min.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 |  |  | Steam Pressure | 42 kg/cm2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 |  |  | Trip Speed | 8800/9200 Revs/Min.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 |  |  | Steam temp. | 415ᵒc
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 |  |  | Critical Speed | 14000 RPM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 |  |  | Exhaust temp. | 150ᵒc
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 |  |  | Exhaust Pressure | 1.2 Kg/cm2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Model | Actuator-RD 06
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Year of Manufacture | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Size | 50 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Cv | 68
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Material Disc/Body | SS-304 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Characteristic | Throttling
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Positioner/SOV | LSWP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Type of Valve | On-Off
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Model
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Air to fail | Valve Close
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Supply Pressure | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | AFR | Janetics
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | P Shut | 1 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) |  |  | Model | FRC 1361 (1/4")
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Sr.No. | 230995065
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Model | Actuator-RD 06
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Year of Manufacture | 2025
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Size | 50 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Cv | 68
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Material Disc/Body | SS-304 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Characteristic | Throttling
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Positioner/SOV | NOLWSP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Type of Valve | On-Off
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Model | RD1101
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Air to fail | Valve Close
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Supply Pressure | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | AFR | Janetics
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | P Shut | 1 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) |  |  | Model | FRC 1361 (1/4")
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Model | Actuator-RD 06
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Year of Manufacture | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Size | 50 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Cv | 68
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Material Disc/Body | SS-304 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Characteristic | Throttling
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Positioner/SOV | NOLWSP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Type of Valve | On-Off
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Model
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Air to fail | Valve Close
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Supply Pressure | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | AFR | Janetics
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | P Shut | 1 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) |  |  | Model | FRC 1361 (1/4")
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Sr.No. | 2412123503
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Model | Actuator-RD 06
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Year of Manufacture | 2025
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Size | 50 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Cv | 68
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Material Disc/Body | SS-304 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Characteristic | Throttling
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Positioner/SOV | NOLWSP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Type of Valve | On-Off
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Model
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Air to fail | Valve Close
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Supply Pressure | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | AFR | Janetics
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | P Shut | 1 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) |  |  | Model | FRC 1361 (1/4")
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) |  |  | Make | Hansford
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) |  |  | Sr.No. | Type -Vibration Sensor
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) |  |  | Model | HS420-F-025-50-01420
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) |  |  | Year of Manufacture | 2023
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) |  |  | Pressure transmitter | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) |  |  | RTD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) |  |  | Pressure transmitter | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Make | Revo-RD5050007000000
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Sr.No. | BIZF194010
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Model | EQRS91.4581
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Year of Manufacture | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Size | 50 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Cv | 68
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Hand wheel
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | No
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Material Disc/Body | SS-304 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Characteristic | Throttling
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Positioner | YTC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Seat Replacement type | EPDM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Type of Valve | Butterfly valve
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Model | EP1000
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Air to fail | Open
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Sr.No. | N0310688
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Supply Pressure | 2.5 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | AFR | Janetics
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | P Shut | 2 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET |  |  | Model | FRC 1361 (1/4")
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Make | Revo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Sr.No. | B15D2106
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Model | RD700600500000
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Year of Manufacture | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Size | 50 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Cv | 68
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Hand wheel
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | No
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Material Disc/Body | GG25SS1.4581
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Characteristic | Throttling
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Positioner | ABB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Seat Replacement type | EPDM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Type of Valve | Butterfly valve
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Model | RD1101
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Air to fail | Valve Open
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Sr.No. | 122122
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Supply Pressure | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | AFR | Janetics
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | P Shut | 1 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Model | FRC 1361 (1/4")
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Conductivity Tx. | ISCT-1072
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 |  |  | Make | I & S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Make | Revo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Sr.No. | B15D2101
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Model | RD700600500000
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Year of Manufacture | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Size | 50 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Cv | 68
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Hand wheel
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | No
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Material Disc/Body | GG25SS1.4581
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Characteristic | Throttling
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Positioner | ABB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Seat Replacement type | EPDM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Type of Valve | Butterfly valve
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Model | RD1101
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Air to fail | Valve Open
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Sr.No. | 122122
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Supply Pressure | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | AFR | Janetics
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | P Shut | 1 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Model | FRC 1361 (1/4")
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Conductivity Tx. | ISCT-1079
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 |  |  | Make | I & S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Sr.No. | 151141517
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Type | Diaphram
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Model | 110/PDC 140S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Year of Manufacture | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Size | 150 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Cv | 450
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Material Disc/Body | SS-304 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Characteristic | Equal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Positioner | Siemens
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Type of Valve | Globe Valve(Contoured)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Model | Sipart PS2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Air to fail | Valve Close
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Sr.No. | N1F8037470853
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Travel | 57 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Supply Pressure | 2.5 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | AFR | Savo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | P Shut | .2 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Model | SB-11-4SN 200 M 1/4"
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Level Transmitter | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Body Temp. Transmitter | Yokogawa/YTA 110 - EA2DB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Brix transmitter | Birth Hold/LB565
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Body Vacuum Transmitter | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Calendria temp. Transmitter | Yokogawa/YTA 110 - EA2DB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Auto feed Panel | GN engineering
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Calendria Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Tail pipe temp Transmitter | ABB/TTF2000Y1A1B1K1C1
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Vacuum/Pr. /temp. Gauge | General
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) |  |  | Vacuum Breaker | Aira
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Manufacturer – | Rose mount
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Serial No. | 13141208
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Working Temperature | (-29 to 60˚)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Model | 8705TSA030C1W0B3
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | working pressure | 285 PSI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Nominal Dia ( MM) | 80 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Calibration Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Accuracy | 0.0015
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | 316 S1 | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | ±0.1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Output | 4-20 mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Comunication | HART
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | 90-220 VAC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Protection | IP 67
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | Display unit | Cable length
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 |  |  | 10 MTR
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Manufacturer – | Rose mount
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Serial No. | 6205899
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Working Temperature | (-29 to 60˚)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Model | 8705TSA030C1W0B3
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | working pressure | 285 PSI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Nominal Dia ( MM) | 80 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Calibration Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Accuracy | 0.0015
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | 316 S1 | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | ±0.1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Output | 4-20 mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Comunication | HART
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | 90-220 VAC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Protection | IP 67
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Display unit | Cable length
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | 10 MTR
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 |  |  | Melt conc. Brix Trans. | SMAR/BR-14160
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | Manufacturer – | Krone Marshal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | Serial No. | Working Temperature
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | (-29 to 60˚)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | Model | Range
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | NA | working pressure
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | 285 PSI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | Nominal Dia ( MM) | Calibration Range
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | NA | Accuracy
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | 316 S1 | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | ±0.1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | Output | 4-20 mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | Comunication | HART
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | 90-220 VAC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | Protection | IP 67
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | Display unit | Cable length
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL |  |  | 10 MTR
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Manufacturer – | Adept
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Serial No. | 2200077
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Working Temperature | (-29 to 60˚)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Model | Mag Flow 6410
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Range | 80 M3/hr
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | working pressure | 285 PSI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Nominal Dia ( MM) | 100 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Calibration Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Accuracy | 0.0015
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | 316 S1 | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | ±0.1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Output | 4-20 mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Comunication | HART
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | 90-220 VAC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Protection | IP 67
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | Display unit | Cable length
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM |  |  | 10 MTR
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Manufacturer – | Adept
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Serial No. | 230808178
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Working Temperature | (-29 to 60˚)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Model | Mag Flow 6415
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Range | 60 M3/hr
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | working pressure | 285 PSI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Nominal Dia ( MM) | 80 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Calibration Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Accuracy | 0.0015
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | 316 S1 | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | ±0.1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Output | 4-20 mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Comunication | HART
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | 90-220 VAC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Protection | IP 67
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | Display unit | Cable length
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL |  |  | 10 MTR
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Manufacturer – | ABB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Serial No. | 075BF15F075
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Working Temperature | (-29 to 60˚)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Model | FET3211AOA1B1C1H1M5
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Range | 70 M3/hr
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | working pressure | 285 PSI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Nominal Dia ( MM) | 80 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Calibration Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Accuracy | 0.0015
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | 316 S1 | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | ±0.1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Output | 4-20 mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Comunication | HART
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | 90-220 VAC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Protection | IP 67
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | Display unit | Cable length
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP |  |  | 10 MTR
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Manufacturer – | Krone Marshal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Serial No. | I25415727C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Working Temperature | (-29 to 60˚)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Model | IFC101
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Range | 180M3/Hr
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | working pressure | 285 PSI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Nominal Dia ( MM) | 150 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Calibration Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Accuracy | 0.0015
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | 316 S1 | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | ±0.1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Output | 4-20 mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Comunication | HART
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | 90-220 VAC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Protection | IP 67
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | Display unit | Cable length
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE |  |  | 10 MTR
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Manufacturer – | Rose Mount
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Serial No. | 6103299
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Working Temperature | (-29 to 60˚)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Model | 8732EST1A1NEM4
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Range | 30 M3/hr
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | working pressure | 285 PSI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Nominal Dia ( MM) | 50 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Calibration Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Accuracy | 0.0015
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | 316 S1 | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | ±0.1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Output | 4-20 mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Comunication | HART
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | 90-220 VAC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Protection | IP 67
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | Display unit | Cable length
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET |  |  | 10 MTR
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Make | Continental
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Sr.No. | 13104
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Type | Single Acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Model | 3102
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Year of Manufacture | 2022
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Tubing | SS
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Size | 150 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Cv | Hand wheel
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Material Disc/Body | SS-316 / WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Characteristic | Throttling
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Positioner | YTC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Type of Valve | Butterfly
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Model | EP-1000RSN
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Seat Leakage Class | Air to fail
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | open
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Sr.No. | NIL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Travel | 90 DEG
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Supply Pressure | 2.5 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | AFR
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | P Shut | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 |  |  | Model
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Make | TRANSTORK
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Sr.No. | 8796
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Type | Double Acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Model | MOR-100
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Year of Manufacture | 2015
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Tubing | PU tube
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Size | 100 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Cv | 1225
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Hand wheel
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | NO
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Material Disc/Body | A216GR WBC/SS 304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Characteristic | On-off
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Positioner | Dome switch
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Type of Valve | Butterfly
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Model
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Air to fail | Valve closed
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Travel | 38 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Supply Pressure | 2.5 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | AFR | Shavo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | P Shut | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Model-SB-11-4SN | 200 M 1/4"
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Actuator Make/model | Crane/B24P 1774
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Vibration Tx.-01 | GEA/ID no:00005-1848-0,BW:10-1000 Hz,FS: 50mm/S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | RTD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Magnetic Flow Meter | Emerson (Rosemount) /8712EMR1A1M4
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Level Tx. | Rosemount/2051CD2A22A1AS1M4Q4
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Level switch
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 |  |  | Magnetic Flow Meter tube | Emerson (Rosemount)/8705TSA030C1W0
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Manufacturer – | Yokogawa
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Serial No. | Y1U600319
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Working Temperature | 120 DEEGRI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Model | EJA11OE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Range | working pressure
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | 10 KG/CM2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Nominal Dia ( MM) | 1000 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Calibration Range | 0-100 M3/hr
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Accuracy
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Material Body | MS (Venturi)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Sensor Material | Linearity
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Liner | Output
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | 4 -20mA | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | 24 VDC | Comunication
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Display unit | 2 line LCD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Cable length | 5 Mtr.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW |  |  | Protection | Earthing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Manufacturer – | SIEMENS
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Serial No. | 7MF4433-1EA02-2AC02
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Working Temperature | 120 DEEGRI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Model | SIRANSP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Range | working pressure
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | 10 KG/CM2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Nominal Dia ( MM) | 150 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Calibration Range | 0-100 TPH
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Accuracy
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Material Body | MS/SS ORIFICE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Sensor Material | Linearity
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Liner | Output
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | 4 -20mA | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | 24 VDC | Comunication
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Display unit | 2 line LCD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Cable length | 5 Mtr.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 |  |  | Protection | Earthing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Manufacturer – | ENDRESS+HAUSER
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Serial No. | H3021A20000
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Working Temperature | 120 DEEGRI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Model | PROMAG P
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Range | 0-300 M3/hr
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | working pressure | 10 KG/CM2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Nominal Dia ( MM) | 200 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Calibration Range | 0-300 M3/hr
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Accuracy
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Linearity
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Output | 4 -20mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | 220VAC | Comunication
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Display unit | 2 line LCD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Cable length | 5 Mtr.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 |  |  | Protection | Earthing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Manufacturer – | Krohne Marshal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Serial No. | J164080098
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Working Temperature | 120 DEEGRI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Model | IFC100
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Range | working pressure
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | 10 KG/CM2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Nominal Dia ( MM) | 50 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Calibration Range | 0-10 M3/Hr.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Accuracy
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Linearity
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Output | 4 -20mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | 220VAC | Comunication
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Display unit | 2 line LCD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Cable length | 5 Mtr.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 |  |  | Protection | Earthing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Manufacturer – | Adept
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Serial No. | 1004974
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Working Temperature | 120 DEEGRI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Model | 6410
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Range | 0-150 M3/Hr.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | working pressure | 10 KG/CM2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Nominal Dia ( MM) | 150MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Calibration Range | 0-150 M3/Hr.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Accuracy
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | SS316 | Linearity
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Output | 4 -20mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | 24 VDC | Comunication
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Display unit | 2 line LCD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Cable length | 5 Mtr.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 |  |  | Protection | Earthing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Manufacturer – | Adept
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Serial No. | 230808234
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Working Temperature | 120 DEEGRI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Model | 6415
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Range | 0-30 M3/Hr.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | working pressure | 10 KG/CM2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Nominal Dia ( MM) | 50MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Calibration Range | .1-30 M3/Hr.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Accuracy
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | SS316 | Linearity
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Output | 4 -20mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | 220VAC | Comunication
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Display unit | 2 line LCD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Cable length | 5 Mtr.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM |  |  | Protection | Earthing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Make | Continental
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Sr. No. | 19127
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Model | 232/SA -100+M
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Year of Mfg. | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Size | 100 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Cv | 175
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Material Disc/Body | SS-316 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Characteristic | THROTTLING
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Positioner | Seimens
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Type of Valve | Butterfly valve
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Model | Sipart PS2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Air to fail | Valve Close
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Sr. No. | N1H1057494184
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Supply Pressure | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | AFR | Savo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | P Shut | 1 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Model | SB-10
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Drain Header Pr. Trans. | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) |  |  | Liqour Feed I/L Flow Meter | Rosemount/8732EMT1A1M4
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Make | R K Valve
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Sr.No. | 15160898
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Type | Diapharm
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Model | 10-765/A30/5T
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Year of Mfg. | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Size | 38 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Cv | 3.2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Material Disc/Body | A351 CR CF8
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Characteristic | Equal %
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Positioner | YTC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Seat Replacement type | SS-316FH
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Type of Valve | Globe valve
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Model
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Air to fail | Valve Open
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Travel | 28 mm
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Supply Pressure | 2.5 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | AFR | Savo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | P Shut | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Model | SB-10
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) |  |  | Spent level Trans. | ABB/AT100SB/L/A1
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Sr.No. | 1602 41994
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Type | Actuator
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Model | 232/SA-150 M
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Year of Mfg. | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Size | 200 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Cv | 3.2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Material Disc/Body | A351 CR CF8
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Characteristic | Equal %
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | SOV | Rotex
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Seat Replacement type | SS-316FH
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Type of Valve | Butterfly
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Model
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Air to fail | Valve close
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Travel | 28 mm
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Supply Pressure | 2.5 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | AFR | Savo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | P Shut | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Model | SB-10
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Hot Water Overhead Tank (22T150) LT | Yokogawa/EJA210E-JMS5J-912EN-WA1JA15
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Hot Water Overhead Tank (22T160) LT | Yokogawa/EJA210E-JMS5J-912EN-WA1JA15
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD |  |  | Cold Water Overhead Tank (22T170) Level Transmitter | Yokogawa/EJA210E-JMS5J-912EN-WA1JA15
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Sr.No. | 1511 41531
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Type | Diaphram
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Model | 110/PDC 140 S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Year of Mfg. | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Size | 150 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Cv | 220
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Material Disc/Body | SS-316 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Characteristic | Equal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Positioner | Siemens
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Type of Valve | Globe Valve(Contoured)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Model | Sipart PS2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Air to fail | Valve Close
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Sr.No. | N1F801748161
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Travel | 57 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Supply Pressure | 2.5 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | AFR | Savo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | P Shut | .2 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Model | SB-11-4SN 200 M 1/4"
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Level Transmitter | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Body Temp. Transmitter | Yokogawa/YTA 110 - EA2DB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Brix transmitter | Birth Hold/LB565
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Body Vacuum Transmitter | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Calendria temp. Transmitter | Yokogawa/YTA 110 - EA2DB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Auto feed Panel | GN engineering
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Calendria Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Tail pipe temp Transmitter | Yokogawa/YTA 110 - EA2DB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) |  |  | Vacuum/Pr. /temp. Gauge | General
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Sr.No. | 1511 41515
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Type | Diaphram
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Model | 110/PDC 140 S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Year of Mfg. | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Size | 150 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Cv | 220
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Material Disc/Body | SS-316 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Characteristic | Equal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Positioner | Siemens
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Type of Valve | Globe Valve(Contoured)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Model | Sipart PS2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Air to fail | Valve Close
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Sr.No. | N1F8037470861
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Travel | 57 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Supply Pressure | 2.5 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | AFR | Savo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | P Shut | .2 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Model | SB-11-4SN 200 M 1/4"
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Level Transmitter | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Body Temp. Transmitter | Yokogawa/YTA 110 - EA2DB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Brix transmitter | Birth Hold/LB565
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Body Vacuum Transmitter | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Calendria temp. Transmitter | Yokogawa/YTA 110 - EA2DB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Auto feed Panel | GN engineering
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Calendria Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Tail pipe temp Transmitter | Yokogawa/YTA 110 - EA2DB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) |  |  | Vacuum/Pr. /temp. Gauge | General
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Sr.No. | 1511 41532
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Type | Diaphram
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Model | 110/PDC 140 S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Year of Mfg. | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Size | 150 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Cv | 220
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Material Disc/Body | SS-316 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Characteristic | Equal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Positioner | Siemens
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Type of Valve | Globe Valve(Contoured)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Model | Sipart PS2
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Air to fail | Valve Close
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Sr.No. | N1F8067473056
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Travel | 57 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Supply Pressure | 2.5 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | AFR | Savo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | P Shut | .2 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Model | SB-11-4SN 200 M 1/4"
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Level Transmitter | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Body Temp. Transmitter | Yokogawa/YTA 110 - EA2DB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Brix transmitter | Birth Hold/LB565
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Body Vacuum Transmitter | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Calendria temp. Transmitter | Yokogawa/YTA 110 - EA2DB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Auto feed Panel | GN engineering
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Calendria Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Tail pipe temp Transmitter | Yokogawa/YTA 110 - EA2DB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | Vacuum/Pr. /temp. Gauge | General
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | R1-Footing Vacuum XLR Level Tx. | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | R2/R3-Footing Vacuum XLR LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | DRY Seed XLR LT | Siemens/7ML52212BA11
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | R2/R3-Footing Vacuum XLR PT | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) |  |  | R1-Footing Vacuum XLR PT | Yokogawa/EJA530E-JAS40N-012EL
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Sr.No. | 1511 41568
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Model | 232SA 200+M
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Year of Mfg. | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Size | 400 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Cv | 4500
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Material Disc/Body | SS-316 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Characteristic | On-off
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Positioner | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Type of Valve | Butterfly valve
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Model | LSWP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Air to fail | Valve Open
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Supply Pressure | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | AFR | Savo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | P Shut | 1 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) |  |  | Model | SB-10
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Sr.No. | 1610 46381
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Model | 232SA 200+M
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Year of Mfg. | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Size | 400 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Cv | 8000
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Material Disc/Body | SS-316 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Characteristic | On-off
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Positioner | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Type of Valve | Butterfly valve
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Model | LSWP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Air to fail | Valve Open
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Supply Pressure | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | AFR | Savo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | P Shut | 1 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) |  |  | Model | SB-10
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Sr.No. | 1610 45374
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Model | 232SA 115+M
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Year of Mfg. | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Size | 125 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Cv | 425
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Material Disc/Body | SS-316 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Characteristic | On-off
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Positioner | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Type of Valve | Butterfly valve
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Model | LSWP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Air to fail | Valve Open
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Supply Pressure | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | AFR | Savo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | P Shut | 1 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) |  |  | Model | SB-10
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Sr.No. | 1610 45371
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Model | 232SA 115+M
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Year of Mfg. | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Size | 125 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Cv | 425
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Material Disc/Body | SS-316 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Characteristic | On-off
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Positioner | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Type of Valve | Butterfly valve
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Model | LSWP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Air to fail | Valve Open
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Supply Pressure | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | AFR | Savo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | P Shut | 1 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) |  |  | Model | SB-10
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Make | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Sr.No. | 1511 41574
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Type | Rotary single acting
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Model | 232SA 115+M
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Year of Mfg. | 2014
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Tubing | SS-304
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Size | 125 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Cv | 425
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Hand wheel | YES
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Material Disc/Body | SS-316 / A216GR WCB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Characteristic | On-off
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Positioner | Pneucon
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Seat Replacement type | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Type of Valve | Butterfly valve
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Model | LSWP
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Seat Leakage Class | VI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Air to fail | Valve Open
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Sr.No.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Travel | 90ᵒ
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Supply Pressure | 4 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | AFR | Savo
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | P Shut | 1 KSC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) |  |  | Model | SB-10
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Manufacturer – | Rosemount
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Serial No. | 13140866
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Working Temperature | (-29 to 60˚)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Model | 8705TSA020C1W0B3
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | working pressure | 285 PSI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Nominal Dia ( MM) | 50 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Calibration Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Accuracy | 0.0015
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | 316 S1 | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | ±0.1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Output | 4-20 mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Comunication | HART
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Display Version | E- Series
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Power Supply | 90-220 VAC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Protection | IP 67
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Display unit | 2 line LCD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 |  |  | Cable length | Head-Mount
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Manufacturer – | ABB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Serial No. | Working Temperature
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | (-29 to 60˚)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Model | FET3211B0A1B1C1M5
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | working pressure | 285 PSI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Nominal Dia ( MM) | 15 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Calibration Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Accuracy | 0.0015
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | 316 S1 | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | ±0.1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Output | 4-20 mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Comunication | HART
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | 90-220 VAC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Protection | IP 67
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | Display unit | Cable length
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 |  |  | 10 MTR
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Manufacturer – | ABB
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Serial No. | Working Temperature
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | (-29 to 60˚)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Model | FET3211B0A1B1C1M5
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | working pressure | 285 PSI
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Nominal Dia ( MM) | 25 MM
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Calibration Range | NA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Accuracy | 0.0015
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Material Body | Sensor Material
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | 316 S1 | Repeatability
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | ±0.1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Liner | PTFE
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Output | 4-20 mA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Comunication | HART
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Display Version | Power Supply
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | 90-220 VAC
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Protection | IP 67
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | Display unit | Cable length
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 |  |  | 10 MTR
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Make/Model | Emerson network power
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Sr. No. | 115UC5251001
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Battery voltage | 110 VDC (2-25 kVA UPS) (170-176 cells for Lead Acid
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Protections(rectifire) | Input MCCB,input single phaseing,input fuse fail,input under/over voltage,rectifire over voltage
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Temperature Operating | upto 50 °C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Nominal Input Voltage | 415 V AC, 3 Phase, 3 wire ( +10 %, -20 % )
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Rectifire type | Full Wave, A-PFC Rectifier
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Battery charging capacity | 2 to 20 KVA ,20 A
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Protections(inverter) | Inverter over temp.,output under voltage,output over voltage,output short circuit,o/p overload
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Temperature Storage | 0 to 55 °C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Nominal Input Frequency | 50 Hz (± 10 %)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Charger type | IGBT based Dual mode of charging
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Type | Ni-CD/Tubular/VRLA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Protections(battery) | Battery MCCB,battery low,battery over voltage,output short circuit
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Relative humidity | 0 to 95 %, non-condensing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Input Power factor | 0.92
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Charging Method | Constant Voltage Constant Current (CVCC) Auto & Manual with 0 to 24 Hr programmable timer
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Protection | Battery breaker,reverse battery indication,reverse polarity,battery eirth fault
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Emitted noise | < 55 dB (A)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Input Fault Level | 10 kA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Voltage Regulation | ± 1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Connectivity | RS232/RS485
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Ripple(without battery) | <1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Make/Model | Emerson network power
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Sr. No. | 115UC5251002
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Battery voltage | 110 VDC (25 kVA UPS) (174 cells for Lead Acid
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Protections(rectifire) | Input MCCB,input single phaseing,input fuse fail,input under/over voltage,rectifire over voltage
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Temperature Operating | upto 50 °C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Nominal Input Voltage | 415 V AC, 3 Phase, 3 wire ( +10 %, -20 % )
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Rectifire type | Full Wave, A-PFC Rectifier
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Battery charging capacity | 2 to 25 KVA ,20 A
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Protections(inverter) | Inverter over temp.,output under voltage,output over voltage,output short circuit,o/p overload
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Temperature Storage | 0 to 55 °C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Nominal Input Frequency | 50 Hz (± 10 %)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Charger type | IGBT based Dual mode of charging
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Type | Ni-CD/Tubular/VRLA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Protections(battery) | Battery MCCB,battery low,battery over voltage,output short circuit
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Relative humidity | 0 to 95 %, non-condensing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Input Power factor | 0.92
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Charging Method | Constant Voltage Constant Current (CVCC) Auto & Manual with 0 to 24 Hr programmable timer
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Protection | Battery breaker,reverse battery indication,reverse polarity,battery eirth fault
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Emitted noise | < 55 dB (A)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Input Fault Level | 10 kA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Voltage Regulation | ± 1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Connectivity | RS232/RS485
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Ripple(without battery) | <1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Make/Model | Emerson network power
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Sr. No. | 115UC5249003
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Battery voltage | 110 VDC (2-15 kVA UPS) (54 to 67 cells for Lead Acid
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Protections(rectifire) | Input MCCB,input single phaseing,input fuse fail,input under/over voltage,rectifire over voltage
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Temperature Operating | upto 50 °C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Nominal Input Voltage | 415 V AC, 3 Phase, 3 wire ( +10 %, -20 % )
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Rectifire type | Full Wave, A-PFC Rectifier
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Battery charging capacity | 2 to 20 KVA ,20 A
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Protections(inverter) | Inverter over temp.,output under voltage,output over voltage,output short circuit,o/p overload
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Temperature Storage | 0 to 55 °C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Nominal Input Frequency | 50 Hz (± 10 %)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Charger type | IGBT based Dual mode of charging
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Type | Ni-CD/Tubular/VRLA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Protections(battery) | Battery MCCB,battery low,battery over voltage,output short circuit
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Relative humidity | 0 to 95 %, non-condensing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Input Power factor | 0.92
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Charging Method | Constant Voltage Constant Current (CVCC) Auto & Manual with 0 to 24 Hr programmable timer
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Protection | Battery breaker,reverse battery indication,reverse polarity,battery eirth fault
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Emitted noise | < 55 dB (A)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Input Fault Level | 10 kA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Voltage Regulation | ± 1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Connectivity | RS232/RS485
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Ripple(without battery) | <1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Make/Model | Emerson network power
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Sr. No. | 115UC5249004
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Battery voltage | 110 VDC (2-15 kVA UPS) (54 to 67 cells for Lead Acid
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Protections(rectifire) | Input MCCB,input single phaseing,input fuse fail,input under/over voltage,rectifire over voltage
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Temperature Operating | upto 50 °C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Nominal Input Voltage | 415 V AC, 3 Phase, 3 wire ( +10 %, -20 % )
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Rectifire type | Full Wave, A-PFC Rectifier
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Battery charging capacity | 2 to 20 KVA ,20 A
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Protections(inverter) | Inverter over temp.,output under voltage,output over voltage,output short circuit,o/p overload
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Temperature Storage | 0 to 55 °C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Nominal Input Frequency | 50 Hz (± 10 %)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Charger type | IGBT based Dual mode of charging
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Type | Ni-CD/Tubular/VRLA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Protections(battery) | Battery MCCB,battery low,battery over voltage,output short circuit
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Relative humidity | 0 to 95 %, non-condensing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Input Power factor | 0.92
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Charging Method | Constant Voltage Constant Current (CVCC) Auto & Manual with 0 to 24 Hr programmable timer
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Protection | Battery breaker,reverse battery indication,reverse polarity,battery eirth fault
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Emitted noise | < 55 dB (A)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Input Fault Level | 10 kA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Voltage Regulation | ± 1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Connectivity | RS232/RS485
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Ripple(without battery) | <1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Make/Model | Emerson network power
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Sr. No. | 115UC5249001
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Battery voltage | 110 VDC (2-15 kVA UPS) (54 to 67 cells for Lead Acid
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Protections(rectifire) | Input MCCB,input single phaseing,input fuse fail,input under/over voltage,rectifire over voltage
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Temperature Operating | upto 50 °C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Nominal Input Voltage | 415 V AC, 3 Phase, 3 wire ( +10 %, -20 % )
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Rectifire type | Full Wave, A-PFC Rectifier
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Battery charging capacity | 2 to 20 KVA ,20 A
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Protections(inverter) | Inverter over temp.,output under voltage,output over voltage,output short circuit,o/p overload
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Temperature Storage | 0 to 55 °C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Nominal Input Frequency | 50 Hz (± 10 %)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Charger type | IGBT based Dual mode of charging
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Type | Ni-CD/Tubular/VRLA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Protections(battery) | Battery MCCB,battery low,battery over voltage,output short circuit
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Relative humidity | 0 to 95 %, non-condensing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Input Power factor | 0.92
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Charging Method | Constant Voltage Constant Current (CVCC) Auto & Manual with 0 to 24 Hr programmable timer
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Protection | Battery breaker,reverse battery indication,reverse polarity,battery eirth fault
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Emitted noise | < 55 dB (A)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Input Fault Level | 10 kA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Voltage Regulation | ± 1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Connectivity | RS232/RS485
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Ripple(without battery) | <1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Make/Model | Emerson network power
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Sr. No. | 115UC5249002
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Battery voltage | 110 VDC (2-15 kVA UPS) (54 to 67 cells for Lead Acid
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Protections(rectifire) | Input MCCB,input single phaseing,input fuse fail,input under/over voltage,rectifire over voltage
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Temperature Operating | upto 50 °C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Nominal Input Voltage | 415 V AC, 3 Phase, 3 wire ( +10 %, -20 % )
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Rectifire type | Full Wave, A-PFC Rectifier
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Battery charging capacity | 2 to 20 KVA ,20 A
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Protections(inverter) | Inverter over temp.,output under voltage,output over voltage,output short circuit,o/p overload
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Temperature Storage | 0 to 55 °C
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Nominal Input Frequency | 50 Hz (± 10 %)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Charger type | IGBT based Dual mode of charging
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Type | Ni-CD/Tubular/VRLA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Protections(battery) | Battery MCCB,battery low,battery over voltage,output short circuit
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Relative humidity | 0 to 95 %, non-condensing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Input Power factor | 0.92
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Charging Method | Constant Voltage Constant Current (CVCC) Auto & Manual with 0 to 24 Hr programmable timer
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Protection | Battery breaker,reverse battery indication,reverse polarity,battery eirth fault
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Emitted noise | < 55 dB (A)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Input Fault Level | 10 kA
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Voltage Regulation | ± 1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Connectivity | RS232/RS485
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Ripple(without battery) | <1%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201

## MAINTENANCE SCHEDULE
source file | sheet id | sheet name | EQUIPMENT TAG NO | Sr.No. | Name of Equipment | Maintenance / Inspection Activities | Daily | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years | 4 - Years | Remarks
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 1 | Stop & Emergency Valve | Blue contact between Valve & Seat | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 1 | Stop & Emergency Valve | Thrust Bearing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 1 | Stop & Emergency Valve | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 2 | Throttle Valves | Bearings | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 2 | Throttle Valves | Pivot Pins & Lock Pins
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 2 | Throttle Valves | Lift measurement & Valve freeness
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 3 | Turbine Casing | Casing to Pedestal alignment | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 3 | Turbine Casing | Casing fasteners bolts elongation check & retightening)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 3 | Turbine Casing | Casing joint line (Compound replacement)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 3 | Turbine Casing | Full assembly (External)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 4 | Relay with Governor | Worm wheel | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 4 | Relay with Governor | Bearing,springs, Sliping clutch.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 4 | Relay with Governor | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 5 | Over Load Valve | Spindles | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 5 | Over Load Valve | Guide box
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 5 | Over Load Valve | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 6 | Nozzle & Diaphragms | Nozzles (1st stage) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 6 | Nozzle & Diaphragms | Steam labyrinth packing (HP & LP)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 6 | Nozzle & Diaphragms | Steam labyrinth packing holders (HP & LP)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 6 | Nozzle & Diaphragms | Oil seal labyrinth packing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 7 | Rotor | Bearings | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 7 | Rotor | Rotor Shaft
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 7 | Rotor | Thrust Bearing Pads
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 7 | Rotor | HP & LP blades
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 8 | Overspeed Trip | Full assembly (Internal) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 8 | Overspeed Trip | Springs
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 9 | Exhaust Steam Relief Valve | Springs | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 9 | Exhaust Steam Relief Valve | Valve seat
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 10 | Gear Box | Alignment between Gear box & Drive Equipment | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 10 | Gear Box | Alignment between Turbine & Gear box
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 10 | Gear Box | Bearings Casing Fastener
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 10 | Gear Box | Gear & Gear wheel
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 10 | Gear Box | Pinion
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 10 | Gear Box | SSS Clutch ,Oil Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 10 | Gear Box | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 11 | Coupling (HS &LS) | Transmission Unit / Elements | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 11 | Coupling (HS &LS) | Shear pins
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 11 | Coupling (HS &LS) | Coupling bolt tightness check
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 12 | Main oil tank | Inspection & Cleaning | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 12 | Main oil tank | Tank's rust preventive coating
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 12 | Main oil tank | Suction strainers & Foot valves
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 13 | Filter | Filter element | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 13 | Filter | Filter Assembly
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 13 | Filter | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 14 | Alternator - | Rotor Shaft | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 14 | Alternator - | Full assembly
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 14 | Alternator - | Shaft balancing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 14 | Alternator - | Bearings
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 15 | All Duties Valve | Full assembly | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | 15 | All Duties Valve | Valve and seat contact
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 1 | Stop & Emergency Valve | Blue contact between Valve & Seat | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 1 | Stop & Emergency Valve | Thrust Bearing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 1 | Stop & Emergency Valve | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 2 | Throttle Valves | Bearings | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 2 | Throttle Valves | Pivot Pins & Lock Pins
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 2 | Throttle Valves | Lift measurement & Valve freeness
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 3 | Turbine Casing | Casing to Pedestal alignment | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 3 | Turbine Casing | Casing fasteners bolts elongation check & retightening)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 3 | Turbine Casing | Casing joint line (Compound replacement)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 3 | Turbine Casing | Full assembly (External)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 4 | Relay with Governor | Worm wheel | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 4 | Relay with Governor | Bearing,springs, Sliping clutch.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 4 | Relay with Governor | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 5 | Over Load Valve | Spindles | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 5 | Over Load Valve | Guide box
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 5 | Over Load Valve | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 6 | Nozzle & Diaphragms | Nozzles (1st stage) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 6 | Nozzle & Diaphragms | Steam labyrinth packing (HP & LP)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 6 | Nozzle & Diaphragms | Steam labyrinth packing holders (HP & LP)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 6 | Nozzle & Diaphragms | Oil seal labyrinth packing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 7 | Rotor | Bearings | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 7 | Rotor | Rotor Shaft
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 7 | Rotor | Thrust Bearing Pads
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 7 | Rotor | HP & LP blades
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 8 | Overspeed Trip | Full assembly (Internal) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 8 | Overspeed Trip | Springs
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 9 | Exhaust Steam Relief Valve | Springs | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 9 | Exhaust Steam Relief Valve | Valve seat
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 10 | Gear Box | Alignment between Gear box & Drive Equipment | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 10 | Gear Box | Alignment between Turbine & Gear box
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 10 | Gear Box | Bearings Casing Fastener
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 10 | Gear Box | Gear & Gear wheel
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 10 | Gear Box | Pinion
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 10 | Gear Box | SSS Clutch ,Oil Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 10 | Gear Box | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 11 | Coupling(HS &LS) | Transmission Unit / Elements | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 11 | Coupling(HS &LS) | Shear pins
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 11 | Coupling(HS &LS) | Coupling bolt tightness check
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 12 | Main oil tank | Inspection & Cleaning | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 12 | Main oil tank | Tank's rust preventive coating
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 12 | Main oil tank | Suction strainers & Foot valves
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 13 | Filter | Filter element | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 13 | Filter | Filter Assembly
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 13 | Filter | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 14 | Alternator - | Rotor Shaft | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 14 | Alternator - | Full assembly
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 14 | Alternator - | Shaft balancing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 14 | Alternator - | Bearings
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 15 | All Duties Valve | Full assembly | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | 15 | All Duties Valve | Valve and seat contact
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 1 | Stop & Emergency Valve | Blue contact between Valve & Seat | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 1 | Stop & Emergency Valve | Thrust Bearing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 1 | Stop & Emergency Valve | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 2 | Throttle Valves | Bearings | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 2 | Throttle Valves | Pivot Pins & Lock Pins
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 2 | Throttle Valves | Lift measurement & Valve freeness
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 3 | Turbine Casing | Casing to Pedestal alignment | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 3 | Turbine Casing | Casing fasteners bolts elongation check & retightening)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 3 | Turbine Casing | Casing joint line (Compound replacement)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 3 | Turbine Casing | Full assembly (External)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 4 | Relay with Governor | Worm wheel | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 4 | Relay with Governor | Bearing,springs, Sliping clutch.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 4 | Relay with Governor | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 5 | Over Load Valve | Spindles | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 5 | Over Load Valve | Guide box
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 5 | Over Load Valve | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 6 | Nozzle & Diaphragms | Nozzles (1st stage) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 6 | Nozzle & Diaphragms | Steam labyrinth packing (HP & LP)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 6 | Nozzle & Diaphragms | Steam labyrinth packing holders (HP & LP)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 6 | Nozzle & Diaphragms | Oil seal labyrinth packing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 7 | Rotor | Bearings | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 7 | Rotor | Rotor Shaft
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 7 | Rotor | Thrust Bearing Pads
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 7 | Rotor | HP & LP blades
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 8 | Overspeed Trip | Full assembly (Internal) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 8 | Overspeed Trip | Springs
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 9 | Exhaust Steam Relief Valve | Springs | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 9 | Exhaust Steam Relief Valve | Valve seat
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 10 | Gear Box | Alignment between Gear box & Drive Equipment | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 10 | Gear Box | Alignment between Turbine & Gear box
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 10 | Gear Box | Bearings Casing Fastener
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 10 | Gear Box | Gear & Gear wheel
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 10 | Gear Box | Pinion
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 10 | Gear Box | SSS Clutch ,Oil Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 10 | Gear Box | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 11 | Coupling (HS &LS) | Transmission Unit / Elements | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 11 | Coupling (HS &LS) | Shear pins
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 11 | Coupling (HS &LS) | Coupling bolt tightness check
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 12 | Main oil tank | Inspection & Cleaning | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 12 | Main oil tank | Tank's rust preventive coating
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 12 | Main oil tank | Suction strainers & Foot valves
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 13 | Filter | Filter element | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 13 | Filter | Filter Assembly
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 13 | Filter | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 14 | All Duties Valve | Full assembly | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | 14 | All Duties Valve | Valve and seat contact
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 1 | Stop & Emergency Valve | Blue contact between Valve & Seat | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 1 | Stop & Emergency Valve | Thrust Bearing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 1 | Stop & Emergency Valve | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 2 | Throttle Valves | Bearings | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 2 | Throttle Valves | Pivot Pins & Lock Pins
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 2 | Throttle Valves | Lift measurement & Valve freeness
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 3 | Turbine Casing | Casing to Pedestal alignment | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 3 | Turbine Casing | Casing fasteners bolts elongation check & retightening)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 3 | Turbine Casing | Casing joint line (Compound replacement)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 3 | Turbine Casing | Full assembly (External)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 4 | Relay with Governor | Worm wheel | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 4 | Relay with Governor | Bearing,springs, Sliping clutch.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 4 | Relay with Governor | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 5 | Over Load Valve | Spindles | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 5 | Over Load Valve | Guide box
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 5 | Over Load Valve | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 6 | Nozzle & Diaphragms | Nozzles (1st stage) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 6 | Nozzle & Diaphragms | Steam labyrinth packing (HP & LP)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 6 | Nozzle & Diaphragms | Steam labyrinth packing holders (HP & LP)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 6 | Nozzle & Diaphragms | Oil seal labyrinth packing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 7 | Rotor | Bearings | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 7 | Rotor | Rotor Shaft
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 7 | Rotor | Thrust Bearing Pads
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 7 | Rotor | HP & LP blades
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 8 | Overspeed Trip | Full assembly (Internal) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 8 | Overspeed Trip | Springs
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 9 | Exhaust Steam Relief Valve | Springs | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 9 | Exhaust Steam Relief Valve | Valve seat
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 10 | Gear Box | Alignment between Gear box & Drive Equipment | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 10 | Gear Box | Alignment between Turbine & Gear box
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 10 | Gear Box | Bearings Casing Fastener
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 10 | Gear Box | Gear & Gear wheel
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 10 | Gear Box | Pinion
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 10 | Gear Box | SSS Clutch ,Oil Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 10 | Gear Box | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 11 | Coupling (HS &LS) | Transmission Unit / Elements | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 11 | Coupling (HS &LS) | Shear pins
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 11 | Coupling (HS &LS) | Coupling bolt tightness check
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 12 | Main oil tank | Inspection & Cleaning | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 12 | Main oil tank | Tank's rust preventive coating
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 12 | Main oil tank | Suction strainers & Foot valves
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 13 | Filter | Filter element | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 13 | Filter | Filter Assembly
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 13 | Filter | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 14 | All Duties Valve | Full assembly | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | 14 | All Duties Valve | Valve and seat contact
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 1 | Stop & Emergency Valve | Blue contact between Valve & Seat | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 1 | Stop & Emergency Valve | Thrust Bearing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 1 | Stop & Emergency Valve | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 2 | Throttle Valves | Bearings | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 2 | Throttle Valves | Pivot Pins & Lock Pins
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 2 | Throttle Valves | Lift measurement & Valve freeness
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 3 | Turbine Casing | Casing to Pedestal alignment | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 3 | Turbine Casing | Casing fasteners bolts elongation check & retightening)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 3 | Turbine Casing | Casing joint line (Compound replacement)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 3 | Turbine Casing | Full assembly (External)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 4 | Relay with Governor | Worm wheel | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 4 | Relay with Governor | Bearing,springs, Sliping clutch.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 4 | Relay with Governor | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 5 | Over Load Valve | Spindles | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 5 | Over Load Valve | Guide box
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 5 | Over Load Valve | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 6 | Nozzle & Diaphragms | Nozzles (1st stage) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 6 | Nozzle & Diaphragms | Steam labyrinth packing (HP & LP)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 6 | Nozzle & Diaphragms | Steam labyrinth packing holders (HP & LP)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 6 | Nozzle & Diaphragms | Oil seal labyrinth packing
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 7 | Rotor | Bearings | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 7 | Rotor | Rotor Shaft
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 7 | Rotor | Thrust Bearing Pads
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 7 | Rotor | HP & LP blades
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 8 | Overspeed Trip | Full assembly (Internal) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 8 | Overspeed Trip | Springs
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 9 | Exhaust Steam Relief Valve | Springs | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 9 | Exhaust Steam Relief Valve | Valve seat
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 10 | Gear Box | Alignment between Gear box & Drive Equipment | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 10 | Gear Box | Alignment between Turbine & Gear box
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 10 | Gear Box | Bearings Casing Fastener
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 10 | Gear Box | Gear & Gear wheel
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 10 | Gear Box | Pinion
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 10 | Gear Box | SSS Clutch ,Oil Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 10 | Gear Box | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 11 | Coupling (HS &LS) | Transmission Unit / Elements | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 11 | Coupling (HS &LS) | Shear pins
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 11 | Coupling (HS &LS) | Coupling bolt tightness check
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 12 | Main oil tank | Inspection & Cleaning | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 12 | Main oil tank | Tank's rust preventive coating
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 12 | Main oil tank | Suction strainers & Foot valves
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 13 | Filter | Filter element | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 13 | Filter | Filter Assembly
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 13 | Filter | Gaskets, O−Rings & Seals
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 14 | All Duties Valve | Full assembly | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | 14 | All Duties Valve | Valve and seat contact
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 4 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | 9 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 4 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | 9 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 4 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | 9 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 4 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | 9 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 1 | Vibration Tx. | Remove all air accessories. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 1 | Vibration Tx. | Unscrew the bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 1 | Vibration Tx. | Check the screw adjustable point.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 1 | Vibration Tx. | Proper clean & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 2 | Pressure Tx. | Check cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 2 | Pressure Tx. | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 3 | RTD | Check damage rtd wire
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 3 | RTD | Check resistance power
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 4 | Indicator | Check power supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 4 | Indicator | Clean its conector ,fuse internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 5 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 5 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 5 | Electronic equipment | Veryfied calibration status.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 5 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 6 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | 6 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 1 | Visual Inspection | Remove all air accessories. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 1 | Visual Inspection | Sensor body free from cracks, dents, or corrosion
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 1 | Visual Inspection | Cable gland and connector secure
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 1 | Visual Inspection | Proper clean & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 2 | Pressure Tx. | Check cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 2 | Pressure Tx. | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 3 | Indicator | Check power supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 3 | Indicator | Clean its conector ,fuse internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 4 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 4 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 4 | Electronic equipment | Veryfied calibration status.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 5 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 6 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | 6 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 4 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 8 | Calibration | Calibration done after install at position. (0-100%)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | 9 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 1 | Electrode | Unscrew the Cylinder from body
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 1 | Electrode | Check the cylinder kit & Neck bush.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 1 | Electrode | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 2 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 2 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 2 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 3 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 3 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 4 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 5 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 5 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 8 | Brick Transmitter | Check & Calibrated
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 9 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | 11 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 1 | Electrode | Unscrew the Cylinder from body
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 1 | Electrode | Check the cylinder kit & Neck bush.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 1 | Electrode | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 2 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 2 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 2 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 3 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 3 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 4 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 5 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 5 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 8 | Brick Transmitter | Check & Calibrated
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 9 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | 11 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 8 | Electronic equipment | Veryfied calibration status.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 6 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 6 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 6 | Electronic equipment | Veryfied calibration status.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | 8 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 6 | Positioner | Check Relay ,cam,spring & kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 6 | Positioner | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 7 | Electronic Equipment | Verfied Calibration Status.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 8 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | 10 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 4 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 6 | Dome Switch/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 6 | Dome Switch/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 6 | Dome Switch/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 7 | Electronic Equipment | Verfied Calibration Status.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 8 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | 10 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 3 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 3 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 3 | Electronic Equipment | Verfied Calibration Status.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 4 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 4 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 5 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 6 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 6 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | 8 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 3 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 3 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 3 | Electronic Equipment | Verfied Calibration Status.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 4 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 4 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 5 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 6 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 6 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | 8 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 8 | Electronic equipment | Veryfied calibration status.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | 10 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 8 | Electroinc equipment | Check equipment condition & clean. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 8 | Electroinc equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 8 | Electroinc equipment | Veryfied calibration status.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | 10 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 8 | Electroinc equipment | Check equipment condition & clean. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 8 | Electroinc equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 8 | Electroinc equipment | Veryfied calibration status.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | 10 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 4 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 8 | Calibration | Calibration done after install at position. (0-100%)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | 9 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 4 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 8 | Calibration | Calibration done after install at position. (0-100%)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | 9 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 4 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 8 | Calibration | Calibration done after install at position. (0-100%)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | 9 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 4 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 8 | Calibration | Calibration done after install at position. (0-100%)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | 9 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 1 | Actuator | Unscrew the actuator from bracket
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 1 | Actuator | Check the actuator kit & adjustable spring.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 1 | Actuator | Proper lubricant & assembling all parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 2 | Body | Check physical condition. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 2 | Body | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 3 | Seat | Replace if any requirement
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 4 | Plug | Check leakage & Scaling condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 4 | Plug | Clean body surface for scaling and foreign particles.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 7 | A.F.R | Clean its air filter & internal parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 8 | Calibration | Calibration done after install at position. (0-100%)
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | 9 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | 1 | Sensor | Check its continuity end the conector.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | 2 | Power supply Card | check Its eatrhing voltage.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | 3 | Microprocessor Unit | Check its output signal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | 5 | Liner | Check its scaling. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | 5 | Liner | Check its any deformation parts.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | 7 | Monitoring Instruments | Check & clean physical condition.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | 1 | Check the Power & electronic card LED Indicator | Check all indicator. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | 3 | Check Connections | Periodically check all connections to the UPS system such as communication cables, terminal strips, sockets, plugs, field wiring, and electronic cards. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | 4 | Inspect the Overall Condition of the UPS Components | Visually inspect the UPS for wear, warping, distortion indications of overheated components like burnt odors or discoloration. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | 6 | Inspect the Cleanliness of your UPS | Check to Dust Removal | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | 6 | Inspect the Cleanliness of your UPS | Clean and Change Filters | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | 6 | Inspect the Cleanliness of your UPS | Maintain Ventilation | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | 1 | Check the Power & electronic card LED Indicator | Check all indicator. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | 3 | Check Connections | Periodically check all connections to the UPS system such as communication cables, terminal strips, sockets, plugs, field wiring, and electronic cards. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | 4 | Inspect the Overall Condition of the UPS Components | Visually inspect the UPS for wear, warping, distortion indications of overheated components like burnt odors or discoloration. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | 6 | Inspect the Cleanliness of your UPS | Check to Dust Removal | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | 6 | Inspect the Cleanliness of your UPS | Clean and Change Filters | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | 6 | Inspect the Cleanliness of your UPS | Maintain Ventilation | [5 empty] | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | 1 | Check the Power & electronic card LED Indicator | Check all indicator. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | 2 | Check the Operating Voltage and Current | Check all value. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | 3 | Check Connections | Periodically check all connections to the UPS system such as communication cables, terminal strips, sockets, plugs, field wiring, and electronic cards. |  |  |  | Yes |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | 4 | Inspect the Overall Condition of the UPS Components | Visually inspect the UPS for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | 6 | Inspect the Cleanliness of your UPS | Check to Dust Removal |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | 6 | Inspect the Cleanliness of your UPS | Clean and Change Filters |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | 6 | Inspect the Cleanliness of your UPS | Maintain Ventilation |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | 1 | Check the Power & electronic card LED Indicator | Check all indicator. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | 2 | Check the Operating Voltage and Current | Check all value. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | 3 | Check Connections | Periodically check all connections to the UPS system such as communication cables, terminal strips, sockets, plugs, field wiring, and electronic cards. |  |  |  | Yes |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | 4 | Inspect the Overall Condition of the UPS Components | Visually inspect the UPS for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | 6 | Inspect the Cleanliness of your UPS | Check to Dust Removal |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | 6 | Inspect the Cleanliness of your UPS | Clean and Change Filters |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | 6 | Inspect the Cleanliness of your UPS | Maintain Ventilation |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | 1 | Check the Power & electronic card LED Indicator | Check all indicator. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | 2 | Check the Operating Voltage and Current | Check all value. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | 3 | Check Connections | Periodically check all connections to the UPS system such as communication cables, terminal strips, sockets, plugs, field wiring, and electronic cards. |  |  |  | Yes |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | 4 | Inspect the Overall Condition of the UPS Components | Visually inspect the UPS for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | 6 | Inspect the Cleanliness of your UPS | Check to Dust Removal |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | 6 | Inspect the Cleanliness of your UPS | Clean and Change Filters |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | 6 | Inspect the Cleanliness of your UPS | Maintain Ventilation |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | 1 | Check the Power & electronic card LED Indicator | Check all indicator. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | 2 | Check the Operating Voltage and Current | Check all value. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | 3 | Check Connections | Periodically check all connections to the UPS system such as communication cables, terminal strips, sockets, plugs, field wiring, and electronic cards. |  |  |  | Yes |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | 4 | Inspect the Overall Condition of the UPS Components | Visually inspect the UPS for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | 6 | Inspect the Cleanliness of your UPS | Check to Dust Removal |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | 6 | Inspect the Cleanliness of your UPS | Clean and Change Filters |  | Yes |  |  |  | Yes
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | 6 | Inspect the Cleanliness of your UPS | Maintain Ventilation |  | Yes |  |  |  | Yes

## EQUIPMENT MAINTENANCE HISTORY
source file | sheet id | sheet name | EQUIPMENT TAG NO | Season / OFF Season | Year | Date of Start | Date of Finish | Outage/ Observation | Action Taken | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2021-02-08 |  |  | Throttle valve seat found damage. | Throttle valve & seat replace.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2022-01-08 |  |  | Found oil Seal , Bearing clearance High. | Replace with new oil seal & Bearing..
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2023-12-09 |  |  | Found Gear coupling teeth damage. | Replace Gear coupling with new.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2024-05-30 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasketfound damage | Gland Packing and Joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2024-05-26 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2024-05-18 |  |  | 3Nos. Oil Cooler Inlet and Outlet side joint found damage | 3Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2024-09-04 |  |  | 45GPM Oil Filter element Found Choked | 45GPM Oil Filter element Replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2024-09-18 |  |  | Emergency Valve 8Nos. Stud Found worn out | Emergency Valve 8Nos. Stud replaced by new |  | External
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2024-10-17 |  |  | Oil chamber lubrication oil servo prime 68/HP | Oil chamber lubrication oil servo prime 68/HP new oil filling in oil chamber |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2025-05-23 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found damage | Gland Packing and Joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2025-04-22 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2025-07-10 |  |  | Main oil pump bushes 4Nos. Found wear out | Main Oil Pump 4Nos. Bushes replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2025-07-05 |  |  | Bottom Casing Diaphragm 3Nos Screw found damage | Bottom Casing Diaphragm 3 nos. Screw replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2025-08-18 |  |  | Oil Cooler Nos.1,2 tubes total 396 Nos. tubes found leaked | Oil Cooler Nos.1,2 tubes total 396 nos. tubes Retubing work done |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2025-08-13 |  |  | Turbine , Oil Cooler, Water Valves,Padstal bearing cover found dirty | Turbine , Oil Cooler, Water Valves,Oil Cooler,Padstal bearing cover Cleaning and painting work done |  | External
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Season | 2026-01-29 |  |  | 3 mw old main exhaust steam valve steam nut broken | old steam watch then new threded in workshop after that fitted in position |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 | Off- Season | 2026-07-16 |  |  | Turbine , Oil Cooler, Water Valves,Padstal bearing cover found dirty | Realy Cylinder oil seal-01 nos.old steam watch then new threded in workshop after that fitted in position |  | External
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | ee2949ed1129 | TURBINE :: POWER TURBINE | ZIL/SUG/01 |  | Mechanic |  |  |  | Sec .Engineer |  | Sec. Head |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2021-08-07 |  |  | Throttle valve seat found damage. | Throttle valve & seat replace.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2022-01-08 |  |  | Found Gear coupling teeth damage. | Replace gear coupling with new.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2023-07-08 |  |  | Turbine rotter blade worn-out & Diphragm Nozzle worn-out. | Turbine rotter blade replace,inter stage labyrinth under size & diphragm replaced. |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2024-05-27 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found damage | Gland Packing and Joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2024-05-29 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2024-05-16 |  |  | 2Nos. Oil Cooler Inlet and Outlet side joint found damage | 2Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2024-08-01 |  |  | Casing 1st stage Top&Bottom Diaphragm blades found cracked and worn out | Casing 1st stage Top&Bottom Diaphragm Replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2024-09-30 |  |  | 45GPM Oil Filter Found Chocked | 45GPM Oil Filter Replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2024-10-01 |  |  | Atlernator D.E Side Top Bottom Bearing 6nos litting pad clearnace found high | Alternator D.E Side Top Bottom Bearing 6Nos. Litting pad replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2024-10-21 |  |  | Main lube oil line oil filter 8G.P.M found chocked | Main lube oil line oil filter 8G.P.M replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2024-10-22 |  |  | 1Nos Trap Valve found malfunctioned | 1Nos Trap Valve replaced by new |  | External
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2025-05-24 |  |  | 2Nos. Oil Cooler Inlet and Outlet side gasket found damage | 3Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2025-05-26 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found Wornout | Gland Packing and Joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2025-05-24 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found wornout | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2025-07-02 |  |  | 1Nos.Relay Oil Seal found wornout | 1Nos. Relay Oil Seal replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2025-07-10 |  |  | Alternator D.E Side padstal bearing(tittling pad) found chipout | Alternator D.E Side padstal bearing(tittling pad) replaced by remettled bearing |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2025-07-30 |  |  | 1Nos Throttle valve O/L drain valve spindle found bend | 1Nos Throttle valve O/L drain valve replaced by new |  | External
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2025-07-10 |  |  | 1Nos. Oil Baffle found leaked | 1Nos. Oil Baffle Replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2025-08-14 |  |  | Turbine , Oil Cooler, Water Valves,Padstal bearing cover found dirty | Turbine , Oil Cooler, Water Valves,Oil Cooler,Padstal bearing cover Cleaning and painting work done |  | External
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4a14e1694ed7 | TURBINE :: POWER TURBINE | ZIL/SUG/02 | Off- Season | 2026-07-11 |  |  | Turbine , Oil Cooler, Water Valves,Padstal bearing cover found dirty | Alt.Padastal bering drive side-1 set,leaf spring-Turbine , Oil Cooler, Water Valves,Oil Cooler,Padstal bearing cover Cleaning and painting work done Sec .Engineer |  | External
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 18/8/2021 |  |  | Turbine governor 2 Nos weight bearing (629ZZ) damage. | Bearing replace with new. |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 25/8/2022 |  |  | Gear Box Bearing & Pinion Thrust bearing damage. | Both bearing Change with new. |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 20/8/2023 |  |  | Turbine governor 4 Nos weight bearing (629ZZ) damage. | Bearing replace with new. |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2024-05-06 |  |  | 2Nos. Oil Cooler Inlet and Outlet side gasket found damage | 2Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2024-06-26 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found damage | Gland Packing and Joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2024-06-05 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2024-06-28 |  |  | Turbine Governor 07Nos.Weight bearing,2Nos.Needle Roller Bearing,3Split Pin found damage | Turbine Governor 07Nos.Weight bearing,2Nos.Needle Roller Bearing,3Split Pin replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2024-09-04 |  |  | 45GPM Oil Filter Found Chocked | 45GPM Oil Filter Replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2024-10-19 |  |  | 1Nos. Steam drain valve found malfunctioned | 1Nos. Steam drain valve replaced by new
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2024-10-19 |  |  | 1Nos. Trap valve found malfunctioned | 1Nos. Trap valve replaced by new
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2024-10-22 |  |  | Oil chamber lubrication oil servo prime 68/HP | Oil chamber lubrication oil servo prime 68/HP 3M.W Old turbine old oil refilling done in oil chamber
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2025-05-21 |  |  | 2Nos. Oil Cooler Inlet and Outlet side gasket found damage | 3Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal | Sarwan Tiwari
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2025-05-30 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found damage | Gland Packing and Joint replaced by new |  | Internal | Anku Yadav
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2025-05-15 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal | Sarwan Tiwari
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2025-07-02 |  |  | 1Nos Pinion Plain Bearing found chipout | 1Nos Pinion Plain Bearing replaced by new |  | Internal | Kishore Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2025-07-03 |  |  | 4Nos rotor fore bearing stud found thread found wearout | 4Nos rotor fore bearing stud replaced by new
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2025-05-08 |  |  | Governor 8 Nos weight bearing (629ZZ),2Nos Needle roller bearing,1Nos Race Carrier,1Nos 7205 bearing ,1nos. Fulcrum pin, 4Nos. Split pin found wornout | Governor 8 Nos weight bearing (629ZZ),2Nos Needle roller bearing,1Nos Race Carrier,1Nos 7205 bearing replaced by new |  | Internal | Sarwan Tiwari
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2025-08-08 |  |  | Turbine ,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler found dirty | Turbine ,,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler Cleaning and painting work done |  | External | Kishore Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Season | 2025-10-29 |  |  | throtle valve opening less then as required | throttle valve opening setting increase 18.5 mm to 20 mm
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e686217c3a8a | TURBINE :: Mill turbine-01 | ZIL/SUG/03 | Off- Season | 2026-07-02 |  |  | Turbine ,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler found dirty | Turbine ,,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler Cleaning and painting work done Rotor active side .5 sim replace at .1 & throtal valve spendal 02 nos nut fitting work done Sec .Engineer |  |  |  | Governor 06 Nos weight bearing replaced with new , weight Pin 03 nos. Adj washer-02 nos ,niddle Roler bearing-02 nos.
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 25/8/2021 |  |  | Turbine governor 2 Nos weight bearing (629ZZ) damage. Oil seal leakage, Turbine gear box bearing replace work. | Gear box Bearing, Governor bearing & Pinion thrust bearing replace with new. Oil seal modified & replaced with new. |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 17/8/2022 |  |  | Turbine governor 2 Nos weight bearing (629ZZ) damage. Pinion bearing,Oil seal leakage, Turbine gear box bearing replace & aligment work. | Gear box Bearing, Governor bearing & Pinion thrust bearing replace with new. Oil seal modified & replaced with new. |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 17/8/2023 |  |  | LP & HP side steam labyrinth modified & replaced. | Labyrinth replaced with new. |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2024-05-07 |  |  | 2Nos. Oil Cooler Inlet and Outlet side joint found damage | 2Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2024-06-11 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found damage | Gland Packing and Joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2024-06-07 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2024-08-11 |  |  | Turbine Rotor fore bearing top&bottom found damage and fore bearing cover stud found wornout | Turbine Rotor fore bearing top&bottom and fore bearing cover stud replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2024-09-12 |  |  | Turbine Governor 1Nos.Race carrier and1Nos. Race carrier bearing ,4Nos. Governor weight, 08Nos.Weight bearing,2Nos.Needle Roller Bearing,2Nos.Split Pin found damage | Turbine Governor 1Nos.Race carrier and1Nos. Race carrier bearing,4Nos. Governor weight, 08Nos.Weight bearing,2Nos.Needle Roller Bearing,2 Nos.Split Pin replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2024-10-22 |  |  | Oil chamber lubrication oil servo prime 68/HP | Oil chamber lubrication oil servo prime 68/HP 3M.W Old turbine old oil refilling done in oil chamber |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2024-10-23 |  |  | ZWICKY Valve Size 24mm found worn out | ZWICKY Valve Size 24mm replaced by new
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2025-05-21 |  |  | 2Nos. Oil Cooler Inlet and Outlet side gasket found damage | 2Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2025-05-28 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found damage | Gland Packing and Joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2025-05-31 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2025-07-05 |  |  | 1Nos Rotor Plain Bearing found chipout | 1Nos Rotor Plain Bearing replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2025-07-07 |  |  | Mop 4Nos. Bushes found wear out | Mop 4Nos. Bushes replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2025-07-04 |  |  | 1Nos Interstage lock screw found wearout | 1Nos Interstage lock screw replaced by New |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2025-05-09 |  |  | Governor 8 Nos weight bearing (629ZZ),2Nos Needle roller bearing,,1Nos 7205 bearing,2Nos Fulcrum pin,3Nos Split pin found wornout | Governor 8 Nos weight bearing (629ZZ),2Nos Needle roller bearing,1Nos 7205,2Nos Fulcrum pin,3Nos Split pin bearing replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2025-08-06 |  |  | Turbine ,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler found dirty | Turbine ,,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler Cleaning and painting work done |  | External
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 5794dba376d9 | TURBINE :: Mill turbine-02 | ZIL/SUG/04 | Off- Season | 2025-07-24 |  |  | Turbine ,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler found dirty | Governor 8 Nos weight bearing,niddle Roler bearing-02, Roter 1 & 2 ,Gear 1 & 2 bearing,race cariar & race cariar bearing-1 nos.Fulkaran pin-04 nos.throtal valve-01 nos. oil feed conection-01 nos. replaced with new,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler Cleaning and painting work done Sec .Engineer |  | External
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Off- Season | 25/8/2021 |  |  | Turbine governor 2 Nos weight bearing (629ZZ) damage. Oil seal leakage, Turbine gear box bearing replace work. | Gear box Bearing, Governor bearing & Pinion thrust bearing replace with new. Oil seal modified & replaced with new. |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Off- Season | 17/8/2022 |  |  | Turbine governor 2 Nos weight bearing (629ZZ) damage. Pinion bearing, Oil seal leakage, Turbine gear box bearing replace & aligment work. | Gear box Bearing, Governor bearing & Pinion thrust bearing replace with new. Oil seal modified & replaced with new. |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Season | 2022-08-12 |  |  | High speed coupling Change. | Change with new . |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Off- Season | 17/8/2023 |  |  | LP & HP side steam labyrinth modified & replaced. | Labyrinth replaced with new. |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Off- Season | 2024-05-11 |  |  | 2Nos. Oil Cooler Inlet and Outlet side joint found damage | 2Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Off- Season | 2024-09-10 |  |  | Turbine Governor 1Nos.Race carrier bearing 07Nos.Weight bearing,2Nos.Needle Roller Bearing,2Nos.Split Pin ,2Nos.weight pin found damage | Turbine Governor and 1Nos.Race carrier bearing,4Nos. Governor weight, 08Nos.Weight bearing,2Nos.Needle Roller Bearing,2 Nos.Split Pin 2Nos.weight pin replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Off- Season | 2024-09-18 |  |  | 45GPM Oil Filter Element found chocked | 45GPM Oil Filter Element replaced by new
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Off- Season | 2025-05-21 |  |  | 2Nos. Oil Cooler Inlet and Outlet side gasket found damage | 2Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Off- Season | 2025-05-25 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found damage | Gland Packing and Joint replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Off- Season | 2025-05-30 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Off- Season | 2025-08-08 |  |  | Turbine ,,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler found dirty | Turbine ,,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler Cleaning and painting work done |  | External
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Off- Season | 2025-10-14 |  |  | Oil filter chocked | Oil filter Replaced 01 nos. |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | season | 2025-11-12 |  |  | turbine tripped due to vibration,high speed coupling leaf spring broken may be abnormal load or jerk load | Replace high speed coupling |  | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 543ec787bb43 | TURBINE :: Mill turbine-03 | ZIL/SUG/05 | Off- Season | 2026-07-28 |  |  | Turbine ,,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler found dirty | Rotor 1st bearing Pinion 1 & 2 ,Gear 1st bearing,governor 8 nos. weight bearing,fulkaran pin-04 nos.nidill rolar -02 nos. ,race cariar & Race cariar bearing-1 nos., Gov. weight 04 nos. cashing stud & Nut 01 nos. , oil feed conection-01 nos., drain valve-01 nos.lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler Cleaning and painting work done Sec .Engineer |  | External
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | OFF Season | 28.06.2022 |  |  | Control valve found scaled and rusty.SOV,dome switch AFR ok | Proper cleaning & overhauling ,checking painting. |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | OFF Season | 24.06.2023 |  |  | Control valve found scaled and rusty. | Proper cleaning & overhauling , checking painting. |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | OFF Season | 08.05.2024 |  |  | Control valve found scaled and liekage,Dome switch out of order .AFR & SOV ok | Proper cleaning & overhauling , dome switch checking work done. with Valve painting. | 180 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | OFF Season | 11.12.2024 |  |  | Rotary Vale actuator prpblem | Repair it |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | OFF Season | 12.08.2025 |  |  | Control valve found seat scaled and liekage AFR,SOV ok | Proper cleaning & Seat replaced with new dome switch checking work done. with painting. | 170 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | OFF Season | 29.04.2026 |  |  | Control valve found seat scaled AFR,SOV ok | Proper Actuator & Seat SOV dome switch overhauling checking work done. | 250 | Internal | Anuj / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0338168a0c42 | Mill-16 :: Control valve | ZIL/SUG./006 (XV_RJ2_SOV2) | Technician | [7 empty] | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | OFF Season | 25.07.2022 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting. |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | OFF Season | 28.06.2023 |  |  | Control valve found scaled and liekage rusty. | Proper cleaning ,overhauling with seat replaced with new & painting. |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | OFF Season | 09.05.2024 |  |  | Control valve found scaled and Dome switch .AFR & SOV ok | Proper cleaning & overhauling , dome switch checking work done. with Valve painting. | 90 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | OFF Season | 13.08.2025 |  |  | Control valve found seat worn-out actuator air passing | Actuator & seat replaced with new | 16500 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | OFF Season | 30.04.2026 |  |  | Control valve found seat scaled AFR,SOV ok | Proper Actuator & Seat SOV dome switch overhauling checking work done. | 250 | Internal | Anuj / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 333534806482 | Mill-16 :: Control valve | ZIL/SUG./007 (XV_RJ2_SOV2) | Technician | [7 empty] | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | OFF Season | 26.07.2022 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting. | 100 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | OFF Season | 28.06.2023 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting. | 100 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | OFF Season | 09.05.2024 |  |  | Control valve found scaled and Dome switch .AFR & SOV ok | Proper cleaning & overhauling , dome switch checking work done. with Valve painting. | 150 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | OFF Season | 14.08.2025 |  |  | Control valve found seat scaled and liekage AFR,SOV ok | Proper cleaning & Seat replaced with new dome switch checking work done. with painting. | 170 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | OFF Season | 30.04.2026 |  |  | Control valve found seat scaled AFR,SOV ok | Proper Actuator & Seat SOV dome switch overhauling checking work done. | 250 | Internal | Anuj / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a73aa53887f2 | Mill-16 :: Control valve | ZIL/SUG./008 (XV_RJ2_SOV3) | Technician | [7 empty] | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | OFF Season | 17.09.2022 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting. | 100 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | OFF Season | 29.06.2023 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting. | 100 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | OFF Season | 10.05.2024 |  |  | Control valve found scaled and Dome switch .AFR & SOV ok | Proper cleaning & overhauling , dome switch checking work done. with Valve painting. | 100 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | OFF Season | 14.08.2025 |  |  | Control valve found seat worn-out actuator air passing | Actuator & seat replaced with new | 16500 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | OFF Season | 30.04.2026 |  |  | Control valve found seat scaled AFR,SOV ok | Proper Actuator & Seat SOV dome switch overhauling checking work done. | 250 | Internal | Anuj / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 819ff4051ef6 | Mill-16 :: Control valve | ZIL/SUG./009 (XV_RJ2_SOV3) | Technician | [7 empty] | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | OFF Season | 27.07.2022 |  |  | Installation of new instrument | Due to shreder Vibration Monitoring system |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | OFF Season | 29.06.2023 |  |  | Remove all Tx & clean it | Calibration checking work are done. |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | OFF Season | 10.05.2024 |  |  | Remove all Tx & clean it | Calibration checking work are done. |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | Season | 2025-01-01 |  |  | Srd Belt Magnet temp. indicatar out of order | Replaced with new take in line. |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | Season | 2026-01-21 |  |  | temp. sensor false reading | Replaced with new take in line. | 1800 | Internal
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7bb58a2ff37f | Mill-16 :: Shreder -2 | ZIL/SUG./016 (VIB103,VIB104,VIB105) | Technician | [7 empty] | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | Off-Season | 2025-09-29 |  |  | New equipment | pressure transmitter installation work done |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c8c7f86779b1 | Mill-16 :: Cane Carrier Pressure transmitter | ZIL/SUG./017 ( PI_502) | Technician | [7 empty] | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | OFF Season | 11.06.2022 |  |  | Control valve found scaled and rusty. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. |  | Internal | A Varma / V singh | Seat replaced with new
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | OFF Season | 26.06.2023 |  |  | Control valve found scaled and rusty & seat is damage | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting seat replaced with new. |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | OFF Season | 03.07.2024 |  |  | Control valve found scaled and rusty,AFR,Positioner Ok. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking work done. | 100 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | OFF Season | 09.07.2025 |  |  | Control valve found scaled and rusty. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting work are done. | 200 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | OFF Season | 06.06.2026 |  |  | Control valve found scaled and rusty. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking work are done. | 200 | Internal | Anuj kr. / V singh | Gide pad worn-out 30%
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 323dbc8cf2bf | RJH-21-27 :: Control valve | ZIL/SUG./016/01/D_SWEET | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | OFF Season | 25.05.2022 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | OFF Season | 05.08.2023 |  |  | Control valve found C light scaling and rusty.Electrode o-ring,seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode o ring,seat replaced with new | 250 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | OFF Season | 05.08.2024 |  |  | Control valve found C light scaling and rusty.Electrode cylinder seal kit damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode cylinder seal kit replaced with new | 685 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | OFF Season | 05.06.2025 |  |  | Control valve found C light scaling and rustry | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are. | 250 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | OFF Season | 11.09.2025 |  |  | Brick transmitter with electrode replaced with new | Spare Sensor absulit in market | 81500 | External | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | OFF Season | 22.04.2026 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24c2390b4b9d | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-05 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | OFF Season | 19.05.2022 |  |  | Control valve found C light scaling and seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. | 150 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | OFF Season | 07.08.2023 |  |  | Control valve found C light scaling and rusty.Electrode o-ring damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done.electrode o ring replaced with new | 200 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | OFF Season | 10.06.2024 |  |  | Control valve found scaling and rusty.Electrode cylinder seal kit damage actuator worn-out. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode cylinder seal kit & actuator replaced with new | 4860 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | OFF Season | 05.06.2025 |  |  | Control valve found C light scaling and rustry | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. | 250 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | OFF Season | 11.09.2025 |  |  | Brick transmitter with electrode replaced with new | Spare Sensor absulit in market | 81500 | External | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | OFF Season | 22.04.2026 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7960222b9717 | B COUNTI.PAN 27-65 :: Control valve | ZIL/SUG./B.COMP-CT-06 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | OFF Season | 21.05.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | OFF Season | 09.06.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | OFF Season | 17.06.2024 |  |  | Control valve Condiction syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & Overhauling work done. | 150 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | Season | 17.03.2025 |  |  | Brix Tx display problem | Repair to third party |  | External | Sushil / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | OFF Season | 27.05.2025 |  |  | Control valve found syrup scaling and rusty. | Seat,Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning Overhauling work done. | 250 | Internal | A Varma / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | OFF Season | 15.05.2026 |  |  | Control valve found scaled and rusty.AFR & Positioner found ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, work are done. | 250 | Internal | Anuj Kr. / V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 3535ab959303 | RAW FEED VALVE-33 :: Control valve | ZIL/SUG./028 (11.BCV.030.B01) | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | OFF Season | 2023-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | OFF Season | 2024-08-18 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | OFF Season | 2025-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | OFF Season | 2026-07-25 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor with gland & conection tighting work are done. | 150 | Internal | Anuj kumar srivastava
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | f8589e108b99 | FLOW METER :: Flow Meter | ZIL/SUG./01/22FT220B01 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | OFF Season | 2023-06-10 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | OFF Season | 2024-08-28 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | OFF Season | 2025-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | OFF Season | 2026-08-08 |  |  | Flow tube found Scale full.transmiter mounting screw was found damage. | Clean its Liner & Sensor with gland & conection tighting work are done. | 150 | Internal | Anuj kumar srivastava
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4584773fa72a | FLOW METER :: Flow meter | ZIL/SUG./01/16.FT.075.B01 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | OFF Season | 2023-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | OFF Season | 2024-07-22 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 009b63c1200e | FLOW METER :: Flow meter | ZIL/SUG./01/36-BLOCK-TWL | OFF Season | 2025-07-13 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | OFF Season | 2023-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | OFF Season | 2024-07-22 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | OFF Season | 2025-07-13 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8df8daf03ecf | FLOW METER :: Flow meter | ZIL/SUG./01/SCUM-FM | OFF Season | 2026-07-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor with gland & conection tighting work are done. | 250 | Internal | Mr Anuj srivastava
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | OFF Season | 2023-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | OFF Season | 2024-07-22 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | OFF Season | 2025-07-13 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4847377faae6 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FINAL | OFF Season | 2026-07-23 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor with gland & conection tighting work are done. | 250 | Internal | Mr Anuj srivastava
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | OFF Season | 2023-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | OFF Season | 2024-07-22 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | OFF Season | 2025-07-13 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 257f64ce90fa | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SYRUP | OFF Season | 2026-07-24 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor with gland & conection tighting work are done. | 250 | Internal | Mr Anuj srivastava
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | OFF Season | 2023-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | OFF Season | 2024-07-22 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | OFF Season | 2025-07-13 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1c07114f164e | FLOW METER :: Flow meter | ZIL/SUG./01/FT-FILTRATE | OFF Season | 2026-07-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor with gland & conection tighting work are done. | 250 | Internal | Mr Anuj srivastava
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | OFF Season | 2023-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | OFF Season | 2024-07-22 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | OFF Season | 2025-07-13 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 24df327cc482 | FLOW METER :: Flow meter | ZIL/SUG./01/FT-SCUM-DE-SWEET | OFF Season | 2026-07-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor with gland & conection tighting work are done. | 250 | Internal | Mr Anuj srivastava
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | OFF Season | 2022-08-07 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | OFF Season | 2023-07-18 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | OFF Season | 2024-05-14 |  |  | Control valve found scaled and rusty. | Proper cleaning & overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | OFF Season | 2025-06-20 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | OFF Season | 2026-04-23 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning & overhauling with checking work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03f504a9eecf | VRL 24-53 :: Control valve | ZIL/SUG./001/SY_B_MOL_CV2 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 8279d1c2b53d | Weingh-54-65 :: Control valve | ZIL/SUG./DECANTER-2/CV-1 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | OFF Season | 2022-06-23 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | OFF Season | 2023-07-20 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | OFF Season | 2024-07-24 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | OFF Season | 2025-07-16 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 200 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | OFF Season | 2026-08-11 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 150 | Internal | Mr Anirudh / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | e6137a7f74de | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS_EX_FLOW | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | OFF Season | 2022-06-23 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | OFF Season | 2023-07-20 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | OFF Season | 2024-07-25 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | OFF Season | 2025-07-16 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | OFF Season | 2026-08-11 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 150 | Internal | Mr Anirudh / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | OFF Season | 2026-08-11 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 150 | Internal | Mr Anirudh / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 34eaba65875f | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-201 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | OFF Season | 2022-06-23 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | OFF Season | 2023-07-20 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | OFF Season | 2024-07-26 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | OFF Season | 2025-07-12 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | OFF Season | 2026-08-07 |  |  | Tube, gland & connection found OK | Tube cleaning, conection checking work is completed. | 150 | Internal | Mr Anirudh / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 517a5ea87f25 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DS/FT-203 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | OFF Season | 2022-06-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | OFF Season | 2023-07-21 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | OFF Season | 2024-07-22 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | OFF Season | 2025-07-18 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | OFF Season | 2026-08-04 |  |  | Tube, gland & connection found OK | Tube cleaning, conection checking work is completed. | 150 | Internal | Mr Anirudh / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 4e7972449bf4 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/Vacuum-FM-01 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | OFF Season | 2022-06-28 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | OFF Season | 2022-07-25 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | OFF Season | 2024-08-29 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | OFF Season | 2026-08-10 |  |  | Tube, gland & connection found OK | Tube cleaning, conection checking work is completed. | 150 | Internal | Mr Anirudh / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 48c0393cc9b3 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/DIST.-TWFM-2 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | OFF Season | 2026-08-01 |  |  | Tube, gland & connection found OK | Tube cleaning, conection checking work is completed. | 150 | Internal | Mr Anirudh / Mr V.Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | c3e9937b8485 | DS Flow Meter-31 :: Flow Meter | ZIL/SUG./01/ETP-DECANTER-FM | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) | OFF Season | 2022-05-06 |  |  | Control valve Body found rusty and valve seat worn-out.AFR & Positioner Gauge found Damage. | Proper cleaning, Painting , valve seat & gauge replace with new. |  |  | Mr. Ritesh / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) | OFF Season | 2023-06-13 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) | OFF Season | 2024-05-06 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) | OFF Season | 2025-05-05 |  |  | Control valve Seat & body found rusty. Actuator surface worn-out with O ring set damage. | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 1600 | Internal | Mr. Anuj Kr / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) | OFF Season | 2026-04-23 |  |  | Control valve Seat & body found rusty. | Actuator ,Gear ,Valve seat Proper cleaning Overhauling ,Painting & Lubrication work with checking workdone. | 250 | Internal | Mr. Anuj kr / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 7950b69d04a3 | D.B.F 14 :: Control valve | ZIL/SUG./001 (40FCV201) | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) | OFF Season | 14/07/2022 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) | OFF Season | 21/07/2023 |  |  | Control valve Seat & Body found rusty .AFR diaphragm found damage & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. AFR Damage part replace with new |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) | OFF Season | 2024-06-23 |  |  | Control valve Seat & Body found rusty .AFR diaphragm found damage & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. AFR Damage part replace with new | 150 | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) | OFF Season | 2025-06-01 |  |  | Control valve Seat & Body found rusty .AFR diaphragm found damage & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. AFR Damage part replace with new | 200 | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a57da8dfe7d0 | Ground floor 19 :: Control valve | ZIL/SUG./001 (FCV 201) | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD | OFF Season | 21/07/2023 |  |  | Control valve Seat & Body found rusty .AFR diaphragm found damage. | Proper cleaning, Painting & Lubrication work done. AFR Damage part replace with new |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD | OFF Season | 2024-06-23 |  |  | Control valve Seat & Body found rusty .AFR diaphragm found damage. | Proper cleaning, Painting & Lubrication work done. AFR Damage part replace with new | 150 | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD | OFF Season | 2025-06-01 |  |  | Control valve Seat & Body found rusty .AFR diaphragm found damage. | Proper cleaning, Painting & Lubrication work done. AFR Damage part replace with new | 200 | Internal | Mr. Anuj / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1e06c2215910 | Ground floor 19 :: Control valve | ZIL/SUG./001 TWC_CMD | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | OFF Season | 13/07/2022 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | OFF Season | 2023-05-06 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | OFF Season | 2024-06-27 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning,Checking ,Painting & Lubrication work done. | 200 | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | OFF Season | 2025-06-03 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning,Checking Painting & Lubrication work done. | 200 | Internal | Mr. Anirudh / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | OFF Season | 2026-05-13 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning,Checking Painting & Lubrication work done.joint seat replaced | 200 | Internal | Mr. Sushil / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 904dbc43d424 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.030 B01) | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | OFF Season | 14/07/2022 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | OFF Season | 2023-06-06 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | OFF Season | 2024-06-27 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. | 200 | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | OFF Season | 2025-06-03 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning,Checking Painting & Lubrication work done. | 200 | Internal | Mr. Anirudh / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | OFF Season | 2026-05-13 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning,Checking Painting & Lubrication work done.joint seat replaced | 200 | Internal | Mr. Sushil / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 0dc553592aaf | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV 020B01) | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | OFF Season | 15/07/2022 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning,Checking Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | OFF Season | 2023-07-06 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning,Checking Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | OFF Season | 2024-06-27 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning,Checking Painting & Lubrication work done. | 200 | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | OFF Season | 2025-06-04 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning,Checking Painting & Lubrication work done. | 200 | Internal | Mr. Anirudh / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | Season | 2025-11-09 |  |  | Rotary Valve leakage | Replaced with new | 600 | Internal | Mr. Anuj Kr. / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | OFF Season | 2026-05-13 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning,Checking Painting & Lubrication work done.joint seat replaced | 200 | Internal | Mr. Sushil / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9047c11458f6 | Pan Feed Valve 3 :: Control valve | ZIL/SUG./001 (17 BCV.010B01) | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | OFF Season | 2022-04-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning, & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | OFF Season | 2023-08-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning, & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | OFF Season | 2024-05-12 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 150 | Internal | Mr. A Varma / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | OFF Season | 2025-04-25 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 150 | Internal | Mr. A Varma / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | OFF Season | 2026-07-18 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. Anuj kr. / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | cb921432e0d1 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022 XV 023B01) | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | OFF Season | 2022-05-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | OFF Season | 2023-08-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | OFF Season | 2024-05-16 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. |  | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | OFF Season | 2025-04-29 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | OFF Season | 2026-07-21 |  |  | Actuator pinion,bottom & top side ,Soft -oring found worn-out. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done.Actuator -o-ring replace with new. | 2265 | Internal | Mr. A Varma / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2ffb61c28344 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B05) | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | OFF Season | 24/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | OFF Season | 17/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV Found healthy & Dome Switch Not working.. | Proper cleaning & Lubrication work done. Dome switch change with new. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | OFF Season | 2024-05-17 |  |  | Control valve Seat & Body found rusty .AFR,SOV Found healthy .AFR gauge Found wornout. | Proper cleaning & Lubrication work done. AFR gauge replace with new. | 250 | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | OFF Season | 2025-04-29 |  |  | Control valve Seat & body found rusty. Seat found worn-out 80%,found 02 nos Spring damage. | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new.Dome switch repair work done. | 13500 | Internal | Mr. A Varma / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | OFF Season | 2026-06-19 |  |  | Control valve Seat & Body found 20% worn-out.AFR,SOV & Dome Switch found Healthy. Nos-01 spring damage. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done.nos-01 spring replace with new. | 1500 | Internal | Mr.Sushil singh / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 79b8f75b04d0 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B01) | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | OFF Season | 25/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | OFF Season | 18/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | OFF Season | 2024-05-18 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | OFF Season | 2025-04-28 |  |  | Control valve Seat & body found rusty. Seat found worn-out 80%, | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new.Dome switch repair work done. | 12500 | Internal | Mr. A Varma / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | OFF Season | 2026-06-19 |  |  | Control valve Seat & Body found 20% worn-out.AFR,SOV & Dome Switch found Healthy. Nos-02 spring damage. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done.Valve seat repairednos-01 spring replace with new. | 1500 | Internal | Mr.Sushil singh / Mr. V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 03ffdf69e4f6 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B02) | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | OFF Season | 25/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | OFF Season | 18/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | OFF Season | 2024-05-18 |  |  | Control valve Seat found wornout & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Replaced Control Valve seat with new spare. Proper cleaning & Lubrication work done. |  | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | OFF Season | 2025-04-26 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | OFF Season | 2026-06-19 |  |  | Control valve Seat & Body found worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done.Valve seat repaired. |  | Internal | Mr.Sushil singh / Mr. V singh | New Seat
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 98591a067f85 | Ref. Condensor 57 :: Control valve | ZIL/SUG./001 (022XV020B03) | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | OFF Season | 2023-06-28 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | OFF Season | 2024-07-31 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | OFF Season | 2025-06-18 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 9886032b2344 | Ref Flow Meter h :: FLOW METER | ZIL/SUG./01/22FT230B01 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | OFF Season | 2023-06-29 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | OFF Season | 2024-08-07 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | OFF Season | 2025-06-20 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 1b40caeb3a99 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-201 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | OFF Season | 2023-06-29 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | OFF Season | 2024-08-08 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | OFF Season | 2025-06-20 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | b3fe6af92e53 | Ref Flow Meter h :: Flow Meter | ZIL/SUG./01/FT-203 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | OFF Season | 2023-08-18 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | OFF Season | 2024-01-17 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | OFF Season | 2024-05-07 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | Season | 2025-01-28 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | Season | 2025-02-25 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & all parameter check & battery voltage checking work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | OFF Season | 2025-04-12 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | OFF Season | 2025-04-12 |  |  | Ups found healthy. | 25 kva ups separate battery bank take in line. | 617700 | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | Season | 2025-12-03 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | OFF Season | 2026-04-10 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 823aa812ca08 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-RAW | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | OFF Season | 2023-08-18 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | OFF Season | 2024-01-17 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | OFF Season | 2024-05-07 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | Season | 2025-01-28 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | Season | 2025-02-25 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & all parameter check & battery voltage checking work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | OFF Season | 2025-04-12 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | Season | 2025-12-03 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | OFF Season | 2026-04-10 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a5d4824f484a | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-RAW | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | OFF Season | 2023-08-18 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | OFF Season | 2024-01-17 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | OFF Season | 2024-05-07 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | Season | 2025-01-28 |  |  | Buck Boost section driver Red indication during power failure system not shift load on battery due to Driver board (1267DB-2) faulty. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed.Driver board (1267DB-2) replace with new one. Now both UPS checked working healthy condition mains & battery mode. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | OFF Season | 2025-04-12 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | Season | 2025-12-03 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | OFF Season | 2026-04-11 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 2cd136de0dc0 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-REFINERY | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | OFF Season | 2023-08-18 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | OFF Season | 2024-01-17 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | OFF Season | 2024-05-08 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | Season | 2025-01-28 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | OFF Season | 2025-04-12 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | Season | 2025-12-03 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | OFF Season | 2026-04-10 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | 436cc6ac16a2 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-REFINERY | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | OFF Season | 2023-08-18 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | OFF Season | 2024-01-17 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | OFF Season | 2024-05-08 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | Season | 2025-01-28 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | OFF Season | 2025-04-12 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | Season | 2025-12-03 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | Season | 2026-01-03 |  |  | UPS-1 was not maintaining rectifire voltage. | Proper checking, & rectyfy problem.found rectifire card feedback not worked so replce with new. Now ok. | AMC | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | OFF Season | 2026-04-11 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | eb7ce6a60f04 | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-1-MILL | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | OFF Season | 2023-08-18 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | OFF Season | 2024-01-17 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | OFF Season | 2024-05-08 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | Season | 2025-01-28 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | OFF Season | 2025-04-12 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | Season | 2025-12-03 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | OFF Season | 2026-04-11 |  |  | All electronic card & cooling fan, transformer found healthy. | Proper checking, cleaning & connection tightness checking all parameter check & battery voltage check work are completed. |  | External | Sushil Singh/MR. V. Singh
Turbine & Instrument Equipment life histroy 20-06-2026 (2).xlsx | a78b376fc91d | UPS HISTORY :: UNINTERRUPTIBLE POWER SUPPLY (UPS) | ZIL/GSM/UPS-2-MILL | Technician |  |  |  | Sec .Engineer |  |  |  | HOD