## Sheet_Summary
IBD_03_2025 | IBD-03
PFW-62-2025 | PFW-62
PFW-62A-2025 | PFW-62A
PFW-63-2025 | PFW-63
PFW-63A-2025 | PFW-63A
PFW-64-2025 | PFW-64
PFW-64A-2025 | PFW-64A
PFW-264-2025 | PFW-264
PFW-264A-2025 | PFW-264A
PFW-79-2025 | PFW-79
PFW-79A-2025 | PFW-79A
PFW-84-2025 | PFW-84
PFW-84A-2025 | PFW-84A
PFW-89-2025 | PFW-89
PFW-89A-2025 | PFW-89A
PFW-9O-2025 | PFW-90
PFW-90A-2025 | PFW-90A
PFW-95-2025 | PFW-95
PFW-95A-2025 | PFW-95A
PFW-100-2025 | PFW-100
PFW-100A-2025 | PFW-100A
PFW-111-2025 | PFW-111
PFW-111A-2025 | PFW-111A
PFW-112-2025 | PFW-112
PFW-112A-2025 | PFW-112A
PFW-113-2025 | PFW-113
PFW-113A-2025 | PFW-113A
PFW-133-2025 | PFW-133
PFW-133A-2025 | PFW-133A
MS-14-2025 | MS-14
MS-16-2025 | MS-16
MS-18-2025 | MS-18
MS-20-2025 | MS-20
MS-21-2025 | MS-21
MS-24-2025 | MS-24
MS-27-2025 | MS-27
MS-28-2025 | MS-28
MS-28A-2025 | MS-28A
MS-27A-2025 | MS-27A
MS-30-2025 | MS-30
MS-43-2025 | MS-43
MS-44-2025 | MS-44
MS-62-2025 | MS-62
MS-66-2025 | MS-66
MS-67-2025 | MS-67
MS-79-2025 | MS-79
MS-81-2025 | MS-81
MS-81A-2025 | MS-81A
MS-85-2025 | MS-85
MS-87-2025 | MS-87
MS-91-2025 | MS-91
MS-93-2025 | MS-93
MS-94-2025 | MS-94
MS-98-2025 | MS-98
MS-100-2024 | MS-100
MS-103-2025 | MS-103
MS-105-2025 | MS-105
MS-107-2025 | MS-107
MS-109-2025 | MS-109
CBD-03-2025 | CBD-03
SB-02-2024 | SB-02
SB-07-2025 | SB-07
SB-37-2025 | SB-37
LPS-05-2024 | LPS-05
LPS-06-2025 | LPS-06
LPS-07-2025 | LPS-07
LPS-22-2024 | LPS-22
MPS-07-2024 | MPS-07
MPS-13-2024 | MPS-13
MPS-14-2024 | MPS-14
AD-12-2024 | AD-12
AD-13-2025 | AD-13
AD-14-2025
MS-58-2025 | MS-58
MS-58A-2025 | MS-58A
MS-67A-2024 | MS-67A
LPS-32-2024 | LPS-32
MOV TURBINE
MOV-201-2025 | MOV-201
MOV-202-2025 | MOV-202
MOV-203-2025 | MOV-203
MOV-204-2025 | MOV-204
MOV-100-2025 | MOV-100
MOV-101-2025 | MOV-101
MOV-102-2025 | MOV-102
MOV-103-2025 | MOV-103
MOV-401-2025 | MOV-401
MOV-402-2025 | MOV-402
MOV-403-2025 | MOV-403
MOV-404-2025 | MOV-404
MOV-405-2025 | MOV-405
MOV-406-2025 | MOV-406
MOV-407-2025 | MOV-407
MOV-408-2025 | MOV-408
MOV-411-2024 | MOV-411
PCW-13-2025 | PCW-13
PCW-14-2024 | PCW-14
PCW-15-2024 | PCW-14
PCW-42-2024 | PCW-42
PCW-43-2024 | PCW-43
PCW-44-2024 | PCW-43
PDW-38-2025 | PDW-38
BC-05 | NBC_PLOUGH

## INDEX
SN | TAG NO | Description | 2024 | 2025 | 2026
1 | PFW-62 | 150 TPH Boiler BFP-A DISCHARGE ISO MOV | 24/06/2024 | 24/04/2025
2 | PFW-62 A | 150 TPH Boiler BFP-A Discharge Integral Isolation MOV) | 29/04/2024 | 2025-12-04
3 | PFW-63 | BFP-B discharge iso MOV | 24/06/2024 | 24/04/2025
4 | PFW-63A | BFP-B dis. integral bypass iso MOV | 29/04/2024 | 2025-12-04
5 | PFW-64 | BFP-C discharge iso MOV | 25/06/2024 | 24/04/2025
6 | PFW-64A | BFP-C dis. integral bypass iso MOV | 29/04/2024 | 14/04/2024
7 | PFW-264 | BFP-D discharge iso MOV | 25/06/2024 | 22/04/2025
8 | PFW-264A | BFP-D dis. integral bypass iso MOV | 30/04/2024 | 14/04/2025
9 | PFW-79 | HP heater-1 inlet iso MOV | 29/04/2024 | 17/04/2025
10 | PFW-79A | HP heater-1 inlet integral bypass iso MOV | 2024-03-05 | 17/04/2025
11 | PFW-84 | HP heater-1 bypass iso MOV | 30/05/2024 | 16/04/2025
12 | PFW-84A | Integral bypass of HP heater-1 bypass iso MOV | 2024-06-05 | 14/04/2025
13 | PFW-89 | HP heater-1 outlet iso MOV | 2024-07-07 | 23/04/2025
14 | PFW-89A | HP heater-1 outlet integral bypass iso MOV | 2024-07-05 | 17/04/2025
15 | PFW-90 | HP heater-2 inlet iso MOV | 30/05/2024 | 18/4/2025
16 | PFW-90A | HP heater-2 inlet integral bypass iso MOV | 2024-06-05 | 14/04/2025
17 | PFW-95 | HP heater-2 bypass iso MOV | 2025-09-07 | 22/04/2025
18 | PFW-95A | Integral bypass of HP heater-2 bypass iso MOV | 2024-07-05 | 15/04/2025
19 | PFW-100 | HP heater-2 outlet iso MOV | 28/06/2024 | 18/04/2025
20 | PFW-100A | HP heater-2 outlet integral bypass iso MOV | 2024-07-05 | 15/04/2025
21 | PFW-111 | 100% bypass feedwater FCV inlet iso MOV | 2024-10-07 | 28/04/2025
22 | PFW-111A | 100% bypass feedwater FCV inlet integral iso | 20/05/2024 | 28/04/2025
23 | PFW-112 | 100% feedwater FCV inlet iso MOV | 2024-12-07 | 26/04/2025
24 | PFW-112A | 100% feedwater FCV inlet integral iso MOV | 21/05/2024 | 26/04/2025
25 | PFW-113 | 30% bypass feedwater FCV inlet iso MOV | 2024-10-07 | 26/04/2025
26 | PFW-113A | 30% bypass feedwater FCV inlet iso MOV | 21/05/2024 | 26/04/2025
27 | PFW-133 | Economiser inlet header iso MOV | 2024-09-07 | 29/04/2025
28 | PFW-133A | Economiser inlet header integral iso MOV | 28/05/2024 | 29/04/2025
29 | MS-14 | Roof tube inlet header drain iso MOV | 19/05/2024 | 2025-01-05
30 | MS-16 | LTSH inlet header drain iso MOV | 19/05/2024 | 29/04/2025
31 | MS-18 | LTSH outlet header vent iso MOV | 28/08/2024 | 2025-01-05
32 | MS-20 | DSH-501 outlet drain iso MOV | 27/05/2024 | 29/04/2025
33 | MS-21 | RSH outlet header vent iso MOV | 28/08/2024 | 2025-01-05
34 | MS-24 | DSH-502 outlet drain iso MOV | 27/08/2024 | 30/04/2025
35 | MS-27 | EMRV inlet iso MOV | 26/05/2024 | 22/05/2025
36 | MS-27A | EMRV inlet integral iso MOV | 26/05/2024 | 22/05/2025
37 | MS-28 | Startup vent iso MOV | 14/07/2024 | 21/05/2025
38 | MS-28A | Startup vent integral iso MOV | 26/05/2024 | 21/05/2025
39 | MS-30 | Main steam drain iso MOV | 28/04/2024 | 2025-03-05
40 | MS-43 | Main steam line iso MOV | 16/07/2024 | 21/05/2025
41 | MS-44 | Main steam line bypass iso MOV | 27/05/2024 | 21/05/2025
42 | MS-66 | TG inlet iso MOV | 25/05/2024 | 20/05/2025
43 | MS-67 | TG inlet bypass iso MOV | 21/06/2024 | 16/05/2025
44 | MS-79 | Turbine warmup vent iso MOV | 2024-03-05 | 2025-10-05
45 | MS-81 | 3 ata steam to process iso MOV | 26/06/2024 | 2025-08-05
46 | MS-81A | 3 ata steam to process integral iso MOV | 26/06/2024 | 2025-08-05
47 | MS-85 | 110/3 ata PRDS PCV-509 drain line MOV | 26/06/2024 | 2025-08-05
48 | MS-87 | 3 ata steam to deaerator iso MOV | 2024-02-07 | 2025-10-05
49 | MS-91 | 110/3 ata deaerator PRDS drain line MOV | 2024-02-07 | 2025-10-05
50 | MS-93 | PCV-511A inlet iso MOV | 29/06/2024 | 2025-09-05
51 | MS-94 | PCV-511B inlet iso MOV | 29/06/2024 | 2025-09-05
52 | MS-98 | PCV-511A inlet drain iso MOV | 2024-05-06 | 2025-07-05
53 | MS-100 | PCV-511B inlet drain iso MOV | 2024-05-06 | 2025-07-05
54 | MS-103 | LTSH outlet drain iso MOV | 15/07/2024 | 2025-02-05
55 | MS-105 | RSH outlet drain iso MOV | 27/08/2024 | 30/04/2025
56 | MS-107 | FSH outlet vent iso MOV | 28/05/2024 | 30/04/2025
57 | MS-109 | FSH outlet drain iso MOV | 27/05/2024 | 2025-02-05
58 | IBD-03 | IBD iso MOV | 2024-11-06 | 23/04/2025
59 | CBD-03 | CBD iso MOV | 19/05/2024 | 2025-12-05
60 | SB-02 | Sootblower iso MOV | 21/05/2024 | 21/05/2025
61 | SB-07 | Sootblower drain at PCV-503 inlet iso MOV | 20/05/2024 | 2025-03-05
62 | SB-37 | Sootblower iso drain MOV | 20/05/2024 | 2025-12-05
63 | LPS-05 | MOV after 110/3 ata process PRDS | 22/07/2024 | 28/05/2025
64 | LPS-06 | 3 ata steam from TG before 3 ata steam to process | 14/07/2024 | 24/05/2025
65 | LPS-07 | 3 ata steam to process drain iso MOV | 26/06/2024 | 2025-09-05
66 | LPS-22 | Deaerator pegging steam iso MOV | 13/07/2024 | 28/05/2025
67 | MPS-07 | MOV after 110/8 ata auxiliary PRDS | 2024-04-07 | 26/05/2025
68 | MPS-13 | 9 ata steam from TG iso MOV before ejector | 2024-08-05 | 23/05/2025
69 | MPS-14 | 9 ata aux. steam iso valve before ejector MOV | 2024-08-05 | 23/05/2025
70 | MS-58 | 110/45 ATA PRDS Steam inlet iso MOV | 15/07/2024 | 2025-07-05
71 | MS-58A | 110/45 ATA PRDS Steam inlet bypass iso MOV | 15/07/2024 | 2025-07-05
72 | MS-62 | 110/45 ATA PRDS inlet drain iso MOV | 2024-04-07 | 2025-10-05
73 | MS-67A | 110/45 ATA PRDS outlet line drain iso MOV | 2024-08-05 | 28/05/2025
74 | LPS-32 | 110/45 ATA PRDS outlet line isolation MOV | 2024-06-09 | 2025-02-06
75 | AD-12 | FD fan bypass motorised damper | 28/05/2024 | 27/05/2025
76 | AD-13 | SA fan bypass motorised damper | 14/07/2024 | 2025-12-05 |  | q
77 | AD-14 | FD fan bypass motorised damper |  | 30-05-2025
78 | AD-15 | BC5_NBC1 PLOUGH MOV | 29/7/2024 |  |  |  | .-
79 | AD-16 | BC5_MECH PLOUGH MOV | 23/07/2024 | 30-05-2025
80 | MOV-201 | CEP-A discharge MOV | 2024-01-05 | 2025-10-05
81 | MOV-202 | CEP-B discharge MOV | 2024-01-05 | 2025-10-05
82 | MOV-203 | CEP-C discharge MOV | 2024-01-05 | 2025-10-05
83 | MOV-204 | Vaccum breaker MOV | 21/06/2024 | 16/05/2025
84 | MOV-100 | Bleed-1 MOV | 2024-01-06 | 28/05/2025
85 | MOV-101 | Bleed-2 MOV | 21/06/2024 | 26/05/2025
86 | MOV-102 | Bleed-2 to ejector MOV | 2024-08-07 | 23/05/2025
87 | MOV-103 | Main steam inlet drain MOV | 2024-01-05 | 19/05/2025
88 | MOV-401 | Steam to hogger ejector MOV | 2024-04-05 | 13/05/2025
89 | MOV-402 | Steam to standby ejector MOV | 2024-04-05 | 14/05/2025
90 | MOV-403 | Steam to Y1 ejector MOV | 2024-03-05 | 15/05/2025
91 | MOV-404 | Air to Y1 ejector MOV(Bush in place of brg) | 2024-03-06 | 14/05/2025
92 | MOV-405 | Air to standby ejector MOV(Bush in place of brg) | 26/04/2024 | 15/05/2025
93 | MOV-406 | Air to hogger ejector MOV(Bush in place of brg) | 2024-04-05 | 14/05/2025
94 | MOV-407 | Condensate to ejector MOV | 2024-03-05 | 13/05/2025
95 | MOV-408 | Condensate from ejector MOV | 2024-03-05 | 13/05/2025
96 | PCW-13 | MCWP-A discharge MOV | 13/07/2024 | 23/05/2025
97 | PCW-14 | MCWP-B discharge MOV | 2024-09-07 | 23/05/2025
98 | PCW-15 | MCWP-C discharge MOV | 2024-08-07 | 23/05/2025
99 | PCW-42 | ACWP-A discharge MOV | 2024-02-06 | 24/05/2025
100 | PCW-43 | ACWP-B discharge MOV | 2024-03-06 | 24/05/2025
101 | PCW-44 | ACWP-C discharge MOV | 2024-02-06 | 24/05/2025
102 | PDW-38 | Deaerator emergency make-up water line MOV | 13/07/2024 | 15/05/2025
Total 98 Sheets ready

## IBD_03_2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler IBD)
EQUIPMENT TAG NAME: | [5 empty] | IBD-03
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 1C27250601
Actuater type |  |  | K 150G 0 A |  |  | Wiring Diagram No. |  |  | BH87Z60PV
O/P speed |  |  | 36.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.720kw |  |  | Avg. Load |  |  | 2.3 Amp
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Bearing Housing and o-ring Replaced.
OFF Season |  | 2021 | All Parts Found Ok |  | Inner ring of brg housing Replaced.
OFF Season |  | 2024-11-06 | Actuator not operated properly |  | 1. Bush found damaged, replaced with other bush. |  |  | 1000 | Internal | S.Pandey / Pankaj Singh
2. Replaced the handwheel retainer.
3. Oil Level checked , Found Ok.
4. Clean the each parts of actuator.
5. Checked the limit assembly & contacts.
6. Checked Remote / Local Operation.
Off Season |  | 23/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  | 0 | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-62-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler BFP-A DISCHARGE ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | PFW-62
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210403
Actuater type |  |  | K 60 F 14 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 2.5KW 3PH |  |  | Avg. Load |  |  | 9.0 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Bearing Housing and o-ring Replaced.
OFF Season |  | 2021 | All Parts Found Ok |  | Inner ring of brg housing Replaced.
OFF Season |  | 24/06/2024 | Indication Bulb found fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Oil Level checked , Found Ok.
4. Clean the each parts of actuator.
5. Checked the limit assembly & contacts.
6. Checked Remote / Local Operation.
OFF Season |  | 24/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-62A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler BFP-A Discharge Integral Isolation MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-62A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210403
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | BH87Z60PV
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Thrust Bearing 01 set Replaced
OFF Season |  | 2021 | All Parts Found Ok |  | Thrust Bearing 2no.s Replaced
OFF Season |  | 29/04/2024 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done.. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Oil Level checked , Found Ok.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-12-04 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-63-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler BFP-B DISCHARGE ISO MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-63
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210404
Actuater type |  |  | K 60 F 14 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 2.5KW 3PH |  |  | Avg. Load |  |  | 9.0 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Thrust Bearing 01 set Replaced
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 24/06/2024 | 1. Indication Bulb Found Fuse. 2. Oil Sepage found From Actuator Shaft. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Replaced the thrust bearing oil seal.
4. Clean the each parts of actuator.
5. Checked the limit assembly & contacts.
6. Checked Remote / Local Operation.
OFF Season |  | 24/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Sealed the cable gland with m-seal.
5. Checked Remote / Local Operation.

## PFW-63A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler BFP-B Discharge Integral Isolation MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-63A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210202
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 29/04/2024 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Oil Level checked , Found Ok.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-12-04 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done.. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Oil Level checked , Found Ok.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.

## PFW-64-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler BFP-C Discharge Isolation MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-64
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210402
Actuater type |  |  | K 60 F 14 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 2.5KW 3PH |  |  | Avg. Load |  |  | 9.0 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Retainer Ring.
OFF Season |  | 25/06/2024 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Replaced the thrust bearing oil seal.
4. Clean the each parts of actuator.
5. Checked the limit assembly & contacts.
6. Checked Remote / Local Operation.
OFF Season |  | 24/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-64A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler BFP-C Discharge Integral Isolation MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-64A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210402
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Old Thrust Bearing 01 no.s Replaced
OFF Season |  | 2021 | All Parts Found Ok |  | Old Thrust Bearing 01 no.s Replaced
OFF Season |  | 29/042024 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Oil Level checked , Found Ok.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 14/04/2025 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done.. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Oil Level checked , Found Ok.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.

## PFW-264-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler BFP-D DIS.ISO MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-264
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210401
Actuater type |  |  | K 60 F 14 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 2.5KW 3PH |  |  | Avg. Load |  |  | 9.0 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.Retainer Ring Replaced
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2024-06-25 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-04-22 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-264A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler BFP-D Discharge Integral Isolation MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-264A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210301
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2024-04-30 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | S. Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 2025-04-14 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-79-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler HP HEATER-1 INLET ISO MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-79
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210501
Actuater type |  |  | K 1000 F 16 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 36.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 3.70KW 3PH |  |  | Avg. Load |  |  | 9.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 29/05/2024 | All Parts Found Ok |  | 1. Replaced the oil seal. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 17/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-84-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler HP HEATER-1 BYPASS ISO MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-84
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210506
Actuater type |  |  | K 1000 F 16 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 36.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 3.70KW 3PH |  |  | Avg. Load |  |  | 9.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Not Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 30/05/2024 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 16/04/2025 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-79A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler HP HEATER-1 INLET INTEGRAL BYPASS ISO MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-79A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210308
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2024-03-05 | All parts found ok |  | 1. Thrust Bearing Cleaning & Checking done.. |  |  |  | Internal | S.Pandey/Pankaj singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 17/04/2025 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-84A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler INTEGRAL BYPASS OF HP HEATER-1 BYPASS ISO MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-84A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210304
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator Torque Excel seal Replaced.
OFF Season |  | 2020 | All Parts Found Ok |  | One sideThrust Bearing Replaced
OFF Season |  | 2021 | All Parts Found Ok |  | Thrust Bearing 01no.as Replaced
OFF Season |  | 2024-06-05 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | S. Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 14/04/2025 | Indication Bulb Found Fuse |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-89-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler HP HEATER-1 OUTLET ISO MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-89
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210507
Actuater type |  |  | K 1000 F 16 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 36.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 3.70KW 3PH |  |  | Avg. Load |  |  | 9.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.control card Replaced.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator Only checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.control card Repaired.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2024-07-07 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | S. Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 23/04/2025 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-89A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler HP HEATER-1 OUTLET INTEGRAL BYPASS ISO MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-89A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210203
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 36.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 3.70KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2024-07-05 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 17/04/2025 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-9O-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler HP HEATER-2 INLET ISO MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-90
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210504
Actuater type |  |  | K 1000 F 16 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 36.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 3.70KW 3PH |  |  | Avg. Load |  |  | 9.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.Bottom Oil Seal Ring Replaced.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.Bottom Oil Seal Replaced.
OFF Season |  | 30/05/2024 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 18/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-90A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler HP HEATER-2 INLET INTEGRAL BYPASS ISO MOV)
EQUIPMENT TAG NAME: | [5 empty] | PFW-90A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210201
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2024-06-05 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | S. Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 14/04/2025 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-95-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler HP HEATER-2 BYPASS ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | PFW-95
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210502
Actuater type |  |  | K 1000 F 16 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 36.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 3.70KW 3PH |  |  | Avg. Load |  |  | 9.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.Top Seal Retainer Replaced.
OFF Season |  | 2024-09-07 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Shailendra Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 22/04/2025 | All Parts Found ok. |  | 1. Oil Level Checked Found ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-95A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler INTEGRAL BYPASS OF HP HEATER-2 BYPASS ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | PFW-95A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210205
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2024-07-05 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 15/04/2025 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-100-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler HP HEATER-2 OUTLET ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | PFW-100
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210509
Actuater type |  |  | K 1000 F 16 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 36.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 3.70KW 3PH |  |  | Avg. Load |  |  | 9.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.Retainer Replaced.
OFF Season |  | 28/06/2024 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 18/04/2025 | Hand Wheel not working properly |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
5. Hand Wheel Cam Spring Replaced.

## PFW-100A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-HP HEATER-2 OUTLET INTEGRAL BYPASS ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | PFW-100A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210209
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2024-07-05 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 15/04/2025 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-111-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-100% BYPASS FEEDWATER FCV INLET ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | PFW-111
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210505
Actuater type |  |  | K 1000 F 16 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 36.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 3.70KW 3PH |  |  | Avg. Load |  |  | 9.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Not Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2024-10-07 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 28/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-111A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-100% BYPASS FEEDWATER FCV INLET INTEGRAL ISO )
EQUIPMENT TAG NAME: | [5 empty] | PFW-111A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210210
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.Felt Seal Replaced.
OFF Season |  | 20/05/2024 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 28/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Hand Wheel Retainer replaced.
5. Checked Remote / Local Operation.

## PFW-112-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-100% BYPASS FEEDWATER FCV INLET INTEGRAL ISO )
EQUIPMENT TAG NAME: | [5 empty] | PFW-112
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210508
Actuater type |  |  | K 1000 F 16 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 3.70KW 3PH |  |  | Avg. Load |  |  | 9.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2024-12-07 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 26/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-112A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-100% FEEDWATER FCV INLET INTEGRAL ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | PFW-112A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210207
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 21/5/2024 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 26/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-113-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-30% BYPASS FEEDWATER FCV INLET ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | PFW-113
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B27030101
Actuater type |  |  | K 300 F 14 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.200KW 3PH |  |  | Avg. Load |  |  | 3.10 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2024-10-07 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 26/04/2025 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-113A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-30% BYPASS FEEDWATER FCV INLET INTEGRAL ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | PFW-113A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210307
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.o1 set bearing replaced
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.2no.s bearing replaced.
OFF Season |  | 21/05/2024 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 26/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-133-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-ECONOMISER INLET HEADER ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | PFW-133
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210503
Actuater type |  |  | K 1000 F 16 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 36.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 3.70KW 3PH |  |  | Avg. Load |  |  | 9.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2024-09-07 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 29/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PFW-133A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-ECONOMISER INLET HEADER INTEGRAL ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | PFW-133A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210204
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.Bottom Bearing Replaced
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.One side bearing Replaced.
OFF Season |  | 28/05/2024 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 29/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-14-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-ROOF TUBE INLET HEADER DRAIN ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-14
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960107
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 19/05/2024 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 2025-01-05 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jhar / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-16-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-LTSH INLET HEADER DRAIN ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-16
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960101
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Thrust Bearing Checked.
OFF Season |  | 19/05/2024 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 29/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-18-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-LTSH OUTLET HEADER VENT ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-18
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960105
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust bearing not Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Thrust Bearing Checked.
OFF Season |  | 28/08/2024 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 2025-01-05 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-20-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boile-DSH-501 OUTLET DRAIN ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-20
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960104
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 27/05/2024 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 29/04/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-21-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-RSH OUTLET HEADER VENT ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-21
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960109
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Thrust Bearing Checked
OFF Season |  | 28/08/2024 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-01-05 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-24-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-DSH-502 OUTLET DRAIN ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-24
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960108
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Thrust Bearing Checked
OFF Season |  | 27/08/2024 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Thrust Bearing Cleaning & Checking done..
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 30/04/2025 | Indication Bulb Found Fuse |  | 1. Replaced the indication bulb. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-27-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-ESV INLET ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-27
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26560201
Actuater type |  |  | K 150 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.20 KW 3PH |  |  | Avg. Load |  |  | 3.10 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 22/05/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 22/05/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-28-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-STARTUP VENT ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-28
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960202
Actuater type |  |  | K 300 F 14 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.200KW 3PH |  |  | Avg. Load |  |  | 3.10 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 14/07/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 21/05/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-28A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-STARTUP VENT INTEGRAL ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-28A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210303
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Thrust Bearing Checked
OFF Season |  | 26/05/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. 1 Litre Oil Top up done.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 21/05/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-27A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-ESV INLET INTEGRAL ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-27A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210208
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Thrust Bearing Checked
OFF Season |  | 26/05/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 22/05/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-30-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-MAIN STEAM DRAIN ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-30
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960306
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Thrust Bearing Checked
OFF Season |  | 28/04/2024 | All Parts Found Ok |  | 1. Replaced the Double Lip Oil Seal |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 2025-03-05 | Actuator Was Not Operated From Remote |  | 1. Replaced the Mother card. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
|  |  | Indication Bulb Found Fuse |  | 4. Checked Remote / Local Operation.
5. Replaced the Indication Bulb.

## MS-43-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-MAIN STEAM LINE ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-43
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210510
Actuater type |  |  | K 1000 F 16 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 36.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 3.70KW 3PH |  |  | Avg. Load |  |  | 9.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked. washer set of upper brg replaced.
OFF Season |  | 16/07/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 21/05/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Replaced the Hand Wheel Retainer .
5. Checked Remote / Local Operation.

## MS-44-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-MAIN STEAM LINEBYPASS ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-44
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960403
Actuater type |  |  | K300 F14 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.20 KW 3PH |  |  | Avg. Load |  |  | 3.10 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.Oil seal replaced.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked. Oil seal (handwheel) side replaced.
OFF Season |  | 27/05/2024 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Thurst Bearing Cleaning & Checking
5. Checked Remote / Local Operation.
OFF Season |  | 21/05/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-62-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler -MS-62)
EQUIPMENT TAG NAME: | [5 empty] | MS-62
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 37201D54240
Actuater type |  |  | SA3A16 |  |  | Wiring Diagram No. |  |  | 3-WDP-D2G-ZDEA1C3
O/P speed |  |  | 16.RPM |  |  | Lubricant |  |  | EP 0
Motor |  |  | 0.06KW 3PH |  |  | Avg. Load |  |  | 0.29 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2024-04-07 | Actuator was not operated from local operation. |  | 1. Grease quantity Checked, Found Ok. |  |  |  | Internal | Amleshwar / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Repaired the power card.
5. Checked Remote / Local Operation Found ok.
OFF Season |  | 2025-10-05 | All Parts Found Ok. |  | 1. Grease quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-66-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-TG INLET ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-66
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 1W64680201
Actuater type |  |  | K 1000 F 16E |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 36.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 3.7 KW 3PH |  |  | Avg. Load |  |  | 9.90A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.upper bearing washer Replaced.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.Bottom oil seal , retainer ring, oil seal of limit switch assembly side and oil seal of manual lever.
OFF Season |  | 25/05/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Prashant Shukla/ Pankaj Singh /Pankaj Kumar
2. Thurst Bearing Cleaning & Checking.
3. Thrust Bearing Washer (4Nos) Replaced.
4. Replaced the double lip oil seal.
5. Replaced the "O" ring for motor housing.
6. Clean the each parts of actuator.
7. 6 Litre Oil Top up done.
8. Replaced the limit switch assembly.
9. Checked Remote / Local Operation.
OFF Season |  | 20/05/2025 | Oil Sepage found from motor side. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Replaced the Felt Seal.
3. Replaced the Hand wheel retainer.
4. Clean the each parts of actuator.
5. Checked the limit assembly & contacts.
6. 5 Litre Oil replaced.
7. Checked Remote / Local Operation.

## MS-67-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-TG INLET BYPASS ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-67
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960402
Actuater type |  |  | K 300 F 14 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.2 KW 3PH |  |  | Avg. Load |  |  | 3.10 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 21/06/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Replaced The hand wheel retainer.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 16/05/2025 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-79-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-TURBINE WARMUP VENT ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-79
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210101
Actuater type |  |  | K300 F14 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.20 KW 3PH |  |  | Avg. Load |  |  | 3.10 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2025-03-05 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 2024-10-05 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-81-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-3ATA STEAM TO PROCESS ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-81
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210102
Actuater type |  |  | K 300 F 14 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.200KW 3PH |  |  | Avg. Load |  |  | 3.10 A S2-15 min
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2024-06-26 | 1. Valve is Not Working Properly. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Replaced the thrust bearing with new one.
3. Replaced the thrust bearing felt seal.
|  |  | 2.Indication Bulb Found Fuse |  | 4. Clean the each parts of actuator.
5. Checked the limit assembly & contacts.
6. Checked Remote / Local Operation.
OFF Season |  | 2025-05-08 | All Parts Found Ok |  | 1. Oil Level checked , Found Ok. |  |  |  | Internal | Prashant Shukla / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-81A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-3ATA STEAM TO PROCESS INTEGRAL ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-81A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210206
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021
OFF Season |  | 2024-06-26 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar/ Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-05-08 | All Parts Found Ok. |  | 1. Oil Level Check Found Ok. |  |  |  | Internal | Prashant/ Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-85-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-110/3 ATA PRDS PCV -509 DRAIN LINE MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-85
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960305
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.01 no.s old top thrust bearing Replaced.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 26/06/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar /Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-08-05 | All Parts Found Ok. |  | 1. Oil Level Check Found Ok. |  |  |  | Internal | Prashant /Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-87-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-3ATA STEAM TO DEAERATOR ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-87
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B5688001
Actuater type |  |  | K 60 F 14 A |  |  | Wiring Diagram No. |  |  | 1687Z60TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.2KW 3PH |  |  | Avg. Load |  |  | 3.10 A S2-15 min
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2024-02-07 | PCB Cord Found Faulty. |  | 1. PCB Card (Old) Replaced from Ms-66 |  |  |  | Internal | Amleshwar /Pankaj Singh
|  |  | Limit Switch Assembly Found Faulty |  | 2. Limit Switch Assembly Replaced with new.
|  |  | Handwheel Retainer Found Faulty |  | 3. Handwheel Retainer Replaced with new
4. Clean the each parts of actuator.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-10-05 | All Parts Found Ok. |  | 1. Oil Level Check Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-91-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-110/3 ATA DEAERATOR PRDS DRAIN LINE MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-91
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960309
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2024-02-07 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar/ Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-10-05 | All Parts Found Ok. |  | 1. Oil Level Check Found Ok. |  |  |  | Internal | S.Pandey /Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-93-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-PCV-511A INLET ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-93
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960301
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 29/06/2024 | Indication Bulb Found Fuse. Oil Level Found 90% |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar/ Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. 10% Oil Top Up.
4. Clean the each parts of actuator.
5. Checked the limit assembly & contacts.
6. Checked Remote / Local Operation.
OFF Season |  | 2025-09-05 | All Parts Found Ok. |  | 1. Oil Level Check Found Ok. |  |  |  | Internal | S.Pandey /Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-94-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-PCV-511B INLET ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-94
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960308
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 29/06/2024 | Indication Bulb Found Fuse. Oil Level Found 90% |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar/ Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. 10% Oil Top Up.
4. Clean the each parts of actuator.
5. Checked the limit assembly & contacts.
6. Checked Remote / Local Operation.
OFF Season |  | 2025-09-05 | All Parts Found Ok. |  | 1. Oil Level Check Found Ok. |  |  |  | Internal | Prashant /Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-98-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-PCV-511A INLET DRAIN ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-98
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960302
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.power card Repaired.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2024-05-06 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Prashant/ Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-07-05 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Prashant/ Pankaj Kumar
2. Oil Level Checked Found Ok.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.

## MS-100-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-PCV-511B INLET DRAIN ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-100
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960303
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Thrust Bearing Checked.
OFF Season |  | 2024-05-06 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Prashant/ Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-07-05 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Prashant/ Pankaj Kumar
1. Clean the each parts of actuator.
2. Checked the limit assembly & contacts.
3. Checked Remote / Local Operation.

## MS-103-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-LTSH OUTLET DRAIN ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-103
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960103
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 15/07/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-02-05 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
1. Clean the each parts of actuator.
2. Checked the limit assembly & contacts.
3. Checked Remote / Local Operation.

## MS-105-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-RHS OUTLET DRAIN ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-105
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960107
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Thrust Bearing Checked.
OFF Season |  | 27/08/2024 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 30/04/2025 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
1. Clean the each parts of actuator.
2. Checked the limit assembly & contacts.
3. Checked Remote / Local Operation.

## MS-107-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-FSH OUTLET Vent ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-107
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960104
Actuater type |  |  | 1687Z00TGZ |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Thrust Bearing Checked.
OFF Season |  | 28/05/2024 | All Parts Found Ok |  | 1. Thrust Bearing Cleaning & Checking done. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 30/04/2025 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
1. Clean the each parts of actuator.
2. Checked the limit assembly & contacts.
3. Checked Remote / Local Operation.

## MS-109-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-FSH OUTLET DRAIN ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | MS-109
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960304
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Thrust Bearing Checked.
OFF Season |  | 27/05/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-02-05 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## CBD-03-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-CBD ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | CBD-03
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 1C27253201
Actuater type |  |  | K 60 G 0 A |  |  | Wiring Diagram No. |  |  | BH87Z40PV
O/P speed |  |  | 24.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.180 KW |  |  | Avg. Load |  |  | 0.90 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.01 set thrust bearing Replaced.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Thrust Bearing Checked.1 set of bearing used.
OFF Season |  | 19/05/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-12-05 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## SB-02-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-SOOTBLOWER ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | SB-02
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B26210103
Actuater type |  |  | K 300 F 14 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.200KW 3PH |  |  | Avg. Load |  |  | 3.10 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.bottom oil seal Ring Replaced.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.bottom oil seal Ring Replaced.
OFF Season |  | 2024 | During Maintenance dismantle the Actuator checking of Thrust bearing status is Normal. |  | Indication Bulb Replaced |  |  |  | Internal | Amleshwar

## SB-07-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-SOOTBLOWER DRAIN AT PCV-503 INLET ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | SB-07
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960102
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 20/05/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-03-05 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## SB-37-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler-SOOTBLOWER DRAIN ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | SB-37
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B27030202
Actuater type |  |  | K 30 F 10A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.0rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.180 KW 3PH |  |  | Avg. Load |  |  | 0.90 A S2-15 min
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 20/05/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar / Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-12-05 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## LPS-05-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- MOV AFTER 110/3 ATA PROCESS PRDS )
EQUIPMENT TAG NAME: | [5 empty] | LPS-05
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 14AI-26372
Actuater type |  |  | Fr-AM71 |  |  | Wiring Diagram No.
O/P speed |  |  | 2800.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.1 |  |  | Avg. Load |  |  | 2.9
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 22/07/2024 | All Parts Found Ok. |  | 1. Grease level Top Up. |  |  |  | Internal | Amleshwar/ Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 28/5/2025 | All Parts Found Ok. |  | 1. Grease Quantity Checked , Found Ok. |  |  |  | Internal | Prashant Shukla / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## LPS-06-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- 3 ATA STEAM FROM TG BEFORE 3ATA STEAM TO PROCESS )
EQUIPMENT TAG NAME: | [5 empty] | LPS-06
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 14AI-26372
Actuater type |  |  | Fr-AM71 |  |  | Wiring Diagram No.
O/P speed |  |  | 2800.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.1 |  |  | Avg. Load |  |  | 2.9
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.Capacitor 47µF & 100µF of 63 Volt Replaced.
OFF Season |  | 14/07/2024 | All Parts Found Ok. |  | 1. Replaced the Handwheel retainer. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Replaced The Limit switch cover "O"ring.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 24/5/2025 | All Parts Found Ok. |  | 1. Grease Quantity Checked , Found Ok. |  |  |  | Internal | Prashant Shukla / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## LPS-07-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- 3 ATA STEAM TO PROCESS DRAIN ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | LPS-07
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960304
Actuater type |  |  | K 60 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27KW 3PH |  |  | Avg. Load |  |  | 1.70 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 26/6/2024 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Amleshwar/ Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-09-05 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Prashant/ Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## LPS-22-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- DEAERATOR PEGGING STEAM ISO MOV )
EQUIPMENT TAG NAME: | [5 empty] | LPS-22
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B25960201
Actuater type |  |  | K300 F14 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.2 KW |  |  | Avg. Load |  |  | 3.10 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 13/7/2024 | All Parts Found Ok. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | Prashant/ Pankaj Singh
2. Thurst Bearing Replaced.
3. Oil Level Checked Found Ok.
4. Clean the each parts of actuator.
5. Checked the limit assembly & contacts.
6. Checked Remote / Local Operation.
OFF Season |  | 28/5/2025 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Prashant/ Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MPS-07-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- MOV AFTER 110/8 ATA AUXILIARY PRDS )
EQUIPMENT TAG NAME: | [5 empty] | MPS-07
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B27030203
Actuater type |  |  | K 30 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.18KW 3PH |  |  | Avg. Load |  |  | 0.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Thrust Bearing Checked.
OFF Season |  | 2024-04-07 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Amleshwar/ Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 26/5/2025 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Prashant/ Pankaj Singh
2. Handwheel Crucifrom Oil Seal Replaced.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.

## MPS-13-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- 9ATA STEAM FROM TG ISO MOV BEFORE EJECTOR )
EQUIPMENT TAG NAME: | [5 empty] | MPS-13
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B27030201
Actuater type |  |  | K 30 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.18KW 3PH |  |  | Avg. Load |  |  | 0.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2024-08-05 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Prashant/ Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Oil Level Checked Found Ok.
4. Clean the each parts of actuator.
5. Checked the limit assembly & contacts.
6. Checked Remote / Local Operation.
OFF Season |  | 23/5/2025 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Prashant/ Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MPS-14-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- 9ATA AUX. STEAM ISO VALVE BEFORE EJECTOR MOV )
EQUIPMENT TAG NAME: | [5 empty] | MPS-14
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B06590201
Actuater type |  |  | K 30 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 48.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.18KW 3PH |  |  | Avg. Load |  |  | 0.90 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked.bottom seal replaced.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2024-08-05 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | Prashant/ Pankaj Singh
2. (35 TB No.) Terminal screw Replaced.
3. Oil Level Checked found Ok.
4. Clean the each parts of actuator.
5. Checked the limit assembly & contacts.
6. Checked Remote / Local Operation.
OFF Season |  | 26/6/2025 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Prashant/ Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.

## AD-12-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- FD FAN BYPASS MOTORIZED DAMPER )
EQUIPMENT TAG NAME: | [5 empty] | AD-12
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 14AI-35751
Actuater type |  |  | Fr-AM63 |  |  | Wiring Diagram No.
O/P speed |  |  | 1400.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | Kw-0.12 |  |  | Avg. Load |  |  | 0.65
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 28/05/2024 | All Parts Found Ok. |  | 1. Grease quantity Checked, Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 27/05/2025 | All Parts Found Ok. |  | 1. Grease quantity Checked, Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## AD-13-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- FD FAN BYPASS MOTORIZED DAMPER )
EQUIPMENT TAG NAME: | [5 empty] | AD-13
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 14AI-35751
Actuater type |  |  | Fr-AM63 |  |  | Wiring Diagram No.
O/P speed |  |  | 1400.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | Kw-0.12 |  |  | Avg. Load |  |  | 0.65
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 14/07/2024 | All Parts Found Ok. |  | 1. Grease quantity Checked, Found Ok. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 2025-12-05 | All Parts Found Ok. |  | 1. Grease quantity Checked, Found Ok. |  |  |  | Internal | Dilip Jha / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-58-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler PRDS 110/45ATA MAIN STEAM FROM BOILER
EQUIPMENT TAG NAME: | [5 empty] | MS-58
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 37201D54240
Actuater type |  |  | SA15A63 |  |  | Wiring Diagram No. |  |  | 3-WDP-B2G-ZDEA103A-A2B00
O/P speed |  |  | 63.RPM |  |  | Lubricant |  |  | EP 0
Motor |  |  | 1.1KW 3PH |  |  | Avg. Load |  |  | 2.9 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 15/07/2024 | All Parts Found Ok. |  | 1. Grease Quantity Checked found ok. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-07-05 | All Parts Found Ok. |  | 1. Grease quantity Checked, Found Ok. |  |  |  | Internal | Prashant Shukla / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-58A-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler -MS-58A)
EQUIPMENT TAG NAME: | [5 empty] | MS-58A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 37201D54240
Actuater type |  |  | SA3A16 |  |  | Wiring Diagram No. |  |  | 3-WDP-D2G-ZDEA1C3
O/P speed |  |  | 16.RPM |  |  | Lubricant |  |  | EP 0
Motor |  |  | 0.06KW 3PH |  |  | Avg. Load |  |  | 0.29 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 15/07/2024 | All Parts Found Ok. |  | 1. Grease Quantity Checked found ok. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 2025-07-05 | All Parts Found Ok. |  | 1. Grease quantity Checked, Found Ok. |  |  |  | Internal | Prashant Shukla / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MS-67A-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler -MS-67A)
EQUIPMENT TAG NAME: | [5 empty] | MS-67A
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 91015205
Actuater type |  |  | SA3A16 |  |  | Wiring Diagram No. |  |  | 3-WDP-D2G-ZDEA1C3A-A2D00
O/P speed |  |  | 16.RPM |  |  | Lubricant |  |  | EP 0
Motor | [5 empty] | Avg. Load |  |  | 0.29 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2024-08-05 | All Parts Found Ok. |  | 1. Grease Quantity Checked found ok. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Clean the each parts of actuator.
4. Checked the limit assembly & contacts.
5. Checked Remote / Local Operation.
OFF Season |  | 28/05/2025 | All Parts Found Ok. |  | 1. Grease quantity Checked, Found Ok. |  |  |  | Internal | Prashant Shukla / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## LPS-32-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler -3 ATA STEAM TO PROCESS MOV.
EQUIPMENT TAG NAME: | [5 empty] | LPS-32
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B66450101
Actuater type |  |  | K 600 F14 A |  |  | Wiring Diagram No. |  |  | 1697Z60 TZT
O/P speed |  |  | 36.RPM |  |  | Lubricant |  |  | SAE 80 EP ORALPHA SP68
Motor |  |  | 3.7KW 3PH |  |  | Avg. Load |  |  | 9.9 A S2-15 min.
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2024-06-09 | All Parts Found Ok. |  | 1. Oil Level Checked, Found Ok. |  |  |  | Internal | Amleshwar / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 2025-02-06 | All Parts Found Ok. |  | 1. Oil Level Checked, Found Ok. |  |  |  | Internal | Prashant/ Pankaj Singh
2. Thurst Bearing Cleaning & Checking.
3. Thurst Bearing with washer Replaced.
4. Clean the each parts of actuator.
5. Checked the limit assembly & contacts.
6. Checked Remote / Local Operation.

## MOV-201-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- CEP-A DISCHARGE MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-201
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29400501
Actuater type |  |  | K30 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z60 TGZ
O/P speed |  |  | 72.0 RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.270 KW 3PH |  |  | Avg. Load |  |  | 1.70 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.Mech.Spiral gear damage.spare mov used.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2024-01-05 | All Parts Found Ok. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | S.Pandey/Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 2025-10-05 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey/Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
+
+

## MOV-202-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- CEP B DISCHARGE MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-202
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29401301
Actuater type |  |  | K30 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z60 TGZ
O/P speed |  |  | 72.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.270 KW 3PH |  |  | Avg. Load |  |  | 1.70 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2024-01-05 | All parts found ok. |  | 1. Clean the each parts of actuator. |  |  |  | Internal | S.Pandey/Pankaj Singh
2. Oil Level Checked found ok.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 2025-10-05 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey/Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MOV-203-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- CEP-C DISCHARGE MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-203
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29400601
Actuater type |  |  | K30 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z60 TGZ
O/P speed |  |  | 72.0 RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.270 KW 3PH |  |  | Avg. Load |  |  | 1.70 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2024-01-05 | All parts found ok. |  | 1. Clean the each parts of actuator. |  |  |  | Internal | S.Pandey/Pankaj Singh
2. Checked the limit assembly & contacts.
3. Checked Remote / Local Operation.
OFF Season |  | 2025-10-05 | Indication Bulb Found Fuse. |  | 1. Replaced the indication bulb. |  |  |  | Internal | S.Pandey/Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MOV-204-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- VACCUM BREAKER MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-204
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B30290101
Actuater type |  |  | K 30 F 10 A |  |  | Wiring Diagram No. |  |  | 1687Z00TGZ
O/P speed |  |  | 96.0 rpm |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.270 KW 3PH |  |  | Avg. Load |  |  | 0.70 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2024-06-21 | All parts found ok. |  | 1.Replaced one side bearing. |  |  |  | Internal | S.Pandey/Pankaj Singh
2.Clean the each parts of actuator.
3.Checked the limit assembly & contacts.
4.Checked Remote / Local Operation.
OFF Season |  | 16/5/2025 | All parts found ok. |  | 1. Clean the each parts of actuator. |  |  |  | Internal | S.Pandey/Pankaj Singh
2. Checked the limit assembly & contacts.
3. Checked Remote / Local Operation.

## MOV-100-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- BLEED-1 MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-100
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29400101
Actuater type |  |  | K150 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z60 TGZ
O/P speed |  |  | 36.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.720 KW 3PH |  |  | Avg. Load |  |  | 2.30 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked. Bottom bearing ,bottom seal ring& felt seal (bottom side)
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.Bottom seal with felt seal and one side bearing.
OFF Season |  | 2024-01-06 | All Parts Found Ok. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Replaced the Both Thrust Bearing & Washer.
3. Replaced the Handwheel Cruciform oil seal .
4. Replaced the Oil.
5. Clean the each parts of actuator.
6. Checked Remote / Local Operation.
OFF Season |  | 28/05/2025 | All Parts Found Ok. |  | 1. Oil Level Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Thurst Bearing Cleaning & Checking.
5.Poteiometer (1K) Replaced.
6. Checked Remote / Local Operation.

## MOV-101-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- BLEED-2 MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-101
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29401001
Actuater type |  |  | K150 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z60 TGZ
O/P speed |  |  | 48.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 1.20 KW 3PH |  |  | Avg. Load |  |  | 3.10 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 28/06/2024 | All Parts Found Ok. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | Amleshwar /Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 26/05/2025 | All Parts Found Ok. |  | 1. Oil Level Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MOV-102-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- BLEED-2 TO EJECTOR MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-102
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29400901
Actuater type |  |  | K30 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z60 TGZ
O/P speed |  |  | 48.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.180 KW 3PH |  |  | Avg. Load |  |  | 0.90 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2024-08-07 | indication bulb found not ok |  | 1.Replaced the potentiometer & indicating bulb |  |  |  | Internal | S.Pandey /Pankaj Kumar
2.Clean the each parts of actuator.
3.Checked the limit assembly & contacts.
4.Checked Remote / Local Operation.
OFF Season |  | 23/05/2025 | All Parts Found Ok. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | S.Pandey /Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## MOV-103-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- MAIN STEAM INLET DRAIN MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-103
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29400301
Actuater type |  |  | K30 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z60 TGZ
O/P speed |  |  | 36.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.27 KW 3PH |  |  | Avg. Load |  |  | 0.70 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2024-01-05 | All Parts Found Ok. |  | 1. Oil Level Checked, Found Ok. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 19/05/2025 | Potentiometer (1 K) & indication bulb found not ok |  | 1.Replaced the potentiometer & indicating bulb |  |  |  | Internal | S.Pandey/Pankaj Singh
2.Clean the each parts of actuator.
3.Checked the limit assembly & contacts.
4. Thrust Bearing Cleaning & Checking done.
5.Checked Remote / Local Operation.

## MOV-401-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- STEAM TO HOGGER EJECTOR MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-401
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29400401
Actuater type |  |  | K30 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z60 TGZ
O/P speed |  |  | 36.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.090 KW 3PH |  |  | Avg. Load |  |  | 0.50 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2024-05-04 | All Parts Found Ok. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | Dilip Jha/Pankaj
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 13/05/2025 | Potentiometer (1 K) & indication bulb found not ok |  | 1.Replaced the potentiometer & indicating bulb |  |  |  | Internal | S.Pandey/Pankaj Singh
2.Clean the each parts of actuator.
|  |  | Cable gland was not proper sealed |  | 3.Checked the limit assembly & contacts.
4. seal the cable gland with m-seal.
5.Checked Remote / Local Operation.

## MOV-402-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- STEAM TO STANDBY EJECTOR MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-402
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29401201
Actuater type |  |  | K30 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z00 TGZ
O/P speed |  |  | 72.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.270 KW 3PH |  |  | Avg. Load |  |  | 1.70 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2024-04-05 | All Parts Found Ok. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 14/05/2025 | indication bulb found not ok |  | 1.Replaced the indicating bulb |  |  |  | Internal | S.Pandey /Pankaj Singh
2.Clean the each parts of actuator.
3.Checked the limit assembly & contacts.
4.Checked Remote / Local Operation.

## MOV-403-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- STEAM TO Y1 EJECTOR MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-403
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29401101
Actuater type |  |  | K30 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z00 TGZ
O/P speed |  |  | 72.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.270 KW 3PH |  |  | Avg. Load |  |  | 1.70 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator & Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator & Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator & Thrust Bearing Checked.02 no.s bearing replaced.
OFF Season |  | 2024-03-05 | Oil Leakage Observed & Oil Level found low |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | Prashant / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
5. Replaced the oil seal.
OFF Season |  | 15/05/2025 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
5. Replaced the Handwheel O-ring

## MOV-404-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- AIR TO Y1 EJECTOR MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-404
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29210101
Actuater type |  |  | K30 F10 E |  |  | Wiring Diagram No. |  |  | 1687Z60 TGZ
O/P speed |  |  | 48.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.180 KW 3PH |  |  | Avg. Load |  |  | 0.90 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked.Ctrl Card Repaired.
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked.Ctrl Card Repaired.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Thrust BearingChecked.O-Ring of handwheel Replaced.
OFF Season |  | 2024-03-06 | All Parts Found Ok. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 14/05/2025 | indication bulb found not ok |  | 1.Replaced the potentiometer & indicating bulb |  |  |  | Internal | S.Pandey /Pankaj Singh
2.Clean the each parts of actuator.
3.Checked the limit assembly & contacts.
4.Checked Remote / Local Operation.

## MOV-405-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- AIR TO STANDBY EJECTOR MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-405
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29210102
Actuater type |  |  | K30 F10 E |  |  | Wiring Diagram No. |  |  | 1687Z00 TGZ
O/P speed |  |  | 48.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.180 KW 3PH |  |  | Avg. Load |  |  | 0.90 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Bush operated Checked
OFF Season |  | 26/04/2024 | All Parts Found Ok. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 15/05/2025 | indication bulb found not ok |  | 1.Replaced the indicating bulb |  |  |  | Internal | S.Pandey /Pankaj Singh
2.Clean the each parts of actuator.
3.Checked the limit assembly & contacts.
4.Checked Remote / Local Operation.

## MOV-406-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- AIR TO HOGGER EJECTOR MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-406
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B3155010
Actuater type |  |  | K30 F10 E |  |  | Wiring Diagram No. |  |  | 1687Z00 TGZ
O/P speed |  |  | 48.RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.180 KW 3PH |  |  | Avg. Load |  |  | 0.90 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2019 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked
OFF Season |  | 2021 | All Parts Found Ok |  | Only Bush operated Checked
OFF Season |  | 2024-04-05 | All Parts found Ok. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
5. Replaced the handwheel "o"ring.
OFF Season |  | 14/05/2025 | indication bulb found not ok |  | 1.Replaced the indicating bulb |  |  |  | Internal | S.Pandey /Pankaj Singh
2.Clean the each parts of actuator.
3.Checked the limit assembly & contacts.
4.Checked Remote / Local Operation.

## MOV-407-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- CONDENSATE TO EJECTOR MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-407
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29400701
Actuater type |  |  | K60 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z60 TGZ
O/P speed |  |  | 72.0 RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.520 KW 3PH |  |  | Avg. Load |  |  | 2.40 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2024-03-05 | All Parts found Ok. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 13/05/2025 | indication bulb found not ok |  | 1.Replaced the indicating bulb |  |  |  | Internal | S.Pandey /Pankaj Singh
2.Clean the each parts of actuator.
3.Checked the limit assembly & contacts.
4.Checked Remote / Local Operation.

## MOV-408-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- CONDENSATE FROM EJECTOR MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-408
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29400801
Actuater type |  |  | K60 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z60 TGZ
O/P speed |  |  | 72.0 RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.520 KW 3PH |  |  | Avg. Load |  |  | 2.40 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2024-03-05 | All Parts found Ok. |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | Dilip Jha / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 13/05/2025 | indication bulb found not ok |  | 1.Replaced the indicating bulb |  |  |  | Internal | S.Pandey /Pankaj Singh
2.Clean the each parts of actuator.
3.Checked the limit assembly & contacts.
4.Checked Remote / Local Operation.

## MOV-411-2024 (hidden)
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- MOTIVE STEAM HEADER DRAIN MOV )
EQUIPMENT TAG NAME: | [5 empty] | MOV-411
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | Rotork control India pvt.ltd |  |  | Sr. No. |  |  | 2B29400201
Actuater type |  |  | K30 F10 A |  |  | Wiring Diagram No. |  |  | 1687Z60 TGZ
O/P speed |  |  | 48.0 RPM |  |  | Lubricant |  |  | SAE80EP Or ALPHA SP68
Motor |  |  | 0.180 KW 3PH |  |  | Avg. Load |  |  | 0.90 A
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season | [10 empty] | NA

## PCW-13-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- MCWP-A DISCHARGE MOV )
EQUIPMENT TAG NAME: | [5 empty] | PCW-13
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 5033814002-GB-01
Actuater type |  |  | SA12E 180 |  |  | Wiring Diagram No.
O/P speed |  |  | 180.0 RPM |  |  | Lubricant |  |  | EP 0
Motor | [5 empty] | Avg. Load
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 13/07/2024 | All Parts Found Ok. |  | 1. Grease Quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 23/05/2025 | All Parts Found Ok. |  | 1. Grease Quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PCW-14-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- MCWP-B DISCHARGE MOV )
EQUIPMENT TAG NAME: | [5 empty] | PCW-14
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 5033814002-GB-02
Actuater type |  |  | SA12E 180 |  |  | Wiring Diagram No.
O/P speed |  |  | 180.0 RPM |  |  | Lubricant |  |  | EP 0
Motor | [5 empty] | Avg. Load
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2024-09-07 | All Parts Found Ok. |  | 1. Grease Quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 23/05/2025 | All Parts Found Ok. |  | 1. Grease Quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PCW-15-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- MCWP-C DISCHARGE MOV )
EQUIPMENT TAG NAME: | [5 empty] | PCW-14
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 5033814002-GB-03
Actuater type |  |  | SA12E 180 |  |  | Wiring Diagram No.
O/P speed |  |  | 180.0 RPM |  |  | Lubricant |  |  | EP 0
Motor | [5 empty] | Avg. Load
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2024-08-07 | All Parts Found Ok. |  | 1. Grease Quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 23/05/2025 | All Parts Found Ok. |  | 1. Grease Quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PCW-42-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- ACWP-A DISCHARGE MOV )
EQUIPMENT TAG NAME: | [5 empty] | PCW-42
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 5033814001-GB-02
Actuater type |  |  | SA3E 32 |  |  | Wiring Diagram No.
O/P speed |  |  | 32.0 RPM |  |  | Lubricant |  |  | EP 0
Motor | [5 empty] | Avg. Load
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2024-02-06 | All Parts Found Ok. |  | 1. Grease Quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 24/05/2025 | All Parts Found Ok. |  | 1. Grease Quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PCW-43-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- ACWP-B DISCHARGE MOV )
EQUIPMENT TAG NAME: | [5 empty] | PCW-43
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 5033814001-GB-01
Actuater type |  |  | SA3E 32 |  |  | Wiring Diagram No.
O/P speed |  |  | 32.0 RPM |  |  | Lubricant |  |  | EP 0
Motor | [5 empty] | Avg. Load
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2024-03-06 | All Parts Found Ok. |  | 1. Grease Quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 24/05/2025 | All Parts Found Ok. |  | 1. Grease Quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PCW-44-2024
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- ACWP-C DISCHARGE MOV )
EQUIPMENT TAG NAME: | [5 empty] | PCW-43
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 5033814001-GB-01
Actuater type |  |  | SA3E 32 |  |  | Wiring Diagram No.
O/P speed |  |  | 32.0 RPM |  |  | Lubricant |  |  | EP 0
Motor | [5 empty] | Avg. Load
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2025-02-06 | All Parts Found Ok. |  | 1. Grease Quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Kumar
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
OFF Season |  | 24/05/2025 | All Parts Found Ok. |  | 1. Grease Quantity Checked, Found Ok. |  |  |  | Internal | S.Pandey / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.

## PDW-38-2025
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- DEARATOR EMERGENCY MAKE-UP WATER LINE )
EQUIPMENT TAG NAME: | [5 empty] | PDW-38
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 5050014002
Actuater type |  |  | SA3A45 |  |  | Wiring Diagram No.
O/P speed |  |  | 45.0 RPM |  |  | Lubricant |  |  | EP 0
Motor | [5 empty] | Avg. Load
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
SN | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2018 | All Parts Found Ok |  | Only Actuator Checked.
OFF Season |  | 2019 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 2020 | All Parts Found Ok |  | Actuator and Thrust Bearing Checked.
OFF Season |  | 2021 | All Parts Found Ok |  | Actuator and Thrust Bearing not Checked.
OFF Season |  | 13/7/2024 | Actuator Not operated in local & remote |  | 1. Thurst Bearing Cleaning & Checking. |  |  |  | Internal | Prashant Shukla / Pankaj Singh
2. Clean the each parts of actuator.
3. Checked the limit assembly & contacts.
4. Checked Remote / Local Operation.
5. Replaced the logic interface card.
OFF Season |  | 15/5/2025 | All Parts Found Ok. |  | 1. Oil Level Checked Found Ok. |  |  |  | Internal | Dilip Jha/ Pankaj Singh
1. Clean the each parts of actuator.
2. Checked the limit assembly & contacts.
3. Checked Remote / Local Operation.

## BC-05
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Motorized Actuator
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler- NBC_PLOUGH)
EQUIPMENT TAG NAME: | [5 empty] | NBC_PLOUGH
DATE OF COMMISSIONING : | [5 empty] | 2015-10-05
EQUIPMENT SPECIFICATION
Make |  |  | AUMA |  |  | Sr. No. |  |  | 5050014002
Actuater type |  |  | SA12A90 |  |  | Wiring Diagram No.
O/P speed |  |  | 45.0 RPM |  |  | Lubricant |  |  | EP 0
Motor | [5 empty] | Avg. Load
Supply |  |  | 415 VAC |  |  | Year of Manufacture |  |  | 2014-01
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years
1 | Mechanical Part | Dismantling & Cleaning all internal parts |  | X | X | X | X | √ | X | X
|  | Checking of Yoke assembly & clutch Ring |  | X | X | X | X | √ | X | X
|  | Checking of thrust bearing & assembly |  | X | X | X | X | X | X | √
|  | Checking of Oil leakage (Oil Seal & O-ring) |  | X | X | X | X | √ | X | X
2 | Handwheel Assembly & Oil Level | Check handwheel retainer, felt seal & Oil level |  | X | X | X | X | √ | X | X
3 | Electronic Part | Cleaning & tightness all connection & connectors |  | X | X | X | X | √ | X | X
|  | Checking of Power card, Control card, transformer & contactors |  | X | X | X | X | √ | X | X
4 | Local/ Remote Operation | Checking the limit switch in open & close condition. Operation checked in local mode & remote mode (DCS) |  | X | X | X | X | √ | X | X
5 | Motor Assembly | Physical Checking of motor & IR Value measurement |  | X | X | X | X | X | X | √
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2024-07-13 | Not operate in local & remote |  | Logic interface card replaced. |  |  |  | Internal | Prahant
98 SHEET.