## Sheet_Summary
FCV-501A | FCV-501A (Boiler feed water 100% control valve-1)
FCV-501B | FCV-501B (Boiler feed water 100% control valve-2)
FCV-500 | FCV-500 (Boiler feed water 30% control valve)
PCV-503 | PCV-503 (Soot Blower control valve)
PCV-505 | PCV-505 (Boiler Start up vent control valve)
LCV-501 | LCV-501 (Boiler CBD Tank Level control valve)
TCV-501A | TCV-501A (Boiler Spray Water Temp. control valve for DSH-501)
TCV-501B | TCV-501B (Boiler Spray Water Bypass Temp. control valve for DSH-501)
TCV-502A | TCV-502A (Boiler Spray Water Temp. control valve For DSH-502)
TCV-502B | TCV-502B (Boiler Spray Water Bypass Temp. control valve for DSH-502)
PCV-509 | PCV-509 (Boiler 110/3 ATA Process PRDS control valve)
PCV-510 | PCV-510 (Boiler 110/3 ATA Dearator Steam Pr. control valve)
PCV-511A | PCV-511A (Boiler 110/8 ATA Auxiliary Steam Pr. control valve)
PCV-511B | PCV-511B (Boiler 110/8 ATA Auxiliary Steam Pr. Bypass control valve)
PRV-501 | PRV-501 (135/67 KG/CM2 Water Pressure Reducing Valve)
PCV-502 | PCV-502 (110/45 ATA Process Steam Pr. Control Valve)
TCV-509A | TCV-509A
TCV-510A | TCV-510B
TCV-511A | TCV-511A/SPRAY WATER TCV FOR 110/8 ATA AUX. STEAM PRDS
TCV-511B | TCV-511B/SPRAY WATER TCV FOR 110/8 ATA AUX. STEAM PRDS
TCV-604A | TCV-604A (Spray Water Control Valve For 110/45 ATA Steam PRDS)
BV-01 | BV-01 (Spray water on/off valve to DSH-502)
BV-02 | BV-02 (Spray water on/off valve to DSH-501)
BV-03 | BV-03 (Spray water on/off valve FOR 110/3 ATA process steam PRDS)
BV-04 | BV-04 (Spray water on/off valve FOR 110/3 ATA Dearator steam PRDS)
BV-05 | BV-05 (Spray water on/off valve FOR 110/8 Auxiliary steam PRDS)
PFW-09 | PFW-09 (Dearator Overflow On/Off Valve)
BV-07
DAM-901 | DAM-901 (ID FAN-A Suction Damper RPC))
DAM-902 | DAM-902 (ID FAN-B Suction Damper RPC))
DAM-903 | DAM-903 (SA FAN-A Suction Damper RPC))
DAM-904 | DAM-904 (SA FAN-B Suction Damper RPC))
DAM-905 | DAM-905 (FD FAN-A Suction Damper RPC))
DAM-906 | DAM-906 (FD FAN-B Suction Damper RPC))
DAM-907 | DAM-907 (DA FAN-A Suction Damper RPC))
DAM-908 | DAM-908 (DA FAN-B Suction Damper RPC))
APH-PC-M | APH-PC-M
APH-PC-S | APH-PC-M
ESP1-PC | APH-PC-M
ESP2-PC | APH-PC-M
ESP3-PC | APH-PC-M
ESP4-PC | APH-PC-M
TCV-509A NEW | TCV-509A
TCV-511A NEW | TCV-511A

## INDEX
Control Valve History (Instrument-Power Plant) |  |  | 2016 |  | 2017 |  | 2018 |  | 2019 |  | 2020 |  | 2021 |  | 2022 |  | 2023 |  | 2024 |  | 2025
S.N. | TAG NO. | DESCRIPTION | MAINTENANCE DATE |  | MAINTENANCE DATE |  | MAINTENANCE DATE |  | MAINTENANCE DATE |  | MAINTENANCE DATE |  | MAINTENANCE DATE |  | MAINTENANCE DATE |  | MAINTENANCE DATE |  | MAINTENANCE DATE |  | MAINTENANCE DATE
A | BOILER & PRDS Control Valves & power Cylinder |  | VALVE | ACTUATOR | VALVE | ACTUATOR | VALVE | ACTUATOR | VALVE | ACTUATOR | VALVE | ACTUATOR | VALVE | ACTUATOR | VALVE | ACTUATOR | VALVE | ACTUATOR | VALVE | ACTUATOR | VALVE | ACTUATOR
1 | FCV-501A | 100% FEED WATER CONTROL VALVE | [10 empty] | 27/7/0221 |  |  |  | 16/05/2023
2 | FCV-501B | 100% BYPASS FEED WATER CONTROL VALVE | [8 empty] | 27/07/2020 |  |  | 2021 | 2022-10-05 |  |  |  | 31/05/2024
3 | FCV-500 | 30% FEED WATER CONTROL VALVE |  |  | 27/07/2017 | [5 empty] | 25/06/2020 |  |  |  | 23/04/2022 | [5 empty] | 17/04/2025 | 16/04/2025
4 | PCV-503 | SOOT BLOWER CONTROL VALVE | [10 empty] | 23/07/2021 |  |  |  | 2023-10-06 |  | 2024-05-07 |  | 21/04/2025 | 20/04/2025
5 | PCV-505 | START UP VENT CONTROL VALVE | 2016-09-27 |  |  |  | 2018-07-10 |  |  |  | 15/11/2020 | [5 empty] | 29/08/2023 | 24/08/2023 |  |  | 2025-03-05 | 30/4/2025
6 | LCV-501 | CBD TANK LEVEL CONTROL VALVE | [10 empty] | 17/07/2021 |  |  |  | 13/6/2023
7 | TCV-501A | SPRAY WATER TEMP. CONTROL VALVE FOR DSH-501 | [8 empty] | 25/07/2020 | 25/07/2020 |  |  | 2022-09-06 |  |  |  | 28/05/2024
8 | TCV-501B | SPRAY WATER BYPASS TEMP. CONTROL VALVE FOR DSH-501 | [10 empty] | 2021-05-08 |  |  |  | 2023-03-06 |  |  |  | 2025-05-05 | 2025-05-05
9 | TCV-502A | SPRAY WATER TEMP. CONTROL VALVE FOR DSH-502 | [8 empty] | 26/07/2020 |  |  |  | 2022-10-06 |  |  |  | 29/05/2024
10 | TCV-502B | SPRAY WATER TEMP. CONTROL VALVE FOR DSH-502 | [10 empty] | 2021-06-08 |  |  |  | 23/08/2023 |  |  |  | 17/05/2025 | 17/05/2025
11 | PCV-509 | 110/3 ATA PROCESS STEAM PRESSURE CV | [8 empty] | 2020 |  |  |  |  | 2022
12 | PCV-510 | 110/3 ATA DEARATOR STEAM PRESS CONTROL VALVE | [14 empty] | 25/05/2023
13 | PCV-511A | 110/8 ATA AUX. STEAM PRESS REDUCING CONTROL VALVE | [8 empty] | 2020 | [5 empty] | 20/06/2023
14 | PCV-511B | 110/8 ATA AUX. STEAM PRESS REDUCING BYPASS CV | [10 empty] | 2021
15 | PRV-501 | 135/67 ATA FEED WATER PRESS CONTROL VALVE
16 | PCV-502 | 110/45 ATA STEAM PRESS CONTROL VALVE
17 | TCV-509A | 110/3 ATA PROCESS STEAM TEMPERATURE CV | 2016-09-27 |  | 2017-09-25 |  | 2018-10-22 |  | 2019-07-20 |  | 2020-07-24 |  | 2021-06-25 |  | 2022-05-18 |  | 30/8/2023
18 | TCV-510A | SPRAY WATER 110/3 ATA DEARATOR STEAM TCV | [16 empty] | 2024-02-08
19 | TCV-511A | SPRAY WATER TCV FOR 110/8 ATA AUX. STEAM PRDS | 2016 |  | 2017 |  | 2018 |  | 2019 |  |  |  | 2021 |  | 29/07/2022 |  | 27/06/2023
20 | TCV-511B | SPRAY WATER BYPASS TCV FOR 110/8 ATA AUX. STEAM PRDS |  |  | 2017 |  | 2018 |  | 2019 |  | 2020 |  | 2021 |  | 2022 |  |  |  | 28/07/2024
21 | TCV-604A | 110/45 ATA PRDS STEAM TEMPERATURE CV
22 | BV-01 | SPRAY WATER ON/OFF CONTROL VALVE TO DSH-501 | [10 empty] | 2021-08-07 | 2021-08-07 |  |  | 2023-05-06
23 | BV-02 | SPRAY WATER ON/OFF CONTROL VALVE TO DSH-502 | [12 empty] | 2022-11-06
24 | BV-03 | SP. WATER ON/OFF TCV FOR 110/3 ATA PRO. STEAM PRDS | 2016 | [5 empty] | 2019 | [5 empty] | 18/04/2022 |  | 31/05/2023 |  |  |  | 14/05/2025 | 13/05/2025
25 | BV-04 | SP. WATER ON/OFF TCV FOR 110/3 ATA DEA. STEAM PRDS | [12 empty] | 2022 | 2022 |  |  | 2024-02-08
26 | BV-05 | SP. WATER ON/OFF TCV FOR 110/8 ATA AUX. STEAM PRDS | [12 empty] | 2022 | 2022 | 30/06/2023
27 | PFW-09 | DEARATOR OVERFLOW ON/FF CONTROL VALVE | [14 empty] | 27/05/2023
28 | BV-07 | SPRAY WATER ON/OFF TCV FOR 110/45 ATA STEAM PRDS
29 | DAM-901 | ID FAN-A POWER CYLINDER | [10 empty] | 2021 |  | 2022 | [5 empty] | 16/05/2025 | 16/05/2025
30 | DAM-902 | ID FAN-B POWER CYLINDER | [10 empty] | 2021 |  |  |  | 2023-07-08
31 | DAM-903 | SA FAN-A POWER CYLINDER | [12 empty] | 2022-06-08 | [5 empty] | 19/05/2025 | 19/05/2025
32 | DAM-904 | SA FAN-B POWER CYLINDER | [12 empty] | 25/08/2022 |  | 20/08/2023
33 | DAM-905 | FD FAN-A POWER CYLINDER | [12 empty] | 2022
34 | DAM-906 | FD FAN-B POWER CYLINDER | [12 empty] | 2022 |  | 13/8/2023
35 | DAM-907 | DA FAN-A POWER CYLINDER
36 | DAM-908 | DA FAN-B POWER CYLINDER
37 | APH-PC-M | APH Master Dome Valve Power Cylinder | [16 empty] | 14/06/2024
38 | APH-PC-S | APH Slave Dome Valve Power Cylinder | [16 empty] | 14/6/2024
39 | ESP1-PC | ESP-1 Dome Valve Power Cylinder | [16 empty] | 29/5/2024
40 | ESP2-PC | ESP-2 Dome Valve Power Cylinder | [16 empty] | 30/05/2024
41 | ESP3-PC | ESP-3 Dome Valve Power Cylinder | [16 empty] | 21/06/2024
42 | ESP4-PC | ESP-4 Dome Valve Power Cylinder | [16 empty] | 31/05/2024
Total 40 Nos. history sheet ready

## FCV-501A
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | FCV-501A (Boiler feed water 100% control valve-1)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140761
Model No. |  |  | 37-41921 |  |  | Body Size/ Actuator Size |  |  | 6"/ 18"-8A
Rating/End |  |  | ASME#1500 (SW) |  |  | Cv/CHA |  |  | 255, Equal%
Stroke/ Seat Leak class |  |  | 50.8 MM/ CLASS IV |  |  | Body/ Trim |  |  | WCC, 17.4 PH+SS316ST
Range/ Supply/ Signal |  |  | 6-30PSI/55PSI/4-20mA |  |  | Air Fail/ Packing |  |  | Open/ Graphite
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 27/07/2021 | Bottom portion of bonnet found heavy eroded. |  | Eroded Portion Repaired by Welding & Machining . Minor Lapping done of seat / Seal Ring, Gland Packing, Body gasket & Seat Gasket Replace. |  |  |  | Internal
OFF Season(preventive) |  | 16/05/2023 | Bottom portion of bonnet found slightly eroded. |  | Minor lapping done of seat & Plug. / Gland Packing, Body gasket & Seat Gasket Replaced. |  |  |  | Internal | S.Pandey/ Amit
OFF Season(preventive) |  | 2025-07-05 | Gland Packing found Leakage from Upper side. |  | Gland packing upper side Replaced with new. |  |  |  | Internal | Amleshwar/ Amit | N.A

## FCV-501B
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | FCV-501B (Boiler feed water 100% control valve-2)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140762
Model No. |  |  | 37-41921 |  |  | Body Size/ Actuator Size |  |  | 6"/ 18"-8A
Rating/End |  |  | ASME#1500 (BW) |  |  | Cv/CHA |  |  | 255, Equal%
Stroke/ Seat Leak class |  |  | 50.8 MM/ CLASS IV |  |  | Body/ Trim |  |  | WCC, 17.4 PH+SS316ST
Range/ Supply/ Signal |  |  | 6-30PSI/55PSI/4-20mA |  |  | Air Fail/ Packing |  |  | Open/ Graphite
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X | √
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X | X
|  | Seat, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | √ | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season (Preventive) |  | 27/07/2020 | Bottom portion of bonnet found eroded. Seal Ring found crack. |  | Eroded portion repaired by welding & grinding. Minor lapping done of seat & plug. Seal Ring, Gland Packing, Body gasket, Seat Gasket & Actuator Diaphragm replaced. |  |  | 55000 | Internal | Sushil Rai & Brijesh Kumar | During trial air leakage found in actuator diaphragm. Checked & crack found in rubber diaphragm. So replaced by new.
Off Season (Preventive) |  | 2021 | Actuator all Parts Found ok. |  | Diaphragm,Spring and Actuator Bolt tightness work done. |  |  |  | Internal |  | NA
Off Season (Preventive) |  | 2022-10-05 | Bottom portion of bonnet found eroded (Same place as previously). |  | Eroded portion repaired by welding & grinding. Minor lapping done of seat & plug. Gland Packing, Body gasket & Seat Gasket replaced. |  |  | 15000 | Internal | Vikas Kumar & Nishant Shukla | Erroded portion of Bonnet checked by MIL engineer at GSML site. Matter is discussed in MIL Head office. Replacement of bonnet suggested by MIL.
Off Season (Preventive) |  | 31/05/2024 | Bonnet portion found normal. Seal Ring found crack. Actuator found ok. |  | Seat & Plug lapping done. Replaced The Body Gasket, seat gasket, upper gland packing & seal ring. |  |  | 40000 | Internal | Amleshwar & Amit Kumar | NA
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## FCV-500
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | FCV-500 (Boiler feed water 30% control valve)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140405
Model No. |  |  | 37-41421 |  |  | Body Size/ Actuator Size |  |  | 3"/ 18"-8A
Rating/End |  |  | ASME#1500 (SW) |  |  | Cv/CHA |  |  | 90, Equal%
Stroke/ Seat Leak class |  |  | 50.8 MM/ CLASS IV |  |  | Body/ Trim |  |  | WCC, 17.4 PH+SS316ST
Range/ Supply/ Signal |  |  | 6-30PSI/55PSI/4-20mA |  |  | Air Fail/ Packing |  |  | Open/ Graphite
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off- Season (Preventive) |  | 27/07/2017 | Gland Packing Found Leakage |  | Minor lapping work done./ Gland packing, Seat & body gasket |  |  |  | Internal
Off- Season (Preventive) |  | 25/06/2020 | Gland Packing Found Leakage |  | Minor lapping work done. / Gland packing, Seat & body gasket |  |  |  | Internal
Off- Season (Preventive) |  | 23/04/2022 | All parts found in good condition. |  | Seat Gasket & body gasket |  |  |  | Internal
Off- Season (Preventive) |  | 17/04/2025 | All parts found in good condition. |  | Seat & Plug minor lapping done. Replaced The Body Gasket and seat gasket. |  |  |  | Internal | Amleshwar/ Amit | N.A

## PCV-503
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | PCV-503 (Soot Blower control valve)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140763
Model No. |  |  | 37-41114 |  |  | Body Size/ Actuator Size |  |  | 2"/ 15"-6A3
Rating/End |  |  | ASME#1500 (BW) |  |  | Cv/CHA |  |  | 107, Equal%
Stroke/ Seat Leak class |  |  | 38.1 MM/ CLASS V |  |  | Body/ Trim |  |  | WCC, CA6NMND
Range/ Supply/ Signal |  |  | 6-30PSI/55PSI/4-20mA |  |  | Air Fail/ Packing |  |  | Open/ Graphite
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 23/07/2021 | Stem of valve plug found bend. |  | New Plug Stem & seat ring , Seat & body gasket Replaced. |  |  |  | Internal
OFF Season(Preventive) |  | 2023-10-06 | All Parts Found Ok. |  | Plug and Seat Minor Lapping done.No Spare used. |  |  |  | Internal |  | N.A
OFF Season(Preventive) |  | 2024-05-07 | All Parts Found Ok. |  | Seat & Plug minor lapping done. Replaced The Body Gasket and seat gasket. |  |  |  | Internal | Amleshwar/ Amit | N.A
Off- Season (Preventive) |  | 21/04/2025 | All Parts Found Ok. |  | Seat & Plug minor lapping done. Replaced The Body Gasket and seat gasket. |  |  |  | Internal | Amleshwar/ Amit | N.A

## PCV-505
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | PCV-505 (Boiler Start up vent control valve)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140765
Model No. |  |  | 38-41433 |  |  | Body Size/ Actuator Size |  |  | 6"/ 18"-6A3
Rating/End |  |  | ASME#2500 (BW) |  |  | Cv/CHA |  |  | 95.0000/MOD/Equal%
Stroke/ Seat Leak class |  |  | 50.8 MM/ CLASS V |  |  | Body/ Trim |  |  | WC9, CA6NMND+SS316
Range/ Supply/ Signal |  |  | 14-27PSI/35PSI/4-20mA |  |  | Air Fail/ Packing |  |  | Close/ Graphite
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2016-09-27 | Huge cut mark found on valve plug & seat ring. 07 Nos. Cage holes found in closed condition by welding flux. |  | Valve plug, seat ring, gland packing, Seat & body gasket Replaced
OFF Season(Preventive) |  | 2018-07-10 | All parts found in good condition. |  | Minor lapping done.Gland packing, Seat & body gasket Replaced.
OFF Season(Preventive) |  | 15/11/2020 | All parts found in good condition. |  | Minor lapping done.Gland packing, Seat & body gasket
OFF Season(Preventive) |  | 29/08/2023 | Huge cut mark found on valve plug & seat ring. |  | seat gasket,plug,graphite o ring Replaced | [5 empty] | N.A
OFF Season(Preventive) |  | 2025-03-05 | Found gland packing Upper side cut.Plug Found dented condition. |  | Major lapping done.Gland packing upper-lower side,Seat and body gasket replaced. |  |  |  | Internal | Amleshwar/ Amit | N.A

## LCV-501
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | LCV-501 (Boiler CBD Tank Level control valve)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140518
Model No. |  |  | 37-21125 |  |  | Body Size/ Actuator Size |  |  | 1.5"/ 11"-6A1
Rating/End |  |  | ASME#150 (RF) |  |  | Cv/CHA |  |  | 10, Equal%
Stroke/ Seat Leak class |  |  | 19.05 MM/ CLASS IV |  |  | Body/ Trim |  |  | WCC, SS316ST+SS316ST
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing |  |  | Open/ PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2021-07-17 | All parts found Ok. |  | Minor Lapping Done Of Seat & Plug.No Spare Used |  |  |  | Internal
OFF Season(Preventive) |  | 13/06/2023 | All parts found Ok. |  | Minor Lapping Done Of Seat & Plug. No Spare Used. |  |  |  | Internal | S.Pandey/Amit
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## TCV-501A
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | TCV-501A (Boiler Spray Water Temp. control valve for DSH-501)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140269
Model No. |  |  | 37-41121 |  |  | Body Size/ Actuator Size |  |  | 1"/ 11"-6A1
Rating/End |  |  | ASME#1500 (BW) |  |  | Cv/CHA |  |  | 8, Equal%
Stroke/ Seat Leak class |  |  | 19.05 MM/ CLASS V |  |  | Body/ Trim |  |  | WCC, 17.4 PH+SS316ST
Range/ Supply/ Signal |  |  | 7-17PSI/50PSI/4-20mA |  |  | Air Fail/ Packing |  |  | Stay Put/ PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2020-07-25 | minor cut found in actuator rubber diaphragm. |  | Seat and Plug Minor Lapping done.New Rubber Diaphragm Replaced.
OFF Season |  | 2022-06-09 | All parts found in good condition. |  | Seat and plug minor lapping done .Replaced Seat Gasket & body gasket
OFF Season |  | 2024-05-28 | All parts Found ok |  | Seat & Plug minor lapping done. Replaced The Body Gasket and seat gasket. |  |  |  | Internal | Amleshwar/ Amit | N.A
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## TCV-501B
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | TCV-501B (Boiler Spray Water Bypass Temp. control valve for DSH-501)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140758
Model No. |  |  | 37-41121 |  |  | Body Size/ Actuator Size |  |  | 1"/ 11"-6A1
Rating/End |  |  | ASME#1500 (BW) |  |  | Cv/CHA |  |  | 8, Equal%
Stroke/ Seat Leak class |  |  | 19.05 MM/ CLASS V |  |  | Body/ Trim |  |  | WCC, 17.4 PH+SS316ST
Range/ Supply/ Signal |  |  | 7-17PSI/50PSI/4-20mA |  |  | Air Fail/ Packing |  |  | Stay Put/ PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(preventive) |  | 2021-08-05 | All parts found in good condition |  | Minor Lapping Done of Seat & Plug . Replaced Gland packing. | [5 empty] | N.A
OFF Season(preventive) |  | 2023-03-06 | All parts found in good condition |  | Minor Lapping Done of Seat & Plug . Replaced Body Gasket Replaced. |  |  |  | Internal | Rajesh Diwedi/ Amit | N.A
OFF Season(preventive) |  | 2025-05-05 | All parts found in good condition |  | Minor Lapping Done of Seat & Plug . Replaced Seat Gasket. |  |  |  | Internal | Amleshwar / Amit | N.A

## TCV-502A
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | TCV-502A (Boiler Spray Water Temp. control valve For DSH-502)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140759
Model No. |  |  | 37-41121 |  |  | Body Size/ Actuator Size |  |  | 1"/ 11"-6A
Rating/End |  |  | ASME#1500 (SW) |  |  | Cv/CHA |  |  | 6, Equal%
Stroke/ Seat Leak class |  |  | 19.05 MM/ CLASS V |  |  | Body/ Trim |  |  | WCC, 17.4 PH+SS316ST
Range/ Supply/ Signal |  |  | 7-17PSI/50PSI/4-20mA |  |  | Air Fail/ Packing |  |  | Stay Put/ PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season (Preventive) |  | 2020-07-26 | All parts found ok. |  | Nil | [5 empty] | N.A
OFF Season (Preventive) |  | 2022-06-10 | All parts found ok. |  | Seat Gasket & body gasket Replaced | [5 empty] | N.A
OFF Season (Preventive) |  | 2024-05-29 | All parts found ok. |  | Seat & Plug minor lapping done. Replaced The Body Gasket and seat gasket. |  |  |  | Internal | Amleshwar/ Amit | N.A
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## TCV-502B
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | TCV-502B (Boiler Spray Water Bypass Temp. control valve for DSH-502)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140760
Model No. |  |  | 37-41121 |  |  | Body Size/ Actuator Size |  |  | 1"/ 11"-6A
Rating/End |  |  | ASME#1500 (SW) |  |  | Cv/CHA |  |  | 6, Equal%
Stroke/ Seat Leak class |  |  | 19.05 MM/ CLASS V |  |  | Body/ Trim |  |  | WCC, 17.4 PH+SS316ST
Range/ Supply/ Signal |  |  | 7-17PSI/50PSI/4-20mA |  |  | Air Fail/ Packing |  |  | Stay Put/ PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2021-08-06 | All parts found ok. |  | Minor Lapping done of seat and Plug. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 23/08/2023 | All parts found ok. |  | Minor Lapping done of seat and Plug. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 17/05/2025 | All parts found ok. |  | Minor Lapping done of seat and Plug.only body gasket Replaced. |  |  |  | Internal | Amleshwar | NA

## PCV-509
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | PCV-509 (Boiler 110/3 ATA Process PRDS control valve)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140748
Model No. |  |  | 38-41432 |  |  | Body Size/ Actuator Size |  |  | 6"/ 18"-8A
Rating/End |  |  | ASME#2500 (BW) |  |  | Cv/CHA |  |  | 145/MOD/LO-DB Equal%
Stroke/ Seat Leak class |  |  | 63.5+5.78 MM/ CLASS V |  |  | Body/ Trim |  |  | WC9, CA6NMND+SS316ST
Range/ Supply/ Signal |  |  | 17-46PSI/55PSI/4-20mA |  |  | Air Fail/ Packing |  |  | Stay Put/ Graphite
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2020 | Bottom portion of plug found dent and eroded. |  | Stem Plug, gland packing, body & seat gasket replaced |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 2022 | Actuator all parts Found Ok. |  | Actuator Diaphragm,Spring and bolt tightness work done. |  |  |  | Internal |  | NA
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## PCV-510
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | PCV-510 (Boiler 110/3 ATA Dearator Steam Pr. control valve)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140751
Model No. |  |  | 38-41114 |  |  | Body Size/ Actuator Size |  |  | 2"/ 18"-6A3
Rating/End |  |  | ASME#2500 (BW) |  |  | Cv/CHA |  |  | 12/2ST/LO-DB LIN
Stroke/ Seat Leak class |  |  | 38.1 MM/ CLASS V |  |  | Body/ Trim |  |  | WC9, CA6NMND+SS316ST
Range/ Supply/ Signal |  |  | 20-30PSI/35PSI/4-20mA |  |  | Air Fail/ Packing |  |  | STAY PUT/ Graphite
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 25/5/2023 | All Parts Found Ok. |  | Plug and Seat Minor lapping done.No Spare Used. |  |  |  | Internal |  | NA
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## PCV-511A
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | PCV-511A (Boiler 110/8 ATA Auxiliary Steam Pr. control valve)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140754
Model No. |  |  | 37-41132 |  |  | Body Size/ Actuator Size |  |  | 1"/ 11"-6A1
Rating/End |  |  | ASME#2500 (BW) |  |  | Cv/CHA |  |  | 2.5/MOD/LO-DB EQUAL%
Stroke/ Seat Leak class |  |  | 19.05 MM/ CLASS V |  |  | Body/ Trim |  |  | WC9, CA6NMND+SS316ST
Range/ Supply/ Signal |  |  | 3-12PSI/40PSI/4-20mA |  |  | Air Fail/ Packing |  |  | Open/ Graphite
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2020 | All parts Found Ok. |  | Minor Lapping done of seat and Plug.No Spare used |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 20/6/2023 | All parts Found Ok. |  | Minor Lapping done of seat and Plug.Seat and Body Gasket Replaced. |  |  |  | Internal | S.pandey/Amit | NA
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## PCV-511B
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | PCV-511B (Boiler 110/8 ATA Auxiliary Steam Pr. Bypass control valve)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140755
Model No. |  |  | 37-41132 |  |  | Body Size/ Actuator Size |  |  | 1"/ 11"-6A1
Rating/End |  |  | ASME#2500 (BW) |  |  | Cv/CHA |  |  | 2.5/MOD/LO-DB EQUAL%
Stroke/ Seat Leak class |  |  | 19.05 MM/ CLASS V |  |  | Body/ Trim |  |  | WC9, CA6NMND+SS316ST
Range/ Supply/ Signal |  |  | 3-12PSI/40PSI/4-20mA |  |  | Air Fail/ Packing |  |  | Open/ Graphite
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2021 | Actuator and Valve all Parts found ok. |  | Minor Lapping done plug and seat.No spare used. |  |  |  | Internal |  | NA
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## PRV-501
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | PRV-501 (135/67 KG/CM2 Water Pressure Reducing Valve)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 20003452
Model No. |  |  | 37-78104 |  |  | Body Size/ Actuator Size |  |  | 1"/ 11"-6A1
Rating/End |  |  | ASME#1500 (SW) |  |  | Cv/CHA |  |  | 1.2/MS.AC.MOD%
Stroke/ Seat Leak class |  |  | 12.7 MM/ CLASS V |  |  | Body/ Trim |  |  | A105, 440C+SLD ST
Range/ Supply/ Signal |  |  | 16-30PSI/35PSI/4-20mA |  |  | Air Fail/ Packing |  |  | STAY PUT/ PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## PCV-502
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | PCV-502 (110/45 ATA Process Steam Pr. Control Valve)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 20003200
Model No. |  |  | 38-41432 |  |  | Body Size/ Actuator Size |  |  | 3"/ 15"-6A3
Rating/End |  |  | ASME#2500 (BW) |  |  | Cv/CHA |  |  | 50/MOD/LO-DB EQUAL2
Stroke/ Seat Leak class |  |  | 38.1 MM/ CLASS V |  |  | Body/ Trim |  |  | WC9, CA6NMND+SS316+ST NO.6
Range/ Supply/ Signal |  |  | 14-31PSI/40PSI/4-20mA |  |  | Air Fail/ Packing |  |  | STAY PUT/ Graphite
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## TCV-509A
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | TCV-509A
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140750
Model No. |  |  | 20G-41132 |  |  | Body Size/ Actuator Size |  |  | 2"/
Rating/End |  |  | ASME#1500(BW) |  |  | Cv/CHA |  |  | 3.8/ANTI-CAV Equal%MOD
Stroke/ Seat Leak class |  |  | 19.05MM/ CLASS V |  |  | Body/ Trim |  |  | WCC/17.4PH+SS410
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing |  |  | / PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2016-09-27 | Seat Ring & Valve Plug found eroded. Checked by MIL (OEM) engineer & recommended to replace the seat & plug. |  | Nil |  |  |  | External |  | Seat & plug was not replaced due to spare parts was not available in inventory.
OFF Season(Preventive) |  | 2017-09-25 | Seat Ring & Valve Plug found eroded. |  | Replaced with new Valve plug & seat ring, | [5 empty] | All replaced parts provided by FC-KCP On FOC basis under warranty.
OFF Season(Preventive) |  | 2018-10-22 | Valve Plug found eroded. Checked by MIL (OEM) engineer & recommended to replace the valve plug. Lapping done with new valve plug & existing seat ring. |  | Lapping done with new valve plug and existing seat ring .Replaced with new Valve plug, Seat & body gasket | [5 empty] | OEM assure to send the root cause of problem after review the current flow parameters as per data sheet.
OFF Season(Preventive) |  | 2019-07-20 | Pitting found in Valve Plug & seat ring. Lapping done with existing valve plug & existing seat ring. |  | Lapping done with existing valve plug and existing valve plug.Replaced with new Gland packing, | [5 empty] | Root cause of problem was not provided by OEM
OFF Season(Preventive) |  | 2020-07-24 | Seat Ring & Valve Plug found eroded. Lapping done with existing valve plug & existing seat ring. |  | Lapping done with existing valve plug and existing valve plug. | [5 empty] | Root cause of problem was not provided by OEM
OFF Season(Preventive) |  | 2021-06-25 | Seat Ring & Valve Plug found eroded. Replaced with new Seat Ring & Valve Plug |  | Replaced with new Valve plug, seat ring, Seat & body gasket | [5 empty] | Leakage observed after 01 month running in season 2021-22.
OFF Season(Preventive) |  | 2022-05-18 | Seat Ring & Valve Plug found in good condition. But inside the valve body found eroded. Hole found in internal body of control valve near base of seat gasket. |  | Nill | [5 empty] | OEM recommonded to change the existing valve with new valve to suit this application (High Inlet Pressure)
OFF Season(Preventive) |  | 30/08/2023 | All Parts Found Ok. |  | Minor lapping done of seat and plug. Seat & body gasket replaced. |  |  |  | Internal
Season 2023-2024 |  | 17/1/2024 | OLD 3ata valve Removed from Process |  | New Valve Installation done. |  |  |  | Internal | Dilip Jha | Installation date-17/1/2024
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## TCV-510A
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | TCV-510B
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140753
Model No. |  |  | 16-29261 |  |  | Body Size/ Actuator Size |  |  | 1"/
Rating/End |  |  | ASME#1500(BW) |  |  | Cv/CHA |  |  | 0.46/
Stroke/ Seat Leak class |  |  | 19.05MM/ CLASS V |  |  | Body/ Trim |  |  | A105/SLDST17.4PH
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing |  |  | / PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(preventive) |  | 2024-02-08 | All Parts Found Ok. |  | Seat & Plug minor lapping done. |  |  |  | Internal | Amleshwar/ Amit | N.A
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## TCV-511A
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | TCV-511A/SPRAY WATER TCV FOR 110/8 ATA AUX. STEAM PRDS
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140756
Model No. |  |  | 17-29234 |  |  | Body Size/ Actuator Size |  |  | 1"/
Rating/End |  |  | #1500/#1500 BW |  |  | Cv/CHA |  |  | 0.036
Stroke/ Seat Leak class |  |  | 25 MM/ |  |  | Body/ Trim |  |  | A 105/17.4PH
Range/ Supply/ Signal |  |  | 30 PSI/4-20 MA |  |  | Air Fail/ Packing |  |  | STAY PUT / PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2016 | All Parts Found Ok |  | Minor Lapping done of Plug and seat.No Spare used. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 2017 | All Parts Found Ok |  | Minor Lapping done of Plug and seat.No Spare used. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 2018 | All Parts Found Ok |  | Minor Lapping done of Plug and seat.No Spare used. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 2019 | All Parts Found Ok |  | Minor Lapping done of Plug and seat.No Spare used. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 2021 | Plug Found in dent condition |  | Plug replaced by old and seat gasket replaced. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 29/07/2022 | All Parts Found Ok |  | Minor Lapping done of Plug and seat.No Spare used. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 27/06/2023 | All Parts Found Ok |  | Seat gasket replaced. |  |  |  | Internal |  | NA
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## TCV-511B
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | TCV-511B/SPRAY WATER TCV FOR 110/8 ATA AUX. STEAM PRDS
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140756
Model No. |  |  | 17-29234 |  |  | Body Size/ Actuator Size |  |  | 1"/
Rating/End |  |  | #1500/#1500 BW |  |  | Cv/CHA |  |  | 0.036
Stroke/ Seat Leak class |  |  | 25 MM/ |  |  | Body/ Trim |  |  | A 105/17.4PH
Range/ Supply/ Signal |  |  | 30 PSI/4-20 MA |  |  | Air Fail/ Packing |  |  | STAY PUT / PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2017 | Plug and seat found in dent condition |  | Plug & seat replaced. |  |  |  | Internal
OFF Season(Preventive) |  | 2018 | All Parts found Ok |  | Minor lapping done of plug and seat. |  |  |  | Internal
OFF Season(Preventive) |  | 2019 | Plug found in dent condition. |  | Plug stem replaced by new. |  |  |  | Internal
OFF Season(Preventive) |  | 2020 | All Parts found Ok |  | Minor lapping done of plug and seat. |  |  |  | Internal
OFF Season(Preventive) |  | 2021 | All Parts found Ok |  | Minor lapping done of plug and seat .Seat gasket Replaced. |  |  |  | Internal
OFF Season(Preventive) |  | 2022 | All Parts found Ok |  | Minor lapping done of plug and seat. |  |  |  | Internal
OFF Season(Preventive) |  | 28/07/2024 | Found upper side gland cut. |  | Seat & Plug major lapping done. Replaced The Gland Packing set. |  |  |  | Internal | Shailendra pandey/ Amit | Upper side Gland Leakeage.
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## TCV-604A
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | TCV-604A (Spray Water Control Valve For 110/45 ATA Steam PRDS)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 20003168
Model No. |  |  | 37-78124 |  |  | Body Size/ Actuator Size |  |  | 1"/ 11"-6A1
Rating/End |  |  | ASME#1500 (SW) |  |  | Cv/CHA |  |  | 6/MS.AC.MOD%
Stroke/ Seat Leak class |  |  | 12.7 MM/ CLASS V |  |  | Body/ Trim |  |  | A105, SS440C+SLD ST NO.6
Range/ Supply/ Signal |  |  | 3-15PSI/40PSI/4-20mA |  |  | Air Fail/ Packing |  |  | STAY PUT/ PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## BV-01
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | ON/OFF Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | BV-01 (Spray water on/off valve to DSH-502)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140719
Model No. |  |  | 37-412X1 |  |  | Body Size/ Actuator Size |  |  | 2"/13"-6A2
Rating/End |  |  | ASME#1500(BW) |  |  | Cv/CHA |  |  | 40, ON/OFF
Stroke/ Seat Leak class |  |  | 19.05MM/ CLASS V |  |  | Body/ Trim |  |  | WCC/17.4PH+SS316
Range/ Supply/ Signal |  |  | 9-15PSI/45PSI/4-20mA |  |  | Air Fail/ Packing |  |  | OPEN / PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Solenoid Valve & Coil | Dismantling & Cleaning of Solenoid Valve |  | X | X | X | √ | X | X
|  | Cleaning & Checking of SOV Coil |  | X | X | X | √ | X | X
|  | Servicing of Solenoid Valve |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2021-08-07 | All parts found Ok |  | Minor lapping done of seat and Plug.No Spare Used.
OFF Season(Preventive) |  | 2023-05-06 | All parts found Ok |  | Minor lapping done of seat and Plug.Seat and Body Gasket Replaced. |  |  |  | Internal | Rajesh Diwedi/ Amit
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## BV-02
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | ON/OFF Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | BV-02 (Spray water on/off valve to DSH-501)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140766
Model No. |  |  | 37-412X1 |  |  | Body Size/ Actuator Size |  |  | 2"/13"-6A2
Rating/End |  |  | ASME#1500(BW) |  |  | Cv/CHA |  |  | 40, ON/OFF
Stroke/ Seat Leak class |  |  | 19.05MM/ CLASS V |  |  | Body/ Trim |  |  | WCC/17.4PH+SS316
Range/ Supply/ Signal |  |  | 9-15PSI/45PSI/4-20mA |  |  | Air Fail/ Packing |  |  | OPEN / PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Solenoid Valve & Coil | Dismantling & Cleaning of Solenoid Valve |  | X | X | X | √ | X | X
|  | Cleaning & Checking of SOV Coil |  | X | X | X | √ | X | X
|  | Servicing of Solenoid Valve |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2022-11-06 | All parts found in good condition. |  | Minor lapping done of plug and seat. Seat Gasket & body gasket |  |  |  | Internal
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## BV-03
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | ON/OFF Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | BV-03 (Spray water on/off valve FOR 110/3 ATA process steam PRDS)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140406
Model No. |  |  | 37-412X1 |  |  | Body Size/ Actuator Size |  |  | 3"/15"-6A3
Rating/End |  |  | ASME#1500(BW) |  |  | Cv/CHA |  |  | 90.0000, ON/OFF
Stroke/ Seat Leak class |  |  | 50.8MM/ CLASS V |  |  | Body/ Trim |  |  | WCC/17.4PH+SS316ST
Range/ Supply/ Signal |  |  | 3-15PSI/40PSI/4-20mA |  |  | Air Fail/ Packing |  |  | OPEN / PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Solenoid Valve & Coil | Dismantling & Cleaning of Solenoid Valve |  | X | X | X | √ | X | X
|  | Cleaning & Checking of SOV Coil |  | X | X | X | √ | X | X
|  | Servicing of Solenoid Valve |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2016 | All Parts Found ok. |  | Plug and Seat Minor Lapping done.No spare used. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 2019 | All Parts Found ok. |  | Plug and Seat Minor Lapping done.No spare used. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 18/04/2022 | All Parts Found ok. |  | Plug and Seat Minor Lapping done.Body and seat gasket replaced. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 31/05/2023 | All Parts Found ok. |  | Plug and Seat Minor Lapping done.Body Gasket Replaced. |  |  |  | Internal | Rajesh Diwedi | NA
OFF Season(Preventive) |  | 14/05/2025 | Plug and seat one side dent at same Position. |  | Plug and Seat Lapping done.Body and seat Gasket Replaced. |  |  |  | Internal | Amleshwar | NA

## BV-04
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | ON/OFF Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | BV-04 (Spray water on/off valve FOR 110/3 ATA Dearator steam PRDS)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140579
Model No. |  |  | 37-411X1 |  |  | Body Size/ Actuator Size |  |  | 1.5"/18"-6A3
Rating/End |  |  | ASME#1500(BW) |  |  | Cv/CHA |  |  | 16, ON/OFF
Stroke/ Seat Leak class |  |  | 19.05MM/ CLASS V |  |  | Body/ Trim |  |  | WCC/17.4PH+SS316S
Range/ Supply/ Signal |  |  | 3-15PSI/35PSI/4-20mA |  |  | Air Fail/ Packing |  |  | OPEN / PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Solenoid Valve & Coil | Dismantling & Cleaning of Solenoid Valve |  | X | X | X | √ | X | X
|  | Cleaning & Checking of SOV Coil |  | X | X | X | √ | X | X
|  | Servicing of Solenoid Valve |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2022 | all parts Found ok. |  | Seat and Plug minor lapping done.No spare used |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 2024-02-08 | all parts Found ok.plug and seat found dented condition. |  | Seat & Plug major lapping done. Replaced The Body Gasket and seat gasket. |  |  |  | Internal | Amleshwar/ Amit | Plug and Seat Scratched
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## BV-05
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | ON/OFF Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | BV-05 (Spray water on/off valve FOR 110/8 Auxiliary steam PRDS)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140767
Model No. |  |  | 37-411X1 |  |  | Body Size/ Actuator Size |  |  | 1"/15"-6A3
Rating/End |  |  | ASME#1500(BW) |  |  | Cv/CHA |  |  | 10, ON/OFF
Stroke/ Seat Leak class |  |  | 19.05MM/ CLASS V |  |  | Body/ Trim |  |  | WCC/17.4PH+SS316S
Range/ Supply/ Signal |  |  | 3-15PSI/40PSI/4-20mA |  |  | Air Fail/ Packing |  |  | OPEN / PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Solenoid Valve & Coil | Dismantling & Cleaning of Solenoid Valve |  | X | X | X | √ | X | X
|  | Cleaning & Checking of SOV Coil |  | X | X | X | √ | X | X
|  | Servicing of Solenoid Valve |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season (preventive) |  | 2022 | All Parts of Actuator and valve Found ok. |  | plug and seat Minor lapping done.no spare used. |  |  |  | Internal |  | NA
Off Season (preventive) |  | 30/06/2023 | All Parts Found Ok. |  | plug and seat Minor lapping done.Body and seat gasket Replaced |  |  |  | Internal |  | NA
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## PFW-09
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | ON/OFF Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | PFW-09 (Dearator Overflow On/Off Valve)
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 140768
Model No. |  |  | 37-211X5 |  |  | Body Size/ Actuator Size |  |  | 8"/18"-8A
Rating/End |  |  | ASME#150(RF) |  |  | Cv/CHA |  |  | 640, ON/OFF
Stroke/ Seat Leak class |  |  | 50.08MM/ CLASS V |  |  | Body/ Trim |  |  | WCC/SS316ST+SS316SST
Range/ Supply/ Signal |  |  | 9-15PSI/45PSI/4-20mA |  |  | Air Fail/ Packing |  |  | OPEN / PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Solenoid Valve & Coil | Dismantling & Cleaning of Solenoid Valve |  | X | X | X | √ | X | X
|  | Cleaning & Checking of SOV Coil |  | X | X | X | √ | X | X
|  | Servicing of Solenoid Valve |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 27/05/2023 | All Parts found ok. |  | Plug and Seat Minor Lapping done.No spare Used |  |  |  | Internal | Rajesh Diwedi/ Amit
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1. Actuator & Valve Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2. Handwheel Operation checked , found ok.
3.Gland Tightness checked , found ok.

## DAM-901
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | DAM-901 (ID FAN-A Suction Damper RPC))
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | ROTEX |  |  | Sr. No. |  |  | 13205822
Model No. |  |  | SPC-D-BG-ZRM-S-MP2+LB2-100/215 |  |  | Body Size/ Actuator Size
Rating/End | [5 empty] | Cv/CHA
Stroke/ Seat Leak class | [5 empty] | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Limit Switch Assembly | Dismantling the Switch assembly |  | X | X | X | X | √ | X
|  | Cleaning & Contact Checking of all switch |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2021 | Power cylinder wiper seal Not suitable for Reused. |  | Power cylinder wiper seal replaced by new |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 2022 | All parts Found ok. |  | Power cylinder wiper seal and piston checked. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 16/05/2025 | All parts Found ok. |  | Power cylinder wiper seal and piston checked.No spare used. |  |  |  | Internal | Amleshwar | NA

## DAM-902
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | DAM-902 (ID FAN-B Suction Damper RPC))
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | ROTEX |  |  | Sr. No. |  |  | 13205822
Model No. |  |  | SPC-D-BG-ZRM-S-MP2+LB2-100/215 |  |  | Body Size/ Actuator Size
Rating/End | [5 empty] | Cv/CHA
Stroke/ Seat Leak class | [5 empty] | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Limit Switch Assembly | Dismantling the Switch assembly |  | X | X | X | X | √ | X
|  | Cleaning & Contact Checking of all switch |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(preventive) |  | 2021 | Power cylinder wiper seal Not suitable for Reused. |  | Power cylinder wiper seal replaced by new |  |  |  | Internal |  | NA
OFF Season(preventive) |  | 2023-07-08 | All parts Found ok. |  | Power cylinder wiper seal and piston checked. |  |  |  | Internal |  | NA
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1.Drum & Piston Rod Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2.Handwheel Operation checked , found ok.
3.Stud Bolt Tightness checked , found ok.

## DAM-903
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | DAM-903 (SA FAN-A Suction Damper RPC))
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | ROTEX |  |  | Sr. No. |  |  | 13205822
Model No. |  |  | SCN1-D-BG-ZRM-S-MP2+LB2-125/215 |  |  | Body Size/ Actuator Size
Rating/End | [5 empty] | Cv/CHA
Stroke/ Seat Leak class | [5 empty] | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Limit Switch Assembly | Dismantling the Switch assembly |  | X | X | X | X | √ | X
|  | Cleaning & Contact Checking of all switch |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 2022-06-08 | All parts Found ok. |  | Power cylinder wiper seal and piston checked. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 19/05/2025 | All parts Found ok.
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1.Drum & Piston Rod Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2.Handwheel Operation checked , found ok.
3.Stud Bolt Tightness checked , found ok.

## DAM-904
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | DAM-904 (SA FAN-B Suction Damper RPC))
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | ROTEX |  |  | Sr. No. |  |  | 13205822
Model No. |  |  | SCN1-D-BG-ZRM-S-MP2+LB2-125/215 |  |  | Body Size/ Actuator Size
Rating/End | [5 empty] | Cv/CHA
Stroke/ Seat Leak class | [5 empty] | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Limit Switch Assembly | Dismantling the Switch assembly |  | X | X | X | X | √ | X
|  | Cleaning & Contact Checking of all switch |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season(Preventive) |  | 25/08/2022 | All parts Found ok. |  | Power cylinder wiper seal and piston checked. |  |  |  | Internal |  | NA
OFF Season(Preventive) |  | 20/08/2023 | All parts Found ok. |  | Power cylinder wiper seal and piston checked. |  |  |  | Internal |  | NA
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1.Drum & Piston Rod Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2.Handwheel Operation checked , found ok.
3.Stud Bolt Tightness checked , found ok.

## DAM-905
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | DAM-905 (FD FAN-A Suction Damper RPC))
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | ROTEX |  |  | Sr. No. |  |  | 13205822
Model No. |  |  | SCN1-D-BG-ZRM-S-MP2+LB2-160/215 |  |  | Body Size/ Actuator Size
Rating/End | [5 empty] | Cv/CHA
Stroke/ Seat Leak class | [5 empty] | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Limit Switch Assembly | Dismantling the Switch assembly |  | X | X | X | X | √ | X
|  | Cleaning & Contact Checking of all switch |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 2022-05-08 | All parts Found ok. |  | Power cylinder wiper seal and piston checked.No spare used. |  |  |  | Internal |  | NA

## DAM-906
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | DAM-906 (FD FAN-B Suction Damper RPC))
DATE OF COMMISSIONING : | [5 empty] | 2015-09-01
EQUIPMENT SPECIFICATION
Make |  |  | ROTEX |  |  | Sr. No. |  |  | 13205822
Model No. |  |  | SCN1-D-BG-ZRM-S-MP2+LB2-160/215 |  |  | Body Size/ Actuator Size
Rating/End | [5 empty] | Cv/CHA
Stroke/ Seat Leak class | [5 empty] | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Limit Switch Assembly | Dismantling the Switch assembly |  | X | X | X | X | √ | X
|  | Cleaning & Contact Checking of all switch |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season |  | 13/8/2023 | All parts Found ok. |  | Power cylinder wiper seal and piston checked.No spare used |  |  |  | Internal |  | NA

## DAM-907
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | DAM-907 (DA FAN-A Suction Damper RPC))
DATE OF COMMISSIONING : | [5 empty] | 2024-01-12
EQUIPMENT SPECIFICATION
Make |  |  | NELES |  |  | Sr. No. |  |  | 4005876282
Model No. |  |  | SCDA00BGNB050300 |  |  | Body Size/ Actuator Size
Rating/End | [5 empty] | Cv/CHA
Stroke/ Seat Leak class | [5 empty] | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Limit Switch Assembly | Dismantling the Switch assembly |  | X | X | X | X | √ | X
|  | Cleaning & Contact Checking of all switch |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1.Drum & Piston Rod Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2.Handwheel Operation checked , found ok.
3.Stud Bolt Tightness checked , found ok.

## DAM-908
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | DAM-908 (DA FAN-B Suction Damper RPC))
DATE OF COMMISSIONING : | [5 empty] | 2024-01-12
EQUIPMENT SPECIFICATION
Make |  |  | NELES |  |  | Sr. No. |  |  | 4005860948
Model No. |  |  | SCDA00BGNB050300 |  |  | Body Size/ Actuator Size
Rating/End | [5 empty] | Cv/CHA
Stroke/ Seat Leak class | [5 empty] | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Limit Switch Assembly | Dismantling the Switch assembly |  | X | X | X | X | √ | X
|  | Cleaning & Contact Checking of all switch |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2025 | All Parts Are Founf ok. |  | 1.Drum & Piston Rod Cleaning done. |  |  |  | Internal | Amleshwar & Amit Kumar | NA
2.Handwheel Operation checked , found ok.
3.Stud Bolt Tightness checked , found ok.

## APH-PC-M
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | APH-PC-M
DATE OF COMMISSIONING : | [5 empty] | 1sep.2015
EQUIPMENT SPECIFICATION
Make |  |  | DUNCAN |  |  | Sr. No. |  |  | PPWOV05502/021
Model No. |  |  | C0601000000B00030500 |  |  | Body Size/ Bore Size |  |  | 6''
Rating/End | [5 empty] | Cv/CHA
Stroke |  |  | 305mm |  |  | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Coil | Dismantling the Coil. |  | X | X | X | X | √ | X
|  | Cleaning & Magnet Checking of all Coil. |  | X | X | X | X | √ | X
3 | SOV | Dismantling & Cleaning of solenoid valve |  | X | X | X | √ | X | X
|  | Checking of solenoid valve & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output air Flow |  | X | X | X | √ | X | X
|  | Checking the air leakage of solenoid valve. |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season
OFF Season |  | 2025-09-07 | All Parts Found Ok |  | Seal kit Inspection done.Piston, Piston rod and Drum Internal Status checking. |  |  |  |  | Amleshwar

## APH-PC-S
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | APH-PC-M
DATE OF COMMISSIONING : | [5 empty] | 1sep.2015
EQUIPMENT SPECIFICATION
Make |  |  | DUNCAN |  |  | Sr. No. |  |  | PPWOV05502/021
Model No. |  |  | C0601000000B00030500 |  |  | Body Size/ Bore Size |  |  | 6''
Rating/End | [5 empty] | Cv/CHA
Stroke |  |  | 305mm |  |  | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Coil | Dismantling the Coil. |  | X | X | X | X | √ | X
|  | Cleaning & Magnet Checking of all Coil. |  | X | X | X | X | √ | X
3 | SOV | Dismantling & Cleaning of solenoid valve |  | X | X | X | √ | X | X
|  | Checking of solenoid valve & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output air Flow |  | X | X | X | √ | X | X
|  | Checking the air leakage of solenoid valve. |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season
OFF Season |  | 2025-12-07 | All Parts Found Ok |  | Seal kit Inspection done.Piston, Piston rod and Drum Internal Status checking. |  |  |  |  | Amleshwar | Piston Rod dent at 04 points.

## ESP1-PC
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | APH-PC-M
DATE OF COMMISSIONING : | [5 empty] | 1sep.2015
EQUIPMENT SPECIFICATION
Make |  |  | DUNCAN |  |  | Sr. No. |  |  | PPWOV05502/021
Model No. |  |  | C0601000000B00030500 |  |  | Body Size/ Bore Size |  |  | 6''
Rating/End | [5 empty] | Cv/CHA
Stroke |  |  | 305mm |  |  | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Coil | Dismantling the Coil. |  | X | X | X | X | √ | X
|  | Cleaning & Magnet Checking of all Coil. |  | X | X | X | X | √ | X
3 | SOV | Dismantling & Cleaning of solenoid valve |  | X | X | X | √ | X | X
|  | Checking of solenoid valve & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output air Flow |  | X | X | X | √ | X | X
|  | Checking the air leakage of solenoid valve. |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season
OFF Season |  | 2025-12-07 | All Parts Found Ok |  | Seal kit Inspection done.Piston, Piston rod and Drum Internal Status checking. |  |  |  |  | Amleshwar

## ESP2-PC
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | APH-PC-M
DATE OF COMMISSIONING : | [5 empty] | 1sep.2015
EQUIPMENT SPECIFICATION
Make |  |  | DUNCAN |  |  | Sr. No. |  |  | PPWOV05502/021
Model No. |  |  | C0601000000B00030500 |  |  | Body Size/ Bore Size |  |  | 6''
Rating/End | [5 empty] | Cv/CHA
Stroke |  |  | 305mm |  |  | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Coil | Dismantling the Coil. |  | X | X | X | X | √ | X
|  | Cleaning & Magnet Checking of all Coil. |  | X | X | X | X | √ | X
3 | SOV | Dismantling & Cleaning of solenoid valve |  | X | X | X | √ | X | X
|  | Checking of solenoid valve & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output air Flow |  | X | X | X | √ | X | X
|  | Checking the air leakage of solenoid valve. |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season
OFF Season |  | 2025-09-07 | All Parts Found Ok |  | Seal kit Inspection done.Piston, Piston rod and Drum Internal Status checking. |  |  |  |  | Amleshwar

## ESP3-PC
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | APH-PC-M
DATE OF COMMISSIONING : | [5 empty] | 1sep.2015
EQUIPMENT SPECIFICATION
Make |  |  | DUNCAN |  |  | Sr. No. |  |  | PPWOV05502/021
Model No. |  |  | C0601000000B00030500 |  |  | Body Size/ Bore Size |  |  | 6''
Rating/End | [5 empty] | Cv/CHA
Stroke |  |  | 305mm |  |  | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Coil | Dismantling the Coil. |  | X | X | X | X | √ | X
|  | Cleaning & Magnet Checking of all Coil. |  | X | X | X | X | √ | X
3 | SOV | Dismantling & Cleaning of solenoid valve |  | X | X | X | √ | X | X
|  | Checking of solenoid valve & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output air Flow |  | X | X | X | √ | X | X
|  | Checking the air leakage of solenoid valve. |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season
OFF Season |  | 2025-09-07 | All Parts Found Ok |  | General Maintenance and air leakage checking |  |  |  |  | Amleshwar

## ESP4-PC
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Regulated Power Cylinder
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | APH-PC-M
DATE OF COMMISSIONING : | [5 empty] | 1sep.2015
EQUIPMENT SPECIFICATION
Make |  |  | DUNCAN |  |  | Sr. No. |  |  | PPWOV05502/021
Model No. |  |  | C0601000000B00030500 |  |  | Body Size/ Bore Size |  |  | 6''
Rating/End | [5 empty] | Cv/CHA
Stroke |  |  | 305mm |  |  | Body/ Trim
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Power Cylinder | Dismantling & Cleaning all parts of Cylinder |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Coller Seal , Piston Seal & Piston checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Coil | Dismantling the Coil. |  | X | X | X | X | √ | X
|  | Cleaning & Magnet Checking of all Coil. |  | X | X | X | X | √ | X
3 | SOV | Dismantling & Cleaning of solenoid valve |  | X | X | X | √ | X | X
|  | Checking of solenoid valve & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output air Flow |  | X | X | X | √ | X | X
|  | Checking the air leakage of solenoid valve. |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
OFF Season
OFF Season |  | 2025-08-07 | All Parts Found Ok |  | Seal kit Inspection done.Piston, Piston rod and Drum Internal Status checking. |  |  |  |  | Amleshwar | Piston Rod dent at 04 points.

## TCV-509A NEW
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | TCV-509A
DATE OF COMMISSIONING : | [5 empty] | 2024-01-17
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 23004940
Model No. |  |  | 3778101 |  |  | Body Size/ Actuator Size |  |  | 2"/
Rating/End |  |  | ASME#1500(BW) |  |  | Cv/CHA |  |  | 4/MS_AC.MODLIN
Stroke/ Seat Leak class |  |  | 12.7MM/ CLASS V |  |  | Body/ Trim |  |  | WCC/SS440C+SS316+STNO.6
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing |  |  | STAY PUT / PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks

## TCV-511A NEW
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | Control Valve
LOCATION : | [5 empty] | Power Plant (150 TPH Boiler)
EQUIPMENT TAG NAME/APPLICATION: | [5 empty] | TCV-511A
DATE OF COMMISSIONING : | [5 empty] | 2024-01-17
EQUIPMENT SPECIFICATION
Make |  |  | MIL Controls Ltd |  |  | Sr. No. |  |  | 24003558
Model No. |  |  | 3778104 |  |  | Body Size/ Actuator Size |  |  | 1"/
Rating/End |  |  | ASME#1500(BW) |  |  | Cv/CHA |  |  | 0.2/MS_AC.MOD%
Stroke/ Seat Leak class |  |  | 12.7MM/ CLASS V |  |  | Body/ Trim |  |  | WCC/SS440C+SLD ST:6
Range/ Supply/ Signal | [5 empty] | Air Fail/ Packing |  |  | / PTFE
MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [6 empty] | Remarks
|  |  |  | Daily | Weekly | Monthly | Yearly | 2 - Years | 3 - Years | 4 - Years
1 | Pneumatic Actuator | Dismantling & Cleaning all parts of actuator |  | X | X | X | X | X | X | √
|  | Hand Wheel assembly checking |  | X | X | X | X | X | X | √
|  | Diaphragm & diaphragm plate checking |  | X | X | X | X | X | X | √
|  | Actuator Spring & Spindle Checking |  | X | X | X | X | X | X | √
|  | Checking of coupling, all nut & bolts |  | X | X | X | X | X | X | √
|  | Checking of Air leakage |  | √ | X | X | X | X | X
2 | Valve Body | Dismantling the valve assembly |  | X | X | X | X | √ | X
|  | Sheet, Plug, Cage & seal ring Checking |  | X | X | X | X | √ | X
|  | Body gasket, seat Gasket & Gland packing checking |  | X | X | X | X | √ | X
|  | Lapping of Seat/ Plug, if required (Blue Matching) |  | X | X | X | X | √ | X
3 | Valve Smart Positinor | Dismantling & Cleaning of Positinor |  | X | X | X | √ | X | X
|  | Cleaning & Checking of relay assembly & air path |  | X | X | X | √ | X | X
|  | Checking of Input & Output Pressure Gauge |  | X | X | X | √ | X | X
|  | Calibration the control valve & Positioner |  | X | X | X | √ | X | X
4 | Air Filter Regulator | AFR internals Dismantling & Cleaning |  | X | X | X | √ | X | X
|  | Spring, pilot & diaphragm checking |  | X | X | X | √ | X | X
|  | Cleaning & Checking of filter element |  | X | X | X | √ | X | X
|  | Checking of Air leakage & Moisture drain |  | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks