## Hierarchy
Sr.No. | Plant | Section | Location | Main Equipment | Sub Equipment | Department | History card Tag Nos. | History card Location
1 | SUGAR | DS HOUSE | DS House | DS NEW PCC | DS NEW PCC (0F0) MAIN INCOMER BREAKER | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/NEW PCC | SUGAR PLANT DS HOUSE MCC ROOM 1ST
2 | SUGAR | DS HOUSE | DS House | DS NEW PCC | DS NEW PCC (1F1) MAIN INCOMER BREAKER(3.15 MVA T/F) | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA | SUGAR PLANT DS HOUSE MCC ROOM 1ST
3 | SUGAR | DS HOUSE | DS House | DS OLD PCC | DS OLD PCC (1F1) MAIN INCOMER BREAKER | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/OLD PCC | SUGAR PLANT DS HOUSE MCC ROOM 1ST
4 | SUGAR | DS HOUSE | DS House | DS TRANSFORMER | DISTRIBUTION TRANSFORMER 3.15 MVA & PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | SUGAR PLANT DS HOUSE

## Sheet Map
source file | sheet name | id | EQUIPMENT TAG NO
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | DS NEW PCC MAIN IC BKR | 7c2ea79e606b | ZIL/GSM/SP/ELECT/DS/NEW PCC
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | DS 3.15 MVA TF BKR | f6e24b66b3c9 | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | DS OLD PCC MAIN IC BKR | ab1d2549b8ac | ZIL/GSM/SP/ELECT/DS/OLD PCC
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | Transformer 3.15 MVA | 670f86f37033 | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F

## EQUIPMENT LIFE HISTORY CARD
source file | sheet id | sheet name | EQUIPMENT TAG NO | NAME OF EQUIPMENT | LOCATION | DATE OF COMMISSIONING | Main Equipment | Sub Equipment | Department
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC | DS NEW PCC (0F0) MAIN INCOMER BREAKER | SUGAR PLANT DS HOUSE MCC ROOM 1ST |  | DS NEW PCC | DS NEW PCC (0F0) MAIN INCOMER BREAKER | ELECTRICAL
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA | DS NEW PCC (1F1) MAIN INCOMER BREAKER(3.15 MVA T/F) | SUGAR PLANT DS HOUSE MCC ROOM 1ST |  | DS NEW PCC | DS NEW PCC (1F1) MAIN INCOMER BREAKER(3.15 MVA T/F) | ELECTRICAL
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC | DS OLD PCC (1F1) MAIN INCOMER BREAKER | SUGAR PLANT DS HOUSE MCC ROOM 1ST |  | DS OLD PCC | DS OLD PCC (1F1) MAIN INCOMER BREAKER | ELECTRICAL
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | DISTRIBUTION TRANSFORMER 3.15 MVA & PANEL | SUGAR PLANT DS HOUSE |  | DS TRANSFORMER | DISTRIBUTION TRANSFORMER 3.15 MVA & PANEL | ELECTRICAL

## EQUIPMENT SPECIFICATION
source file | sheet id | sheet name | EQUIPMENT TAG NO | section | sub_section | Parameter label | Parameter value
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC |  |  | Make | ABB
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC |  |  | Machine Sr. No.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC |  |  | Rated Current | 4000A
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC |  |  | Year of Manufacture
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC |  |  | Rated Voltage | 415 ±10%V
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC |  |  | Existing Protection Setting - L | 0.9 x In
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC |  |  | Model | SACE Emax
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC |  |  | Existing Protection Setting - S | 3.5 x In
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC |  |  | Sace | PR121/P
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC |  |  | Existing Protection Setting - I | 4 x In
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC |  |  | Starter | PCC PANEL
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC |  |  | Existing ProtectionSetting - G | 0.4 x In
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA |  |  | Make | ABB
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA |  |  | Machine Sr. No.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA |  |  | Rated Current | 5000A
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA |  |  | Year of Manufacture
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA |  |  | Rated Voltage | 415 ±10%V
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA |  |  | Existing Protection Setting - L | 0.8 x In
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA |  |  | Model | SACE Emax
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA |  |  | Existing Protection Setting - S | 4 x In
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA |  |  | Sace | PR121/P
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA |  |  | Existing Protection Setting - I | 8 x In
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA |  |  | Starter | PCC PANEL
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA |  |  | Existing ProtectionSetting - G | 0.6 x In
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC |  |  | Make | ABB
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC |  |  | Machine Sr. No.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC |  |  | Rated Current | 5000 A
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC |  |  | Year of Manufacture
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC |  |  | Rated Voltage | 415 ±10%V
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC |  |  | Existing Protection Setting - L | 0.6 x In
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC |  |  | Model | SACE Emax
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC |  |  | Existing Protection Setting - S | 4 x In
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC |  |  | Sace | PR121/P
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC |  |  | Existing Protection Setting - I | 6 x In
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC |  |  | Starter | PCC PANEL
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC |  |  | Existing ProtectionSetting - G | 0.4 x In
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Rated Power | 3150 KVA
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Rated Current H.V | 165.33A
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Volume of oil | 2620 Ltrs.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Sr No. | 1712/3
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | LV1 WTI CT as per IS: 2705 | Ratio 420/1.6A, 15VA, CL-1
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Rated Voltage H.V | 11000V
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Rated Current L.V | 4200.1A
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Year of Manufacture | 2015
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Connection | Dyn11
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | LV NCT as per IS: 2705
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Ratio 5000/1A,CL- PS,Vk>850, RCT<20 ohms, @75°C, Imag<30mA@50%VK.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Rated Voltage L.V | 433V
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Cooling Type | ONAN
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Mass of oil | 2290 Kg.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F |  |  | Make | Delta

## MAINTENANCE SCHEDULE
source file | sheet id | sheet name | EQUIPMENT TAG NO | Sr.No. | Name of Equipment | Maintenance / Inspection Activities | Daily | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years | 4 - Years | Remarks
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC | 1 | (0F0) Main Incomer Breaker for DS new PCC, EDO, ACB | Clean & Check of fixed & moving contact | [5 empty] | Yes
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC | 1 | (0F0) Main Incomer Breaker for DS new PCC, EDO, ACB | Charging spring.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC | 1 | (0F0) Main Incomer Breaker for DS new PCC, EDO, ACB | Open, close & triping.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC | 1 | (0F0) Main Incomer Breaker for DS new PCC, EDO, ACB | On, Off and trip indication.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA | 1 | (1F1) T/F 3.15 MVA BKR for DS new PCC, EDO, ACB | Clean & Check of fixed & moving contact | [5 empty] | Yes
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA | 1 | (1F1) T/F 3.15 MVA BKR for DS new PCC, EDO, ACB | Charging spring.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA | 1 | (1F1) T/F 3.15 MVA BKR for DS new PCC, EDO, ACB | Open, close & triping.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA | 1 | (1F1) T/F 3.15 MVA BKR for DS new PCC, EDO, ACB | On, Off and trip indication.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC | 1 | (1F1) Main INCOMER BREAKER for DS OLD PCC, EDO, ACB | Clean & Check of fixed & moving contact | [5 empty] | Yes
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC | 1 | (1F1) Main INCOMER BREAKER for DS OLD PCC, EDO, ACB | Charging spring.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC | 1 | (1F1) Main INCOMER BREAKER for DS OLD PCC, EDO, ACB | Open, close & triping.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC | 1 | (1F1) Main INCOMER BREAKER for DS OLD PCC, EDO, ACB | On, Off and trip indication.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | 1 | Panel | Clean & Check of busbar, Supports & Bandages | [5 empty] | Yes | Yes
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | 1 | Panel | Checking of Busbar terminal & Joints.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | 1 | Panel | Cleaning of Panel
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | 2 | Breaker | Checking of Fix & moving contact. | [5 empty] | Yes
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | 2 | Breaker | Check whether all fastening elements are tight.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | 2 | Breaker | Visual Inspection of Rotor.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | 3 | Oil status | Check Quality of oil. | [5 empty] | Yes
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | 3 | Oil status | Extended visual inspection of end shields.
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | 6 | Cooling System | External Fan | [5 empty] | Yes
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | 7 | Heating system | Check function of heating system | [5 empty] | Yes
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | 8 | Monitoring Instruments | Winding Temprature |  | Yes

## EQUIPMENT MAINTENANCE HISTORY
source file | sheet id | sheet name | EQUIPMENT TAG NO | Season / OFF Season | Year | Date of Start | Date of Finish | Outage/ Observation | Action Taken | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC | Off Season | 2023 |  |  | Repair Maintenance | Complete overhauling done | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC | Off Season | 2024 |  |  | Repair Maintenance | Complete overhauling done | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC | Off Season | 2025 |  |  | Repair Maintenance | Complete overhauling done | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 7c2ea79e606b | DS NEW PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC | Season | 2025-26 |  |  | Breaker cradle over heated(02 nos B-phase & 01 nos Y-phase) | Breaker cradle replaced and started. | NO | Internal | Vijay Chaudhary/ Abhaylal/Vikash
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA | Off Season | 2023 |  |  | Repair Maintenance | Complete overhauling done | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA | Off Season | 2024 |  |  | Repair Maintenance | Complete overhauling done | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA | Off Season | 2025 |  |  | Repair Maintenance | Complete overhauling done | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | f6e24b66b3c9 | DS 3.15 MVA TF BKR | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA | Off Season | 2026 |  |  | Repair Maintenance | Complete overhauling done | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC | Off Season | 2023 |  |  | Repair Maintenance | Complete overhauling done | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC | Off Season | 2024 |  |  | Repair Maintenance | Complete overhauling done | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC | Off Season | 2025 |  |  | Repair Maintenance | Complete overhauling done | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | ab1d2549b8ac | DS OLD PCC MAIN IC BKR | ZIL/GSM/SP/ELECT/DS/OLD PCC | Off Season | 2026 |  |  | Repair Maintenance | Complete overhauling done | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | Off-Season 2023 | 2023 |  |  | Repair Maintenance | Complete overhauling done
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | Off-Season 2024 | 2024 |  |  | Repair Maintenance | Complete overhauling done
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | Off-Season 2025 | 2025 |  |  | Repair Maintenance | Complete overhauling done
1_DS Equipment Life History - PCC PANEL & Transformer.xlsx | 670f86f37033 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | Season 2025-26 | 2026 |  |  | Transformer LT Side flashed in R & Y Phase. | Transformer send to ELECON CONDUCTORS LTD. MEERUT. For Repairing.