## Summary Index
Sr.No. | Plant | Section | Location | Main Equipment | Sub Equipment | Department | History card Tag nas. | History card Location
1 | SUGAR | POWER HOUSE | STEAM TG SET | OLD POWER STEAM TURBINE ALTENATOR (OLD-STG) | OLD 3 MW ALTERNATOR | ELECTRICAL | ZIL/GSM/SP/ELECT/PH/01 | SUGAR PLANT PH
2 | SUGAR | POWER HOUSE | STEAM TG SET | NEW POWER STEAM TURBINE (NEW-STG) | NEW 3 MW ALTERNATOR | ELECTRICAL | ZIL/GSM/SP/ELECT/PH/02 | SUGAR PLANT PH
3 | SUGAR | POWER HOUSE | POWER HOUSE ELECT PANEL | POWER HOUSE LT PCC | L.T PCC PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/PH/03 | SUGAR PLANT PH
4 | SUGAR | POWER HOUSE | POWER HOUSE TRANSFORMER | POWER HOUSE TRANSFORMER 2.5 MVA | TRANSFORMER 2.5 MVA | ELECTRICAL | ZIL/GSM/SP/ELECT/PH/04 | SUGAR PLANT PH
5 | SUGAR | POWER HOUSE | POWER HOUSE ELECT PANEL | POWER HOUSE LT PCC | CAPACITOR PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/PH/05 | SUGAR PLANT PH
6 | SUGAR | POWER HOUSE | POWER HOUSE AIR CONDITIONER | AIR CONDITIONER | CONTROL ROOM AIR CONDITIONER | ELECTRICAL | ZIL/GSM/SP/ELCT/PH/06 | SUGAR PLANT PH

## Summary Link
S/N | Sheet
1 | 3 MW Old alternator No.1'!A1
2 | 3 MW Old alternator No. 2'!A1
3 | Power house PCC '!A1
4 | Power house Transformer'!A1
5 | Capacitor Panel'!A1
6 | Air Conditioner'!A1

## 3 MW Old alternator No.1
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : |  |  | OLD 3 MW ALTERNATOR
LOCATION : |  |  | SUGAR PLANT PH
EQUIPMENT NO: |  |  | ZIL/GSM/SP/ELECT/PH/01
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make | BHEL | Machine Sr. No. | 44221A261-11-03 | Protection | IP 54 | Winding Insulation Class | F - Class | P.F | 0.8 Lag
Rated Power | 3750 KVA / 3000 KW | Year of Manufacture | 1996 | Frame | G 54904 | Duty | Continuous | Weight | 16000 Kg.
Rated Voltage | 420V | Rated Current | 5155 | Connection | Star | Specification | IS 4722 | Excitation Voltage | 95V
Rated RPM | 1500 | Bearings |  | Ambient Temp. | 45°C | Inlet Temp. | 50°C | Excitation Current | 385A
BRUSHLESS EXCITER
Make | BHEL | Voltage | 108 V | Rated RPM | 1500 | Specification | IS4722 | Field Resistance | 25.6, Ohm
Rated Power | 45.9 KW | Current | 425A | Connection | Star | Manufacturing Year | 1996
Excitation Voltage | 160V | Hz | 150 | Excitation Current | 4.5A | Sr. No. | 44221A261-11-03
AVR PANEL
Generator | Rating | 3000 KW | Excitation | Voltage | 110V | Make | Sanelec
| Voltage | 415 V |  | Current | 3.7A | SN. | ECP No. 150705
| Frequency | 50 Hz
| Phase | 3
OEM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities | Interval | [5 empty] | Remarks
|  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | Stator | Clean & Check of winding , Supports & Bandages | X | X | X | X | √ | √
Checking of Busbar terminal & Joints.
Cleaning of Stator winding and Connection
Measure IR of Stator winding.
2 | Rotor | Measure IR of Field winding. | X | X | X | X | √ | X
Check whether all fastening elements are tight.
Visual Inspection of Rotor.
3 | Exciter | Check Quality of bearing oil. | X | X | X | X | √ | X
Extended visual inspection of end shields.
6 | Cooling System | Internal Fan | X | X | X | X | √ | X
7 | Heating system | Check function of heating system | X | X | X | X | √ | X
8 | Monitoring Instruments | Winding Temprature | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off-Season 2026 |  | 2026 | Repair Maintenance | Complete overhauling done

## 3 MW Old alternator No. 2
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : |  |  | OLD 3 MW ALTERNATOR
LOCATION : |  |  | SUGAR PLANT PH
EQUIPMENT NO: |  |  | ZIL/GSM/SP/ELECT/PH/02
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make | BHEL | Machine Sr. No. | 44221A261-11-03 | Protection | IP 54 | Winding Insulation Class | F - Class | P.F | 0.8 Lag
Rated Power | 3750 KVA / 3000 KW | Year of Manufacture | 1996 | Frame | G 54904 | Duty | Continuous | Weight | 16000 Kg.
Rated Voltage | 420V | Rated Current | 5155 | Connection | Star | Specification | IS 4722 | Excitation Voltage | 95V
Rated RPM | 1500 | Bearings |  | Ambient Temp. | 45°C | Inlet Temp. | 50°C | Excitation Current | 385A
BRUSHLESS EXCITER
Make | BHEL | Voltage | 108 V | Rated RPM | 1500 | Specification | IS4722 | Field Resistance | 25.6, Ohm
Rated Power | 45.9 KW | Current | 425A | Connection | Star | Manufacturing Year | 1996
Excitation Voltage | 160V | Hz | 150 | Excitation Current | 4.5A | Sr. No. | 44221A261-11-03
AVR PANEL
Generator | Rating | 3000 KW | Excitation | Voltage | 40V | Make | Sanelec
| Voltage | 415 V |  | Current | 5.2A | SN. | ECP No. 230804
| Frequency | 50 Hz
| Phase | 3
OEM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities | Interval | [5 empty] | Remarks
|  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | Stator | Clean & Check of winding , Supports & Bandages | X | X | X | X | √ | √
Checking of Busbar terminal & Joints.
Cleaning of Stator winding and Connection
Measure IR of Stator winding.
2 | Rotor | Measure IR of Field winding. | X | X | X | X | √ | X
Check whether all fastening elements are tight.
Visual Inspection of Rotor.
3 | Exciter | Check Quality of bearing oil. | X | X | X | X | √ | X
Extended visual inspection of end shields.
6 | Cooling System | Internal Fan | X | X | X | X | √ | X
7 | Heating system | Check function of heating system | X | X | X | X | √ | X
8 | Monitoring Instruments | Winding Temprature | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off-Season 2026 |  | 2026 | Repair Maintenance | Complete Motor overhauling done |  |  | External Party M/S Durga Construction

## Power house PCC
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : |  |  | L.T PCC PANEL
LOCATION : |  |  | SUGAR PLANT PH
EQUIPMENT NO: |  |  | ZIL/GSM/SP/ELECT/PH/03
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION (ACB)
Feeder-1, D.S House | SACE E4.2S, 4000A | Feeder-5,Main I/C New T.G-1, 52A | SACE E4.2S, 4000A | Feeder-8 Bus coupler | SACE E6H 50, 5000A | Feeder-12, 70 TPH PCC-1 | FA2C-1600 | Feeder-17, Cane Yard & Capacitor Panel | CN-CS 1000C
Feeder-2, Capacitor panel-1 | SACE E3N 32, 3200A | Feeder-5,Main I/C New T.G-1, 52B | SACE E4.2S, 4000A | Feeder-9 Power plant L.T | CN-CS 2500C | Feeder-13, 70 TPH PCC-2 | FA2C-1600 | Feeder-18 Mill House L.T PCC | CN-CS 1000C
Feeder-3 Mill House L.T PCC | SACE E2N 20, 2000A | Feeder-6,Raw house PCC | SACE E3N 32, 3200A | Feeder-10 Raw House VFD Panel | CN-CS 2000C | Feeder-14 Power House Lighting | CN-CS 1000C | Feeder-19 Colony | CN-CS 1000C
Feeder-4 D.S House Injection | SACE E1N 10, 1000A | Feeder-7 D.S House Injection | SACE E1N 16, 1600A | Feeder-11 D.S House PCC-2 | CN-CS 4000C | Feeder-16 D.S House ETP | CN-CS 1000C
Feeder-20,Main I/C OLD, T.G, 52A | SACE E4.2H, 4000A | Feeder-20,Main I/C OLD, T.G, 52B | SACE E4.2H, 4000A | Feeder-21 Grid Tie | SACE E6H 50, 5000A | Feeder-21 Grid Tie NIS | SACE E1N 10, 1000A
OEM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities | Interval | [5 empty] | Remarks
|  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | Panel | Clean & Check of busbar, Supports & Bandages | X | X | X | X | √ | √
Checking of Busbar terminal & Joints.
Cleaning of Panel
2 | Breaker | Checking of Fix & moving contact. | X | X | X | X | √ | X
Check whether all fastening elements are tight.
Visual Inspection of Contactors.
3 | Terminal | Checking & Tightening. | X | X | X | X | √ | X
Extended visual inspection of end shields.
6 | Cooling System | Internal Fan | X | X | X | X | √ | X
7 | Heating system | Check function of heating system | X | X | X | X | √ | X
8 | Monitoring Instruments | Winding Temprature | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off-Season 2026 |  | 2026 | Repair Maintenance | Complete overhauling done

## Power house Transformer
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : |  |  | TRANSFORMER 2.5 MVA
LOCATION : |  |  | SUGAR PLANT PH
EQUIPMENT NO: |  |  | ZIL/GSM/SP/ELECT/PH/04
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Rated Power ONAN | 2500 KVA | Rated Current ONAN H.V | 131.22A | Volume of oil | 2900 Ltrs. | Sr No. | 1713/1 | HV WTI CT as per IS: 2705 | Ratio 166/1.6A, 15VA, CL-1
Rated Power ONAF | 3150 KVA | Rated Current ONAF H.V | 165.33A | Year of Manufacture | 2014 | Connection | Dyn11 | LV WTI CT as per IS: 2705 | Ratio 4383/1.6A, 15VA, CL-1
Rated Voltage H.V | 11000V | Rated Current ONAN L.V | 3478.01A | Mass of oil | 2540 Kg. | Make | Delta | LV NCT as per IS: 2705 | Ratio 5000/1A,CL- PS,Vk>700, RCT<20 ohms, @75°C, Imag<30mA@50%VK.
Rated Voltage L.V | 415V | Rated Current ONAF L.V | 4382.3A | Cooling Type | ONAN
OEM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities | Interval | [5 empty] | Remarks
|  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | Panel | Clean & Check of busbar, Supports & Bandages | X | X | X | X | √ | √
Checking of Busbar terminal & Joints.
Cleaning of Panel
2 | Breaker | Checking of Fix & moving contact. | X | X | X | X | √ | X
Check whether all fastening elements are tight.
Visual Inspection of Measuring instrument.
3 | Oil status | Check Quality of oil. | X | X | X | X | √ | X
Extended visual inspection of end shields.
6 | Cooling System | External Fan | X | X | X | X | √ | X
7 | Heating system | Check function of heating system | X | X | X | X | √ | X
8 | Monitoring Instruments | Winding Temprature | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off-Season 2026 |  | 2026 | Repair Maintenance | Complete overhauling done

## Capacitor Panel
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : |  |  | CAPACITOR PANEL
LOCATION : |  |  | SUGAR PLANT PH
EQUIPMENT NO: |  |  | ZIL/GSM/SP/ELECT/PH/05
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION (ACB)
Capcitor Panel -1 | 900 KVAR | Capcitor Panel -1 | 375 KVAR
OEM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities | Interval | [5 empty] | Remarks
|  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | Panel | Clean & Check of busbar, Supports & Bandages | X | X | X | X | √ | √
Checking of Busbar terminal & Joints.
Cleaning of Panel
2 | Breaker | Checking of Fix & moving contact. | X | X | X | X | √ | X
Check whether all fastening elements are tight.
Visual Inspection of contactors.
3 | Terminal | Checking & Tightening. | X | X | X | X | √ | X
Extended visual inspection of end shields.
6 | Cooling System | Internal Fan | X | X | X | X | √ | X
7 | Heating system | Check function of heating system | X | X | X | X | √ | X
8 | Monitoring Instruments | Winding Temprature | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off-Season 2026 |  | 2026 | Repair Maintenance | Complete overhauling done

## Air Conditioner
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : |  |  | CONTROL ROOM AIR CONDITIONER
LOCATION : |  |  | SUGAR PLANT PH
EQUIPMENT NO: |  |  | ZIL/GSM/SP/ELCT/PH/06
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION UNIT-1
Make |  | Rated Voltage | 230 V | Machine Sr. No. |  | Capacity | 2 Ton | Rated Current
Type of A.C |  | Type of Gas |  | Discharge Pressure |  | Suction Pressure |  | Year of Manufacture
EQUIPMENT SPECIFICATION UNIT-2
Make |  | Rated Voltage | 230 V | Machine Sr. No. |  | Capacity | 2 Ton | Rated Current
Type of A.C |  | Type of Gas |  | Discharge Pressure |  | Suction Pressure |  | Year of Manufacture
EQUIPMENT SPECIFICATION UNIT-2
Make |  | Rated Voltage | 230 V | Machine Sr. No. |  | Capacity | 2 Ton | Rated Current
Type of A.C |  | Type of Gas |  | Discharge Pressure |  | Suction Pressure |  | Year of Manufacture
OEM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities | Interval | [5 empty] | Remarks
|  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | Out Door Unit | Clean & Check of cleaning. | X | X | X | X | √ | X
Checking of terminal & Joints.
Cleaning of Coil fins and Connection
2 | Indoor Unit | Clean & Check of cleaning. | X | X | X | X | √ | X
Checking of terminal & Joints.
Cleaning of Coil fins and Connection
3 | Fan | Check of bearing. | X | X | X | X | √ | X
Extended visual inspection.
6 | Cooling System | External Fan Motor | X | X | X | X | √ | X
7 | Heating system | Check function of heating system | X | X | X | X | √ | X
8 | Monitoring Instruments | Winding Temprature | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off-Season 2026 |  | 2026 | Repair Maintenance | Complete Motor overhauling done |  |  | Internal Service | Akhilesh Chaudhari