## INDEX
Sugar Plant DS House Electrical Equipments-TRANSFORMER & PCC BREAKER
Sr.No. | Plant | Section | Location | Main Equipment | Sub Equipment | Department | History card Tag Nos. | History card Location
1 | SUGAR | DS HOUSE | DS House | DS NEW PCC | DS NEW PCC (0F0) MAIN INCOMER BREAKER | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/NEW PCC | SUGAR PLANT DS HOUSE MCC ROOM 1ST
2 | SUGAR | DS HOUSE | DS House | DS NEW PCC | DS NEW PCC (1F1) MAIN INCOMER BREAKER(3.15 MVA T/F) | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA | SUGAR PLANT DS HOUSE MCC ROOM 1ST
3 | SUGAR | DS HOUSE | DS House | DS OLD PCC | DS OLD PCC (1F1) MAIN INCOMER BREAKER | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/OLD PCC | SUGAR PLANT DS HOUSE MCC ROOM 1ST
4 | SUGAR | DS HOUSE | DS House | DS TRANSFORMER | DISTRIBUTION TRANSFORMER 3.15 MVA & PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F | SUGAR PLANT DS HOUSE

## DS NEW PCC MAIN IC BKR
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS NEW PCC (0F0) MAIN INCOMER BREAKER
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE MCC ROOM 1ST
EQUIPMENT NO: | [5 empty] | ZIL/GSM/SP/ELECT/DS/NEW PCC
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | Machine Sr. No.
Rated Current |  |  | 4000A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V |  |  | Existing Protection Setting - L |  | 0.9 x In
Model |  |  | SACE Emax |  |  | Existing Protection Setting - S |  | 3.5 x In
Sace |  |  | PR121/P |  |  | Existing Protection Setting - I |  | 4 x In
Starter |  |  | PCC PANEL |  |  | Existing ProtectionSetting - G |  | 0.4 x In
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | (0F0) Main Incomer Breaker for DS new PCC, EDO, ACB | Clean & Check of fixed & moving contact |  | X | X | X | X | √ | X
|  | Charging spring. |  |  | X
|  | Open, close & triping. |  |  | X
|  | On, Off and trip indication. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 | Repair Maintenance |  | Complete overhauling done |  | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
Off Season |  | 2024 | Repair Maintenance |  | Complete overhauling done |  | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
Off Season |  | 2025 | Repair Maintenance |  | Complete overhauling done |  | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
Season |  | 2025-26 | Breaker cradle over heated(02 nos B-phase & 01 nos Y-phase) |  | Breaker cradle replaced and started. |  | NO | Internal | Vijay Chaudhary/ Abhaylal/Vikash

## DS 3.15 MVA TF BKR
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS NEW PCC (1F1) MAIN INCOMER BREAKER(3.15 MVA T/F)
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE MCC ROOM 1ST
EQUIPMENT NO: | [5 empty] | ZIL/GSM/SP/ELECT/DS/NEW PCC/3.15 MVA
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | Machine Sr. No.
Rated Current |  |  | 5000A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V |  |  | Existing Protection Setting - L |  | 0.8 x In
Model |  |  | SACE Emax |  |  | Existing Protection Setting - S |  | 4 x In
Sace |  |  | PR121/P |  |  | Existing Protection Setting - I |  | 8 x In
Starter |  |  | PCC PANEL |  |  | Existing ProtectionSetting - G |  | 0.6 x In
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | (1F1) T/F 3.15 MVA BKR for DS new PCC, EDO, ACB | Clean & Check of fixed & moving contact |  | X | X | X | X | √ | X
|  | Charging spring. |  |  | X
|  | Open, close & triping. |  |  | X
|  | On, Off and trip indication. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 | Repair Maintenance |  | Complete overhauling done |  | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
Off Season |  | 2024 | Repair Maintenance |  | Complete overhauling done |  | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
Off Season |  | 2025 | Repair Maintenance |  | Complete overhauling done |  | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
Off Season |  | 2026 | Repair Maintenance |  | Complete overhauling done |  | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash

## DS OLD PCC MAIN IC BKR
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS OLD PCC (1F1) MAIN INCOMER BREAKER
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE MCC ROOM 1ST
EQUIPMENT NO: | [5 empty] | ZIL/GSM/SP/ELECT/DS/OLD PCC
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | Machine Sr. No.
Rated Current |  |  | 5000 A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V |  |  | Existing Protection Setting - L |  | 0.6 x In
Model |  |  | SACE Emax |  |  | Existing Protection Setting - S |  | 4 x In
Sace |  |  | PR121/P |  |  | Existing Protection Setting - I |  | 6 x In
Starter |  |  | PCC PANEL |  |  | Existing ProtectionSetting - G |  | 0.4 x In
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | (1F1) Main INCOMER BREAKER for DS OLD PCC, EDO, ACB | Clean & Check of fixed & moving contact |  | X | X | X | X | √ | X
|  | Charging spring. |  |  | X
|  | Open, close & triping. |  |  | X
|  | On, Off and trip indication. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 | Repair Maintenance |  | Complete overhauling done |  | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
Off Season |  | 2024 | Repair Maintenance |  | Complete overhauling done |  | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
Off Season |  | 2025 | Repair Maintenance |  | Complete overhauling done |  | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash
Off Season |  | 2026 | Repair Maintenance |  | Complete overhauling done |  | NO | NO | Vijay Chaudhary/ Abhaylal/Vikash

## Transformer 3.15 MVA
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : |  |  | DISTRIBUTION TRANSFORMER 3.15 MVA & PANEL
LOCATION : |  |  | SUGAR PLANT DS HOUSE
EQUIPMENT NO: |  |  | ZIL/GSM/SP/ELECT/DS/3.15 MVA T/F
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Rated Power | 3150 KVA | Rated Current H.V | 165.33A | Volume of oil | 2620 Ltrs. | Sr No. | 1712/3 | LV1 WTI CT as per IS: 2705 | Ratio 420/1.6A, 15VA, CL-1
Rated Voltage H.V | 11000V | Rated Current L.V | 4200.1A | Year of Manufacture | 2015 | Connection | Dyn11 | LV NCT as per IS: 2705 | Ratio 5000/1A,CL- PS,Vk>850, RCT<20 ohms, @75°C, Imag<30mA@50%VK.
Rated Voltage L.V | 433V | Cooling Type | ONAN | Mass of oil | 2290 Kg. | Make | Delta
OEM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities | Interval | [5 empty] | Remarks
|  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | Panel | Clean & Check of busbar, Supports & Bandages | X | X | X | X | √ | √
Checking of Busbar terminal & Joints.
Cleaning of Panel
2 | Breaker | Checking of Fix & moving contact. | X | X | X | X | √ | X
Check whether all fastening elements are tight.
Visual Inspection of Rotor.
3 | Oil status | Check Quality of oil. | X | X | X | X | √ | X
Extended visual inspection of end shields.
6 | Cooling System | External Fan | X | X | X | X | √ | X
7 | Heating system | Check function of heating system | X | X | X | X | √ | X
8 | Monitoring Instruments | Winding Temprature | √ | X | X | X | X | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off-Season 2023 |  | 2023 | Repair Maintenance | Complete overhauling done
Off-Season 2024 |  | 2024 | Repair Maintenance | Complete overhauling done
Off-Season 2025 |  | 2025 | Repair Maintenance | Complete overhauling done
Season 2025-26 |  | 2026 | Transformer LT Side flashed in R & Y Phase. | Transformer send to ELECON CONDUCTORS LTD. MEERUT. For Repairing.