## Sheet Map
source file | sheet name | id | EQUIPMENT TAG NO
electrical Mill house life history Data-30072026.xlsx | SHREDDER MOTOR No. 1 | 88f7926d1273 | ZIL/GSM/SP/ELECT/MH/01
electrical Mill house life history Data-30072026.xlsx | SHREDDER MOTOR No. 2 | ddef4dd1cd11 | ZIL/GSM/SP/ELECT/MH/02
electrical Mill house life history Data-30072026.xlsx | Zero Mill Drive Motor No.3 | 88e72bf6e174 | ZIL/GSM/SP/ELECT/MH/03
electrical Mill house life history Data-30072026.xlsx | 4rth Mill Drive Motor No.4 | 1d004acba7b9 | ZIL/GSM/SP/ELECT/MH/04
electrical Mill house life history Data-30072026.xlsx | CU-No.1 | 3b203dd8600f | ZIL/GSM/SP/ELECT/MH/05
electrical Mill house life history Data-30072026.xlsx | CU-No. 2 | b582619592fb | ZIL/GSM/SP/ELECT/MH/06
electrical Mill house life history Data-30072026.xlsx | CU-No. 3 | 5b60e82f9a72 | ZIL/GSM/SP/ELECT/MH/07
electrical Mill house life history Data-30072026.xlsx | CU-No.4 | c92e585550a9 | ZIL/GSM/SP/ELECT/MH/08
electrical Mill house life history Data-30072026.xlsx | CU-No.5 | 5b46d0d4e790 | ZIL/GSM/SP/ELECT/MH/09
electrical Mill house life history Data-30072026.xlsx | CU-No.6 | f450390a23e9 | ZIL/GSM/SP/ELECT/MH/10
electrical Mill house life history Data-30072026.xlsx | Transformer 3.15 MVA | 57f6157ec7b8 | ZIL/GSM/SP/ELECT/MH/11
electrical Mill house life history Data-30072026.xlsx | Transformer 2.5 MVA | 05701eb041bb | ZIL/GSM/SP/ELECT/MH/12
electrical Mill house life history Data-30072026.xlsx | Mill house H.T PCC | 6d80d2dcc874 | ZIL/GSM/SP/ELECT/MH/13
electrical Mill house life history Data-30072026.xlsx | Mill house L.T PCC & MCC PANEL | 4f98e76a1452 | ZIL/GSM/SP/ELECT/MH/14
electrical Mill house life history Data-30072026.xlsx | Mill house VFD PANEL | dbc83d23d4df | ZIL/GSM/SP/ELECT/MH/15
electrical Mill house life history Data-30072026.xlsx | Fourth Mill Blower Motor | 6b536c59ab7e | ZIL/GSM/SP/ELECT/MH/16
electrical Mill house life history Data-30072026.xlsx | Aux. Cane Carier | 78cac24605c7 | ZIL/GSM/SP/ELECT/MH/17
electrical Mill house life history Data-30072026.xlsx | Main Cane Carier | a12171d74d5d | ZIL/GSM/SP/ELECT/MH/18
electrical Mill house life history Data-30072026.xlsx | Cardian Drum-1 | 31262d78a3d7 | ZIL/GSM/SP/ELECT/MH/19
electrical Mill house life history Data-30072026.xlsx | Cardian Drum-2 | c20f5995596a | ZIL/GSM/SP/ELECT/MH/20
electrical Mill house life history Data-30072026.xlsx | Cane Kicker | 42ee48a19e25 | ZIL/GSM/SP/ELECT/MH/21
electrical Mill house life history Data-30072026.xlsx | Feeder Drum | d94be2fb6a44 | ZIL/GSM/SP/ELECT/MH/22
electrical Mill house life history Data-30072026.xlsx | Shredder Carier | 73320a1d47e6 | ZIL/GSM/SP/ELECT/MH/23
electrical Mill house life history Data-30072026.xlsx | Shredder Belt | bf0c8551629e | ZIL/GSM/SP/ELECT/MH/24
electrical Mill house life history Data-30072026.xlsx | Cane Equalizer | 570c5a68d64e | ZIL/GSM/SP/ELECT/MH/25
electrical Mill house life history Data-30072026.xlsx | IRC-No.1 | 87e5104868ca | ZIL/GSM/SP/ELECT/MH/26
electrical Mill house life history Data-30072026.xlsx | IRC-No.2 | a108a3d17e24 | ZIL/GSM/SP/ELECT/MH/27
electrical Mill house life history Data-30072026.xlsx | IRC-No.3 | 1b63820ad211 | ZIL/GSM/SP/ELECT/MH/28
electrical Mill house life history Data-30072026.xlsx | IRC-No.4 | c40eb57afda6 | ZIL/GSM/SP/ELECT/MH/29
electrical Mill house life history Data-30072026.xlsx | Secondary Rotary Screen No-2 | 835390f402a0 | ZIL/GSM/SP/ELECT/MH/30
electrical Mill house life history Data-30072026.xlsx | Secondary Rotary Screen No-1 | 7ea20abab10d | ZIL/GSM/SP/ELECT/MH/31
electrical Mill house life history Data-30072026.xlsx | Primary Rotary Screen | d5a12edd9a99 | ZIL/GSM/SP/ELECT/MH/32
electrical Mill house life history Data-30072026.xlsx | Screen Juice Pump-1 Ref. | d4cf174640b3 | ZIL/GSM/SP/ELECT/MH/33
electrical Mill house life history Data-30072026.xlsx | Screen Juice Pump-2 Ref. | 40874a1f5235 | ZIL/GSM/SP/ELECT/MH/34
electrical Mill house life history Data-30072026.xlsx | DS Screen Juice Pump-1 | 949391122c0b | ZIL/GSM/SP/ELECT/MH/35
electrical Mill house life history Data-30072026.xlsx | DS Screen Juice Pump-2 | ef91aabd20cb | ZIL/GSM/SP/ELECT/MH/36
electrical Mill house life history Data-30072026.xlsx | 1 st Stage Screen Juice Pump-1 | 2a026b1dd4a3 | ZIL/GSM/SP/ELECT/MH/37
electrical Mill house life history Data-30072026.xlsx | 1 st Stage Screen Juice Pump-2 | c08c6c21f044 | ZIL/GSM/SP/ELECT/MH/38
electrical Mill house life history Data-30072026.xlsx | Cooling Tower Pump-1 Motor | 583ef04a018e | ZIL/GSM/SP/ELECT/MH/39
electrical Mill house life history Data-30072026.xlsx | Cooling Tower Pump-2 Motor | 5c12aeaa8129 | ZIL/GSM/SP/ELECT/MH/40
electrical Mill house life history Data-30072026.xlsx | Hot Water Imbibition Pump-1 | ee6618a17ff5 | ZIL/GSM/SP/ELECT/MH/41
electrical Mill house life history Data-30072026.xlsx | Hot Water Imbibition Pump-2 | 475510cf7f1f | ZIL/GSM/SP/ELECT/MH/42
electrical Mill house life history Data-30072026.xlsx | Zero Mill Juice Pump-1 | 49d4599fd86d | ZIL/GSM/SP/ELECT/MH/43
electrical Mill house life history Data-30072026.xlsx | Zero Mill Juice Pump-2 | d3ea4afed584 | ZIL/GSM/SP/ELECT/MH/44
electrical Mill house life history Data-30072026.xlsx | Mill No-1 Juice Pump-1 | 94c1f1f0811e | ZIL/GSM/SP/ELECT/MH/45
electrical Mill house life history Data-30072026.xlsx | Mill No-1 Juice Pump-2 | 4f456ea36610 | ZIL/GSM/SP/ELECT/MH/46
electrical Mill house life history Data-30072026.xlsx | Mill No-2 Juice Pump-1 | 924949997c40 | ZIL/GSM/SP/ELECT/MH/47
electrical Mill house life history Data-30072026.xlsx | Mill No-2 Juice Pump-2 | 0266594cbb2b | ZIL/GSM/SP/ELECT/MH/48
electrical Mill house life history Data-30072026.xlsx | Mill No-3 Juice Pump-1 | 8f4e613ac91d | ZIL/GSM/SP/ELECT/MH/49
electrical Mill house life history Data-30072026.xlsx | Mill No-3 Juice Pump-2 | 8b4673274358 | ZIL/GSM/SP/ELECT/MH/50
electrical Mill house life history Data-30072026.xlsx | Mill No-4 Juice Pump-1 | aae7e67deecc | ZIL/GSM/SP/ELECT/MH/51
electrical Mill house life history Data-30072026.xlsx | Mill No-4 Juice Pump-2 | f3d0135cbb25 | ZIL/GSM/SP/ELECT/MH/52
electrical Mill house life history Data-30072026.xlsx | Hot Water Pump-3 | 58991dbdb665 | ZIL/GSM/SP/ELECT/MH/53
electrical Mill house life history Data-30072026.xlsx | Aux. Cane Carier oil Pump 1 &2 | 6883ad88637e | ZIL/GSM/SP/ELECT/MH/54
electrical Mill house life history Data-30072026.xlsx | Main Cane Carrier Oil Pump | c8f3734afe11 | ZIL/GSM/SP/ELECT/MH/55
electrical Mill house life history Data-30072026.xlsx | Shredder Oil Pump 1 & 2 | 65b767b4f650 | ZIL/GSM/SP/ELECT/MH/56
electrical Mill house life history Data-30072026.xlsx | Zero Mill Oil Pump 1 & 2 | 75eedf0781a5 | ZIL/GSM/SP/ELECT/MH/57
electrical Mill house life history Data-30072026.xlsx | Slate Cleaning Brush Motor | 61b6b133d3bf | ZIL/GSM/SP/ELECT/MH/58
electrical Mill house life history Data-30072026.xlsx | MILL EOT 50 MT | 7ca7e0834751 | ZIL/GSM/SP/ELECT/MH/59
electrical Mill house life history Data-30072026.xlsx | MILL EOT 25 MT | 278a6bafc3d8 | ZIL/GSM/SP/ELECT/MH/60
electrical Mill house life history Data-30072026.xlsx | Truck Tripler | 2ae969efa411 | ZIL/GSM/SP/ELECT/MH/61
electrical Mill house life history Data-30072026.xlsx | Air Conditioner | b65b65e052d9 | ZIL/GSM/SP/ELECT/MH/62
2_70 TPH boiler life history.xlsx | Control Room A.C | be4f92f1b6f3 | ZIL/GSM/SP/ELCT/70 TPH/52
2_70 TPH boiler life history.xlsx | C.T Fan-2 | d0376042701f | ZIL/GSM/SP/ELCT/MH/50
2_70 TPH boiler life history.xlsx | C.T Fan-1 | 03cee6cd6ee8 | ZIL/GSM/SP/ELCT/MH/49
2_70 TPH boiler life history.xlsx | Cooling Tower Pump-2 | a3950a24a73f | ZIL/GSM/SP/ELCT/MH/48
2_70 TPH boiler life history.xlsx | Cooling Tower Pump-1 | b8caff109e6d | ZIL/GSM/SP/ELCT/MH/47
2_70 TPH boiler life history.xlsx | UGR Pump NO-3 | 24485eebd568 | ZIL/GSM/SP/ELCT/MH/46
2_70 TPH boiler life history.xlsx | UGR Pump NO-2 | b0daab9b6718 | ZIL/GSM/SP/ELCT/MH/45
2_70 TPH boiler life history.xlsx | UGR Pump NO-1 | 9f1f45dca11b | ZIL/GSM/SP/ELCT/MH/44
2_70 TPH boiler life history.xlsx | CHEMICAL DOSING PUMP-2 | f9848ed33ca0 | ZIL/GSM/SP/ELCT/70 TPH/43
2_70 TPH boiler life history.xlsx | CHEMICAL DOSING PUMP-1 | 85294b29c704 | ZIL/GSM/SP/ELCT/70 TPH/42
2_70 TPH boiler life history.xlsx | BAGAS BLOWER-3 | 905c352537a7 | ZIL/GSM/SP/ELCT/BH/41
2_70 TPH boiler life history.xlsx | BAGAS BLOWER-2 | 46336f87db96 | ZIL/GSM/SP/ELCT/BH/40
2_70 TPH boiler life history.xlsx | BAGAS BLOWER-1 | e3445e6f2460 | ZIL/GSM/SP/ELCT/BH/39
2_70 TPH boiler life history.xlsx | S.A Fan-2 | b1b37c55efce | ZIL/GSM/SP/ELCT/70 TPH/38
2_70 TPH boiler life history.xlsx | PCC & MCC PANEL | 9bd6cf49ab16 | ZIL/GSM/SP/ELCT/70 TPH/37
2_70 TPH boiler life history.xlsx | Transfer pump | 8ef4fc57a116 | ZIL/GSM/SP/ELCT/70 TPH/36
2_70 TPH boiler life history.xlsx | Bagas Elevator | 92768fde2ff6 | ZIL/GSM/SP/ELCT/70 TPH/35
2_70 TPH boiler life history.xlsx | RBC | bbd72cd93434 | ZIL/GSM/SP/ELCT/70 TPH/34
2_70 TPH boiler life history.xlsx | MBC | 9f2862f2d79e | ZIL/GSM/SP/ELCT/70 TPH/33
2_70 TPH boiler life history.xlsx | F.D Fan | 3acf66164a31 | ZIL/GSM/SP/ELCT/70 TPH/32
2_70 TPH boiler life history.xlsx | Bagas Feeder-6 | 0eaf8221f4e5 | ZIL/GSM/SP/ELCT/70 TPH/31
2_70 TPH boiler life history.xlsx | Bagas Feeder-2 | ed04e2fdd164 | ZIL/GSM/SP/ELCT/70 TPH/30
2_70 TPH boiler life history.xlsx | Bagas Feeder-1 | 3eaa98fe3cea | ZIL/GSM/SP/ELCT/70 TPH/29
2_70 TPH boiler life history.xlsx | Back Wash Pump Motor | 2e4ccad4bc6c | ZIL/GSM/SP/ELCT/70 TPH/28
2_70 TPH boiler life history.xlsx | Shellery Pump No-3 Motor | b828d471a785 | ZIL/GSM/SP/ELCT/70 TPH/27
2_70 TPH boiler life history.xlsx | Shellery Pump No-2 Motor | fc1541a9339d | ZIL/GSM/SP/ELCT/70 TPH/26
2_70 TPH boiler life history.xlsx | Shellery Pump No-1 Motor | 1b21cdcf1a5a | ZIL/GSM/SP/ELCT/70 TPH/25
2_70 TPH boiler life history.xlsx | Injection Pump No.3 Motor | 96cd42fc75e9 | ZIL/GSM/SP/ELCT/70 TPH/24
2_70 TPH boiler life history.xlsx | Injection Pump No.2 Motor | 0c0623c999d2 | ZIL/GSM/SP/ELCT/70 TPH/23
2_70 TPH boiler life history.xlsx | Injection Pump No.1 Motor | 2646a29ad079 | ZIL/GSM/SP/ELCT/70 TPH/22
2_70 TPH boiler life history.xlsx | Soot blower LRSB No.-2 | b191a8de1096 | ZIL/GSM/SP/ELCT/70 TPH/21
2_70 TPH boiler life history.xlsx | Soot blower LRSB No.-1 | 7060d351d647 | ZIL/GSM/SP/ELCT/70 TPH/20
2_70 TPH boiler life history.xlsx | Soot blower No.-7 | 6c5eb0dc3ce0 | ZIL/GSM/SP/ELCT/70 TPH/19
2_70 TPH boiler life history.xlsx | Soot blower No.-6 | 393ef88b14aa | ZIL/GSM/SP/ELCT/70 TPH/18
2_70 TPH boiler life history.xlsx | Soot blower No.-5 | 62d49f38a125 | ZIL/GSM/SP/ELCT/70 TPH/17
2_70 TPH boiler life history.xlsx | Soot blower No.-4 | 8bae9acec9f2 | ZIL/GSM/SP/ELCT/70 TPH/16
2_70 TPH boiler life history.xlsx | Soot blower No.-3 | 29b933d4f4e9 | ZIL/GSM/SP/ELCT/70 TPH/15
2_70 TPH boiler life history.xlsx | Soot blower No.-2 | ada2db5c822b | ZIL/GSM/SP/ELCT/70 TPH/14
2_70 TPH boiler life history.xlsx | Soot blower No.-1 | 0be4ee47fed1 | ZIL/GSM/SP/ELCT/70 TPH/13
2_70 TPH boiler life history.xlsx | Ash Convayer-1 | 38c19e29aeac | ZIL/GSM/SP/ELCT/70 TPH/12
2_70 TPH boiler life history.xlsx | D-SUPPER HEATER PUMP-2 | dcba26f84010 | ZIL/GSM/SP/ELCT/70 TPH/11
2_70 TPH boiler life history.xlsx | D-SUPPER HEATER PUMP-1 | 48dd28b6b829 | ZIL/GSM/SP/ELCT/70 TPH/10
2_70 TPH boiler life history.xlsx | Feed Pump Motor No.3 | 3f56fc77602f | ZIL/GSM/SP/ELCT/70 TPH/09
2_70 TPH boiler life history.xlsx | Feed Pump Motor No.2 | 0429b063f4dc | ZIL/GSM/SP/ELCT/70 TPH/08
2_70 TPH boiler life history.xlsx | Feed Pump Motor No.1 | 81be79503174 | ZIL/GSM/SP/ELCT/70 TPH/07
2_70 TPH boiler life history.xlsx | S.A Fan Motor No.1 | 0e87c9ccca02 | ZIL/GSM/SP/ELCT/70 TPH/06
2_70 TPH boiler life history.xlsx | I.D Fan Motor No.1 | fd2130ee1788 | ZIL/GSM/SP/ELCT/70 TPH/05
2_70 TPH boiler life history.xlsx | I.D Fan Motor No.2 | e4e65237b99a | ZIL/GSM/SP/ELCT/70 TPH/04
2_70 TPH boiler life history.xlsx | Bagas Feeder No.3 | 186fc1810911 | ZIL/GSM/SP/ELCT/70 TPH/03
2_70 TPH boiler life history.xlsx | Bagas Feeder No. 5 | b3330b85cff6 | ZIL/GSM/SP/ELCT/70 TPH/02
2_70 TPH boiler life history.xlsx | Bagas Feeder No. 4 | 0613e2cb4be0 | ZIL/GSM/SP/ELCT/70 TPH/01
3_Power House life history.xlsx | 3 MW Old alternator No.1 | 45e977a5faac | ZIL/GSM/SP/ELECT/PH/01
3_Power House life history.xlsx | 3 MW Old alternator No. 2 | 2d4ca4f1c78d | ZIL/GSM/SP/ELECT/PH/02
3_Power House life history.xlsx | Power house PCC | 6b2a710f86a6 | ZIL/GSM/SP/ELECT/PH/03
3_Power House life history.xlsx | Power house Transformer | 88c61735fc65 | ZIL/GSM/SP/ELECT/PH/04
3_Power House life history.xlsx | Capacitor Panel | 36d90941b60e | ZIL/GSM/SP/ELECT/PH/05
3_Power House life history.xlsx | Air Conditioner | 38607a69f3d2 | ZIL/GSM/SP/ELCT/PH/06
4_DS Electrical Equipment Life History - MOTORS.xlsx | DS BATCH MC-1 | 7cfff294592a | ZIL/GSM/SP/ELECT/DS/BATCH/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | DS BATCH MC-2 DC MOTOR | 6def177440b5 | ZIL/GSM/SP/ELECT/DS/BATCH/M-02
4_DS Electrical Equipment Life History - MOTORS.xlsx | DS BATCH MC-3 | ad2746d8f458 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03
4_DS Electrical Equipment Life History - MOTORS.xlsx | B-CONTI MC-1 | 522941d634f7 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | B-CONTI MC-2 | 35fcb418488d | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02
4_DS Electrical Equipment Life History - MOTORS.xlsx | B-CONTI MC-3 | 54a769fa40d7 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03
4_DS Electrical Equipment Life History - MOTORS.xlsx | B-CONTI MC-4 | 6788c926e1d7 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04
4_DS Electrical Equipment Life History - MOTORS.xlsx | SPRAY-1 | 67cc6f53d340 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | INJECTION-1 | ec13bcd72998 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | INJECTION-4 | 8a1370e488c0 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04
4_DS Electrical Equipment Life History - MOTORS.xlsx | INJECTION-5 | 294b34b0d597 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05
4_DS Electrical Equipment Life History - MOTORS.xlsx | C-CONTI-1 | ec89beb0f12b | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | C-CONTI-3 | bb397fb51401 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03
4_DS Electrical Equipment Life History - MOTORS.xlsx | C-CONTI-4 | d035ca63a238 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04
4_DS Electrical Equipment Life History - MOTORS.xlsx | C-CONTI-5 | ae9191c2f449 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05
4_DS Electrical Equipment Life History - MOTORS.xlsx | C-CONTI-6 | 7f894c1cfcff | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06
4_DS Electrical Equipment Life History - MOTORS.xlsx | C-CONTI-7 | 297e27c093cd | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07
4_DS Electrical Equipment Life History - MOTORS.xlsx | C-CONTI-9 | 06069ef28f45 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09
4_DS Electrical Equipment Life History - MOTORS.xlsx | C-CONTI-10 | ae1bea521916 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10
4_DS Electrical Equipment Life History - MOTORS.xlsx | CLEAR JUICE PUMP MOTOR-1 | d8508e86acff | ZIL/GSM/SP/ELECT/DS/CJ/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | CLEAR JUICE PUMP MOTOR-2 | 6d1e304f8f8b | ZIL/GSM/SP/ELECT/DS/CJ/M-02
4_DS Electrical Equipment Life History - MOTORS.xlsx | SEMI KESTNER JUICE TRANSFER -1 | 616a3e706daa | ZIL/GSM/SP/ELECT/DS/SK/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | SEMI KESTNER JUICE TRANSFER -2 | 150d14d6e2b1 | ZIL/GSM/SP/ELECT/DS/SK/M-02
4_DS Electrical Equipment Life History - MOTORS.xlsx | Vapour cell juice TF pump-1 | 9ea41d709fd3 | ZIL/GSM/SP/ELECT/DS/VC/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | Vapour cell juice TF-2 | 8bfe573ffe41 | ZIL/GSM/SP/ELECT/DS/VC/M-02
4_DS Electrical Equipment Life History - MOTORS.xlsx | COMMON CONDENSATE-1 | bd45edf4260a | ZIL/GSM/SP/ELECT/DS/CC/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | COMMON CONDENSATE-2 | 68491d7f2ee9 | ZIL/GSM/SP/ELECT/DS/CC/M-02
4_DS Electrical Equipment Life History - MOTORS.xlsx | FFE(2500)-1 | 776f1fe47a51 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | FFE(2500)-2 | c2527a93343d | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02
4_DS Electrical Equipment Life History - MOTORS.xlsx | FFE(2500)T-1 | f7f5138c0071 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | FFE(2500)T-2 | fb6b0fce857c | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02
4_DS Electrical Equipment Life History - MOTORS.xlsx | FFE(1250)-1 | 3ea7585630eb | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | FFE(1250)-2 | 8b9f5f930d8c | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02
4_DS Electrical Equipment Life History - MOTORS.xlsx | FFE(1250)T-1 | 475d22660434 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | FFE(1250)T-2 | b6d6708cc8ad | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02
4_DS Electrical Equipment Life History - MOTORS.xlsx | ETP COMPRESSOR-1 | 1cb9bc6f28c9 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01
4_DS Electrical Equipment Life History - MOTORS.xlsx | ETP COMPRESSOR-2 | cddbe671aa0e | ZIL/GSM/SP/ELECT/DS/ETP C/M-02
4_DS Electrical Equipment Life History - MOTORS.xlsx | ETP COMPRESSOR-3 | 59dff8d3563e | ZIL/GSM/SP/ELECT/DS/ETP C/M-03
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | VACUUM FILTER 14'x36' | 507848044fc6 | ZIL/GSM/SP/ELECT/DS/VFD/14'x36'
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | VACUUM FILTER 14'x30 | ebc2f73d2f54 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30'
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | Distillery W S Pump-1 | 0e6b1d866a20 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | Distillery W S Pump-2 | 144b3a144cb8 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | MOLTEN SULPHUR DOSING PUMP(E) | c6c9b109879f | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E)
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | MOLTEN SULPHUR DOSING PUMP(W) | be61d63bf5d0 | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W)
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | AIR BLOWER NO.3 | 9d66c4e44b79 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | CLEAR JUICE PUMP-1 | 7f66c3ac4739 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | Injection Pump No.5 | dfdb59e34766 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | DS 1750 WIL AC-1 | 0d325cf72b67 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | DS 1750 NHEC DC-2 | 193d0a777007 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | DS 1750 WIL AC-3 | f140f6187093 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3

## EQUIPMENT LIFE HISTORY CARD
source file | sheet id | sheet name | EQUIPMENT TAG NO | NAME OF EQUIPMENT | LOCATION | DATE OF COMMISSIONING | Main Equipment | Sub Equipment | Department
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | SHREDDER MOTOR 1 & PANEL | CANE PREPRATORY |  | SHREDDER | SHREDDER MOTOR 1 & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 | SHREDDER MOTOR 2 & PANEL | CANE PREPRATORY |  | SHREDDER | SHREDDER MOTOR 2 & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | ZERO MILL DRIVE MOTOR & PANEL | MILLING |  | ZERO MILL | ZERO MILL DRIVE MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | FOURTH MILL DRIVE MOTOR & PANEL | MILLING |  | FOURTH MILL | FOURTH MILL DRIVE MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | CANE UNLOADER 1 MOTOR & PANEL | CANE HANDLING |  | CANE UNLOADER 1 | CANE UNLOADER 1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | CANE UNLOADER 2 MOTOR & PANEL | CANE HANDLING |  | CANE UNLOADER 2 | CANE UNLOADER 2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | CANE UNLOADER 3 MOTOR & PANEL | CANE HANDLING |  | CANE UNLOADER 3 | CANE UNLOADER 3 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | CANE UNLOADER 4 MOTOR & PANEL | CANE HANDLING |  | CANE UNLOADER 4 | CANE UNLOADER 4 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | CANE UNLOADER 5 MOTOR & PANEL | CANE HANDLING |  | CANE UNLOADER 5 | CANE UNLOADER 5 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | CANE UNLOADER 6 MOTOR & PANEL | CANE HANDLING |  | CANE UNLOADER 6 | CANE UNLOADER 6 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | DISTRIBUTION TRANSFORMER 3.15 MVA & PANEL | MILL TRANSFORMER YARD |  | MILL TRANSFORMER | DISTRIBUTION TRANSFORMER 3.15 MVA & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | CONVERTER TRANSFORMER 2.5 MVA & PANEL | MILL TRANSFORMER YARD |  | MILL TRANSFORMER | CONVERTER TRANSFORMER 2.5 MVA & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | H.T PCC PANEL | MILL ELECT PANEL ROOM |  | MILL ELECTRICAL PANEL | H.T PCC PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | L.T PCC & MCC PANEL | MILL ELECT PANEL ROOM |  | MILL ELECTRICAL PANEL | L.T PCC & MCC PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | VFD PANEL | MILL ELECT PANEL ROOM |  | MILL ELECTRICAL PANEL | VFD PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | FOURTH MILL BLOWER MOTOR & PANEL | MILLING |  | FOURTH MILL | FOURTH MILL BLOWER MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | AUX CANE CARRIER MOTOR & PANEL | CANE HANDLING |  | AUXILLERY CANE CARRIER | AUX CANE CARRIER MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | MAIN CANE CARRIER MOTOR & PANEL | CANE HANDLING |  | MAIN CANE CARRIER | MAIN CANE CARRIER MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | CARDIAN DRUM-1 MOTOR & PANEL | CANE PREPRATORY |  | CARDIAN DRUM 1 | CARDIAN DRUM-1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | CARDIAN DRUM-2 MOTOR & PANEL | CANE PREPRATORY |  | CARDIAN DRUM 2 | CARDIAN DRUM-2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | CANE KICKER MOTOR & PANEL | CANE PREPRATORY |  | CANE KICKER | CANE KICKER MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | FEEDER DRUM MOTOR & PANEL | CANE PREPRATORY |  | FEEDER DRUM | FEEDER DRUM MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | SHREDDER CARRIER MOTOR & PANEL | CANE PREPRATORY |  | SHREDDER RAKE CARRIER | SHREDDER CARRIER MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | SHREDDER BELT CONVEYORV MOTOR & PANEL | MILLING |  | SHREDDER BELT CONVEYOR | SHREDDER BELT CONVEYORV MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | CANE EQUALIZER MOTOR & PANEL | MILLING |  | CANE EQUALIZER OF SHREDDER BELT | CANE EQUALIZER MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | INTER RAKE CARRIER NO.1 MOTOR & PANEL | MILLING |  | INTER RAKE CARRIER 1 | INTER RAKE CARRIER NO.1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | INTER RAKE CARRIER NO.2 MOTOR & PANEL | MILLING |  | INTER RAKE CARRIER 2 | INTER RAKE CARRIER NO.2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | INTER RAKE CARRIER NO.3 MOTOR & PANEL | MILLING |  | INTER RAKE CARRIER 3 | INTER RAKE CARRIER NO.3 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | INTER RAKE CARRIER NO.4 MOTOR & PANEL | MILLING |  | INTER RAKE CARRIER 4 | INTER RAKE CARRIER NO.4 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | SECONDARY JUICE ROTARY SCREEN NO-2 MOTOR & PANEL | MILLING |  | SECONDARY JUICE ROTARY SCREEN-2 | SECONDARY JUICE ROTARY SCREEN NO-2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | SECONDARY JUICE ROTARY SCREEN NO-1 MOTOR & PANEL | MILLING |  | SECONDARY JUICE ROTARY SCREEN -1 | SECONDARY JUICE ROTARY SCREEN NO-1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | PRIMERY JUICE ROTARY SCREEN NO-1 MOTOR & PANEL | MILLING |  | PRIMERY JUICE ROTARY SCREEN | PRIMERY JUICE ROTARY SCREEN NO-1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | REF SCREEN JUICE PUMP NO.1 MOTOR & PANEL | MILLING |  | REFINERY SCREEN JUICE PUMP-1 | REF SCREEN JUICE PUMP NO.1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | REF SCREEN JUICE PUMP NO.2 MOTOR & PANEL | MILLING |  | REFINERY SCREEN JUICE PUMP-2 | REF SCREEN JUICE PUMP NO.2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | DS SCREEN JUICE PUMP NO.1 MOTOR & PANEL | MILLING |  | DS SCREEN JUICE PUMP-1 | DS SCREEN JUICE PUMP NO.1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | DS SCREEN JUICE PUMP NO.2 MOTOR & PANEL | MILLING |  | DS SCREEN JUICE PUMP-2 | DS SCREEN JUICE PUMP NO.2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 1st STAGE SCREEN JUICE PUMP NO-1 MOTOR & PANEL | MILLING |  | 1st STAGE SCREEN JUICE PUMP NO-1 | 1st STAGE SCREEN JUICE PUMP NO-1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 1st STAGE SCREEN JUICE PUMP NO-2 MOTOR & PANEL | MILLING |  | 1st STAGE SCREEN JUICE PUMP NO-2 | 1st STAGE SCREEN JUICE PUMP NO-2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | COOLING TOWER PUMP NO-1 MOTOR & PANEL | MILLING |  | COOLING TOWER | COOLING TOWER PUMP NO-1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | COOLING TOWER PUMP NO-2 MOTOR & PANEL | MILLING |  | COOLING TOWER | COOLING TOWER PUMP NO-2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | HOT WATER IMBIBITION PUMP NO-1 MOTOR & PANEL | MILLING |  | HOT WATER IMBIBITION PUMP-1 | HOT WATER IMBIBITION PUMP NO-1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | HOT WATER IMBIBITION PUMP NO-2 MOTOR & PANEL | MILLING |  | HOT WATER IMBIBITION PUMP-2 | HOT WATER IMBIBITION PUMP NO-2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | ZERO MILL JUICE PUMP NO-1 MOTOR & PANEL | MILLING |  | ZERO MILL | ZERO MILL JUICE PUMP NO-1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | ZERO MILL JUICE PUMP NO-2 MOTOR & PANEL | MILLING |  | ZERO MILL | ZERO MILL JUICE PUMP NO-2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | MILL NO.1 JUICE PUMP NO-1 MOTOR & PANEL | MILLING |  | MILL NO 1 | MILL NO.1 JUICE PUMP NO-1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | MILL NO.1 JUICE PUMP NO-2 MOTOR & PANEL | MILLING |  | MILL NO 1 | MILL NO.1 JUICE PUMP NO-2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | MILL NO.2 JUICE PUMP NO-1 MOTOR & PANEL | MILLING |  | MILL NO 2 | MILL NO.2 JUICE PUMP NO-1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | MILL NO.2 JUICE PUMP NO-2 MOTOR & PANEL | MILLING |  | MILL NO 2 | MILL NO.2 JUICE PUMP NO-2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | MILL NO.3 JUICE PUMP NO-1 MOTOR & PANEL | MILLING |  | MILL NO 3 | MILL NO.3 JUICE PUMP NO-1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | MILL NO.3 JUICE PUMP NO-2 MOTOR & PANEL | MILLING |  | MILL NO 3 | MILL NO.3 JUICE PUMP NO-2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | MILL NO.4 JUICE PUMP NO-1 MOTOR & PANEL | MILLING |  | MILL NO 4 | MILL NO.4 JUICE PUMP NO-1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | MILL NO.4 JUICE PUMP NO-2 MOTOR & PANEL | MILLING |  | MILL NO 4 | MILL NO.4 JUICE PUMP NO-2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | HOT WATER IMBIBITION PUMP NO-3 MOTOR & PANEL | MILLING |  | COOLING TOWER | HOT WATER IMBIBITION PUMP NO-3 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | AUX. CANE CARRIER OIL PUMP 1 & 2 MOTOR & PANEL | CANE HANDLING |  | AUXILLERY CANE CARRIER OIL PUMP | AUX. CANE CARRIER OIL PUMP 1 & 2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | MAIN CANE CARRIER OIL PUMP 1 MOTOR & PANEL | CANE HANDLING |  | MAIN CANE CARRIER | MAIN CANE CARRIER OIL PUMP 1 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | SHREDDER OIL PUMP 1 & 2 MOTOR & PANEL | CANE PREPRATORY |  | SHREDDER OIL PUMP | SHREDDER OIL PUMP 1 & 2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | ZERO MILL OIL PUMP 1 & 2 MOTOR & PANEL | MILLING |  | ZERO MILL | ZERO MILL OIL PUMP 1 & 2 MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | SLATE CLEANING BRUSH MOTOR & PANEL | CANE HANDLING |  | MAIN CANE CARRIER | SLATE CLEANING BRUSH MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | MILL EOT 50 TON MOTOR & PANEL | MILLING |  | MILL EOT CRANE 50 MT | MILL EOT 50 TON MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | MILL EOT 25 TON MOTOR & PANEL | MILLING |  | MILL EOT CRANE 25 MT | MILL EOT 25 TON MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | TRUCK TRIPLER MOTOR & PANEL | CANE HANDLING |  | TRUCK TRIPLER | TRUCK TRIPLER MOTOR & PANEL | ELECTRICAL
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | VFD CONTROL ROOM AIR CONDITIONER | MILLING |  | AIR CONDITIONER | VFD CONTROL ROOM AIR CONDITIONER | ELECTRICAL
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | CONTROL ROOM AIR CONDITIONER | 70 TPH BOILER |  | CONTROL ROOM | CONTROL ROOM AIR CONDITIONER | ELECTRICAL
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | COOLING TOWER NO.3 FAN MOTOR & PANEL | MILLING |  | COOLING TOWER NO.2 | COOLING TOWER NO.2 FAN MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | COOLING TOWER NO.1 FAN MOTOR & PANEL | MILLING |  | COOLING TOWER NO.1 | COOLING TOWER NO.1 FAN MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | COOLING TOWER PUMP NO-2 MOTOR & PANEL | MILLING |  | COOLING TOWER | COOLING TOWER PUMP NO-2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | COOLING TOWER PUMP NO-1 MOTOR & PANEL | MILLING |  | COOLING TOWER | COOLING TOWER PUMP NO-1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | UGR PUMP NO-3 MOTOR & PANEL | MILLING |  | UNDER GROUND RESORVIOR (UGR) | UGR PUMP NO-3 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | UGR PUMP NO-2 MOTOR & PANEL | MILLING |  | UNDER GROUND RESORVIOR (UGR) | UGR PUMP NO-2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | UGR PUMP NO-1 MOTOR & PANEL | MILLING |  | UNDER GROUND RESORVIOR (UGR) | UGR PUMP NO-1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | CHEMICAL DOSING PUMP-2 MOTOR & PANEL | 70 TPH BOILER |  | CHEMICAL DOSING PUMP-2 | CHEMICAL DOSING PUMP-2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | CHEMICAL DOSING PUMP-1 MOTOR & PANEL | 70 TPH BOILER |  | CHEMICAL DOSING PUMP-1 | CHEMICAL DOSING PUMP-1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | BAGAS BLOWER-3 MOTOR & PANEL | BOILING HOUSE |  | BAGAS BLOWER-3 | BAGAS BLOWER-3 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | BAGAS BLOWER-2 MOTOR & PANEL | BOILING HOUSE |  | BAGAS BLOWER-2 | BAGAS BLOWER-2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | BAGAS BLOWER-1 MOTOR & PANEL | BOILING HOUSE |  | BAGAS BLOWER-1 | BAGAS BLOWER-1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | S.A FAN-2 MOTOR & PANEL | 70 TPH BOILER |  | S.A FAN-2 | S.A FAN-2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | PCC & MCC PANEL | 70 TPH BOILER |  | PCC & MCC PANEL | PCC & MCC PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | TRANSFER PUMP MOTOR & PANEL | 70 TPH BOILER |  | TRANSFER PUMP | TRANSFER PUMP MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | BAGAS ELEVATOR MOTOR & PANEL | 70 TPH BOILER |  | BAGAS ELEVATOR | BAGAS ELEVATOR MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | RBC MOTOR & PANEL | 70 TPH BOILER |  | RBC | RBC MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | MBC MOTOR & PANEL | 70 TPH BOILER |  | MBC | MBC MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | F.D FAN MOTOR & PANEL | 70 TPH BOILER |  | F.D FAN | F.D FAN MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | BAGAS FEEDER NO. 6 MOTOR & PANEL | 70 TPH BOILER |  | BAGAS FEEDER NO. 6 | BAGAS FEEDER NO. 6 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | BAGAS FEEDER NO. 2 MOTOR & PANEL | 70 TPH BOILER |  | BAGAS FEEDER NO. 2 | BAGAS FEEDER NO. 2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | BAGAS FEEDER NO.1 MOTOR & PANEL | 70 TPH BOILER |  | BAGAS FEEDER NO. 1 | BAGAS FEEDER NO.1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | BACK WASH PUMP MOTOR & PANEL | 70 TPH BOILER |  | BACK WASH PUMP | BACK WASH PUMP MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | SHELLERY PUMP NO.3 MOTOR & PANEL | 70 TPH BOILER |  | SHELLERY PUMP NO.3 | SHELLERY PUMP NO.3 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | SHELLERY PUMP NO.2 MOTOR & PANEL | 70 TPH BOILER |  | SHELLERY PUMP NO.2 | SHELLERY PUMP NO.2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | SHELLERY PUMP NO.1 MOTOR & PANEL | 70 TPH BOILER |  | SHELLERY PUMP NO.1 | SHELLERY PUMP NO.1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | INJECTION PUMP NO.3 MOTOR & PANEL | 70 TPH BOILER |  | INJECTION PUMP NO.3 | INJECTION PUMP NO.3 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | INJECTION PUMP NO.2 MOTOR & PANEL | 70 TPH BOILER |  | INJECTION PUMP NO.2 | INJECTION PUMP NO.2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | INJECTION PUMP NO.1 MOTOR & PANEL | 70 TPH BOILER |  | INJECTION PUMP NO.1 | INJECTION PUMP NO.1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | SOOT BLOWER LRSB NO.2 MOTOR & PANEL | 70 TPH BOILER |  | SOOT BLOWER LRSB NO.2 | SOOT BLOWER LRSB NO.2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | SOOT BLOWER LRSB NO.1 MOTOR & PANEL | 70 TPH BOILER |  | SOOT BLOWER LRSB NO.1 | SOOT BLOWER LRSB NO.1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | SOOT BLOWER NO.7 MOTOR & PANEL | 70 TPH BOILER |  | SOOT BLOWER LRSB NO.7 | SOOT BLOWER NO.7 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | SOOT BLOWER NO.6 MOTOR & PANEL | 70 TPH BOILER |  | SOOT BLOWER LRSB NO.6 | SOOT BLOWER NO.6 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | SOOT BLOWER NO.5 MOTOR & PANEL | 70 TPH BOILER |  | SOOT BLOWER LRSB NO.5 | SOOT BLOWER NO.5 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | SOOT BLOWER NO.4 MOTOR & PANEL | 70 TPH BOILER |  | SOOT BLOWER LRSB NO.4 | SOOT BLOWER NO.4 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | SOOT BLOWER NO.3 MOTOR & PANEL | 70 TPH BOILER |  | SOOT BLOWER LRSB NO.3 | SOOT BLOWER NO.3 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | SOOT BLOWER NO.2 MOTOR & PANEL | 70 TPH BOILER |  | SOOT BLOWER LRSB NO.2 | SOOT BLOWER NO.2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | SOOT BLOWER NO.1 MOTOR & PANEL | 70 TPH BOILER |  | SOOT BLOWER LRSB NO.1 | SOOT BLOWER NO.1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | ASH CONVEYOR-1 MOTOR & PANEL | 70 TPH BOILER |  | ASH CONVEYOR-1 | ASH CONVEYOR-1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | D-SUPPER HEATER PUMP-2 MOTOR & PANEL | 70 TPH BOILER |  | D-SUPPER HEATER PUMP-2 | D-SUPPER HEATER PUMP-2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | D-SUPPER HEATER PUMP-1 MOTOR & PANEL | 70 TPH BOILER |  | D-SUPPER HEATER PUMP-1 | D-SUPPER HEATER PUMP-1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | FEED PUMP NO.3 MOTOR & PANEL | 70 TPH BOILER |  | FEED PUMP NO.3 | FEED PUMP NO.3 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | FEED PUMP NO.2 MOTOR & PANEL | 70 TPH BOILER |  | FEED PUMP NO.2 | FEED PUMP NO.2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | FEED PUMP NO.1 MOTOR & PANEL | 70 TPH BOILER |  | FEED PUMP NO.1 | FEED PUMP NO.1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | S.A FAN NO.1 MOTOR & PANEL | 70 TPH BOILER |  | S.A FAN NO.1 | S.A FAN NO.1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | I.D FAN NO.1 MOTOR & PANEL | 70 TPH BOILER |  | I.D FAN NO.1 | I.D FAN NO.1 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | I.D FAN NO.2 MOTOR & PANEL | 70 TPH BOILER |  | I.D FAN NO.2 | I.D FAN NO.2 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | BAGAS FEEDER NO.3 MOTOR & PANEL | 70 TPH BOILER |  | BAGAS FEEDER NO.3 | BAGAS FEEDER NO.3 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | BAGAS FEEDER NO.5 MOTOR & PANEL | 70 TPH BOILER |  | BAGAS FEEDER NO.5 | BAGAS FEEDER NO.5 MOTOR & PANEL | ELECTRICAL
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | BAGAS FEEDER NO.4 MOTOR & PANEL | 70 TPH BOILER |  | BAGAS FEEDER NO.4 | BAGAS FEEDER NO.4 MOTOR & PANEL | ELECTRICAL
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | OLD 3 MW ALTERNATOR | STEAM TG SET |  | OLD POWER STEAM TURBINE ALTENATOR (OLD-STG) | OLD 3 MW ALTERNATOR | ELECTRICAL
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | OLD 3 MW ALTERNATOR | STEAM TG SET |  | NEW POWER STEAM TURBINE (NEW-STG) | NEW 3 MW ALTERNATOR | ELECTRICAL
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | L.T PCC PANEL | POWER HOUSE ELECT PANEL |  | POWER HOUSE LT PCC | L.T PCC PANEL | ELECTRICAL
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | TRANSFORMER 2.5 MVA | POWER HOUSE TRANSFORMER |  | POWER HOUSE TRANSFORMER 2.5 MVA | TRANSFORMER 2.5 MVA | ELECTRICAL
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | CAPACITOR PANEL | POWER HOUSE ELECT PANEL |  | POWER HOUSE LT PCC | CAPACITOR PANEL | ELECTRICAL
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | CONTROL ROOM AIR CONDITIONER | POWER HOUSE AIR CONDITIONER |  | AIR CONDITIONER | CONTROL ROOM AIR CONDITIONER | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | DS 'A' C/F MACHINE(1750 KG) NO.1 MOTOR(AC) | DS House |  | DS 'A' C/F MACHINE | DS 'A' C/F MACHINE(1750 KG) NO.1 MOTOR(AC) | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | DS 'A' C/F MACHINE(1750 KG) NO.2 MOTOR(DC) | DS House |  | DS 'A' C/F MACHINE | DS 'A' C/F MACHINE(1750 KG) NO.2 MOTOR(DC) | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 | DS 'A' C/F MACHINE(1750 KG) NO.3 MOTOR(AC) | DS House |  | DS 'A' C/F MACHINE | DS 'A' C/F MACHINE(1750 KG) NO.3 MOTOR(AC) | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | DS B-CONTI NO-1 MOTOR | DS House |  | DS B-CONTI MACHINE | DS B-CONTI NO-1 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | DS B-CONTI NO-2 MOTOR | DS House |  | DS B-CONTI MACHINE | DS B-CONTI NO-2 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | DS B-CONTI NO-3 MOTOR | DS House |  | DS B-CONTI MACHINE | DS B-CONTI NO-3 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | DS B-CONTI NO-4 MOTOR | DS House |  | DS B-CONTI MACHINE | DS B-CONTI NO-4 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | DS SPRAY-1 MOTOR | DS House |  | DS SPRAY | DS SPRAY-1 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | DS INJECTION-1 MOTOR | DS House |  | DS INJECTION | DS INJECTION-1 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | DS INJECTION-4 MOTOR | DS House |  | DS INJECTION | DS INJECTION-4 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | DS INJECTION-5 MOTOR | DS House |  | DS INJECTION | DS INJECTION-5 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | DS C-CONTI-1 MOTOR | DS House |  | DS C-CONTI MACHINE | DS C-CONTI-1 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | DS C-CONTI-3 MOTOR | DS House |  | DS C-CONTI MACHINE | DS C-CONTI-3 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | DS C-CONTI-4 MOTOR | DS House |  | DS C-CONTI MACHINE | DS C-CONTI-4 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | DS C-CONTI-5 MOTOR | DS House |  | DS C-CONTI MACHINE | DS C-CONTI-5 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | DS C-CONTI-6 MOTOR | DS House |  | DS C-CONTI MACHINE | DS C-CONTI-6 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | DS C-CONTI-7 MOTOR | DS House |  | DS C-CONTI MACHINE | DS C-CONTI-7 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | DS C-CONTI-9 MOTOR | DS House |  | DS C-CONTI MACHINE | DS C-CONTI-9 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | DS C-CONTI-10 MOTOR | DS House |  | DS C-CONTI MACHINE | DS C-CONTI-10 MOTOR | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | DS CLEAR JUICE PUMP MOTOR-1 | DS House |  | DS CLEAR JUICE | DS CLEAR JUICE PUMP MOTOR-1 | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | DS CLEAR JUICE PUMP MOTOR-2 | DS House |  | DS CLEAR JUICE | DS CLEAR JUICE PUMP MOTOR-2 | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | DS Semi kestner juice transfer pump-1 (South) Motor | DS House |  | DS Semi kestner | DS Semi kestner juice transfer pump-1 (South) Motor | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | DS Semi kestner juice transfer pump-2 (North) Motor | DS House |  | DS Semi kestner | DS Semi kestner juice transfer pump-2 (North) Motor | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | DS Vapour cell juice transfer pump-1(S) Motor | DS House |  | DS Vapour cell juice | DS Vapour cell juice transfer pump-1(S) Motor | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | DS Vapour cell juice transfer pump-2(N) Motor | DS House |  | DS Vapour cell juice | DS Vapour cell juice transfer pump-2(N) Motor | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | DS COMMON CONDENSATE PUMP MOTOR-1 | DS House |  | DS COMMON CONDENSATE | DS COMMON CONDENSATE PUMP MOTOR-1 | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | DS COMMON CONDENSATE PUMP MOTOR-2 | DS House |  | DS COMMON CONDENSATE | DS COMMON CONDENSATE PUMP MOTOR-2 | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | DS FFE(2500) CIRCULATION PUMP NO.1 MOTOR. | DS House |  | DS FFE(2500) CIRCULATION | DS FFE(2500) CIRCULATION PUMP NO.1 MOTOR. | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | DS FFE(2500) CIRCULATION PUMP NO.2 MOTOR. | DS House |  | DS FFE(2500) CIRCULATION | DS FFE(2500) CIRCULATION PUMP NO.2 MOTOR. | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | DS FFE(2500) TRANSFER PUMP NO.1 MOTOR. | DS House |  | DS FFE(2500) TRANSFER | DS FFE(2500) TRANSFER PUMP NO.1 MOTOR. | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | DS FFE(2500) TRANSFER PUMP NO.2 MOTOR. | DS House |  | DS FFE(2500) TRANSFER | DS FFE(2500) TRANSFER PUMP NO.2 MOTOR. | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | DS FFE(1250) CIRCULATION PUMP NO.1 MOTOR. | DS House |  | DS FFE(1250) CIRCULATION | DS FFE(1250) CIRCULATION PUMP NO.1 MOTOR. | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | DS FFE(1250) CIRCULATION PUMP NO.2 MOTOR. | DS House |  | DS FFE(1250) CIRCULATION | DS FFE(1250) CIRCULATION PUMP NO.2 MOTOR. | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | DS FFE(1250) TRANSFER PUMP NO.1 MOTOR. | DS House |  | DS FFE(1250) TRANSFER | DS FFE(1250) TRANSFER PUMP NO.1 MOTOR. | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | DS FFE(1250) TRANSFER PUMP NO.2 MOTOR. | DS House |  | DS FFE(1250) TRANSFER | DS FFE(1250) TRANSFER PUMP NO.2 MOTOR. | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | DS ETP COMPRESSOR NO.1 MOTOR. | DS House |  | DS ETP COMPRESSOR | DS ETP COMPRESSOR NO.1 MOTOR. | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | DS ETP COMPRESSOR NO.2 MOTOR. | DS House |  | DS ETP COMPRESSOR | DS ETP COMPRESSOR NO.2 MOTOR. | ELECTRICAL
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | DS ETP COMPRESSOR NO.3 MOTOR. | DS House |  | DS ETP COMPRESSOR | DS ETP COMPRESSOR NO.3 MOTOR. | ELECTRICAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | DS VACUUM filter 14'x36' VFD PANEL | DS House |  | DS VACUUM filter 14'x36' | DS VACUUM filter 14'x36' VFD PANEL | ELECTRICAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | DS VACUUM filter 14'x30' VFD PANEL | DS House |  | DS VACUUM filter 14'x30' | DS VACUUM filter 14'x30' VFD PANEL | ELECTRICAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | DS Distillery Syrup weightment Pump no.1 VFD PANEL | DS House |  | Distillery Syrup weightment | DS Distillery Syrup weightment Pump no.1 VFD PANEL | ELECTRICAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | DS Distillery Syrup weightment Pump no.2 VFD PANEL | DS House |  | Distillery Syrup weightment | DS Distillery Syrup weightment Pump no.2 VFD PANEL | ELECTRICAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | DS Molten Sulphur Dosing pump(E) VFD PANEL | DS House |  | DS Molten Sulphur Dosing | DS Molten Sulphur Dosing pump(E) VFD PANEL | ELECTRICAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | DS Molten Sulphur Dosing pump(W) VFD PANEL | DS House |  | DS Molten Sulphur Dosing | DS Molten Sulphur Dosing pump(W) VFD PANEL | ELECTRICAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | DS AIR BLOWER NO.3 VFD PANEL | DS House |  | DS AIR BLOWER | DS AIR BLOWER NO.3 VFD PANEL | ELECTRICAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | DS CLEAR JUICE PUMP-1 VFD PANEL | DS House |  | DS CLEAR JUICE PUMP | DS CLEAR JUICE PUMP-1 VFD PANEL | ELECTRICAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | DS INJECTION PUMP NO.5 VFD PANEL | DS House |  | DS INJECTION PUMP | DS INJECTION PUMP NO.5 VFD PANEL | ELECTRICAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | DS 1750 WIL AC VFD PANEL-1 | DS House |  | DS 1750 WIL MACHINE-1 | DS 1750 WIL AC VFD PANEL-1 | ELECTRICAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | DS 1750 NHEC(DC) VFD PANEL-2 | DS House |  | DS 1750 NHEC MACHINE-2 | DS 1750 NHEC(DC) VFD PANEL-2 | ELECTRICAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 | DS 1750 WIL AC VFD PANEL-3 | DS House |  | DS 1750 WIL MACHINE-3 | DS 1750 WIL AC VFD PANEL-3 | ELECTRICAL

## EQUIPMENT SPECIFICATION
source file | sheet id | sheet name | EQUIPMENT TAG NO | section | sub_section | Parameter label | Parameter value
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Make | CROMPTON GREAVES
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Machine Sr. No. | 2131790/01
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Rated RPM | 991
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Bearings DE | NU 240 C3,
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Starter | VCB
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Rated Power | 2500 KW
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Year of Manufacture
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Protection | IP55
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Bearings NDE | NU 236 C3 + 6236 C3
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | VCB Rating | 1250 A
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Rated Voltage | 11 ±10% KV
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Rated Current | 157 Amp.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Frame | UWR710G
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | Winding Insulation Class | F - Class
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  | VCB Make | ABB
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | Rated RPM | 1400
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | Bearing DE | 6201 ZZ
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | Rated Power | 0.37 KW
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | 6202 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | Rated Current | 0.65A
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | Frame | Starter
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | ASR PANEL | DOL
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Make | CROMPTON GREAVES
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Machine Sr. No. | 2131790/02
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Winding Insulation Class | F - Class
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Bearings DE | NU 240 C3,
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Starter | VCB
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Rated Power | 2500 KW
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Year of Manufacture
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Protection | IP55
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Bearings NDE | NU 236 C3 + 6236 C3
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | VCB Rating | 1250 A
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Rated Voltage | 11 ±10% KV
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Rated Current | 157 Amp.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Frame | UWR710G
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | Rated RPM | 991
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  | VCB Make | ABB
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | Rated RPM | 1400
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | Bearing DE | 6201 ZZ
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | Rated Power | 0.37 KW
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | Duty | S1
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | 6202 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | Rated Current | 0.65A
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | Frame | Starter
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | ASR PANEL | DOL
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Rated RPM | 996
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Machine Sr. No. | N8/ 64713928
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Bearings DE | 6330 C3,
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Rated Power | 900 KW
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Protection | IP55
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Year of Manufacture | 09/2014
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Bearings NDE | 6330 C3 (insulated)
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | VFD Model | ACS800-704-0910-7+0F253+A992
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Rated Voltage | 690 V
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Frame | 500
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Rated Current | 907 Amp
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  |  | Winding Insulation Class | H - Class
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Machine Sr. No. | 65268063
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Rated RPM | 996
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Bearings DE | 6232 C3
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Rated Power | 900 KW
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Year of Manufacture | 10/2020
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Protection | IP55
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Bearings NDE | 6228 C3 (insulated)
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | VFD Model | ACS880-304-0820A-7+A018
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Rated Voltage | 690 V
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Rated Current | 2 X 465 Amp
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Frame | N8 / 3006805122 - 100-23
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  |  | Winding Insulation Class | F - Class
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Make | CG
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Machine Sr. No. | BDWG 2666 / KC5554
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Rated Power | 4.5 KW
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Rotor Current | 21 A
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | 6307 ZZ | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | 110 V
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Rated Current | 11.2 Amp
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Duty | S4
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Make | CG
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Machine Sr. No. | 069626957J / KB2048
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Rotor Voltage | 110 V
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Rated Power | 4.5 KW
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Duty | S4
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | 6307 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | 27 A
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Rated Current | 11 Amp
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | L.T MOTOR WEST SIDE | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Make | CG
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Machine Sr. No. | 069626286J/JB1605
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Rated Power | 4 KW
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Rotor Current | 19 A
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | 6307 ZZ | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | 110 V
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Rated Current | 9.8 Amp
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Duty | S4
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Insulation | F/F - Class
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | C.T MOTOR | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | Make | Kirloskar
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | Frame
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | Rated Power | 24.5 KW
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | Rotor Current | Carbon brush
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | 16 X 20 X 32 mm | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | 6313 C3 | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | Rated Current | 40 Amp
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | Duty | S4
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | INS. | F - Class
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 |  | HOIST MOTOR | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Make | BBL
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Machine Sr. No. | M1713358
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Rated Current | 11 Amp
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Rotor Voltage | 110 V
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Rated Power | 4 KW
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Year of Manufacture
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Bearings | DE- 6208ZZ, NDE 6208
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Rotor Current | 26 A
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Protection
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Winding Insulation Class | F/B - Class
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Frame
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Duty | S3
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  |  | Carbon Brush | 9 X 16 X 32 mm
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Make | CG
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Machine Sr. No. | 06962/6901J/J12183
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Rotor Voltage | 110 V
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Rated Power | 4 KW
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Duty | S4
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | 6307 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | 19 A
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Rated Current | 9.8 Amp
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | L.T MOTOR WEST SIDE | Carbon Brush | 9 X 16 X 32 mm
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Make | BBL
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Machine Sr. No. | L1703483
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Rated RPM | 1470
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Frame | 225S
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Rated Power | 37 KW
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Rotor Current | NA
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Protection | 55
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Bearing NDE | 6213 C3
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Rotor Voltage | NA
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Rated Current | 64 Amp
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Duty | S1
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Winding Insulation Class | F/B - Class
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | HYDRAULIC MOTOR | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Make | Havells
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Rated RPM | 1435
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Bearing DE | 6206 ZZ
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Frame | 100L
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Rated Power | 2.2 KW
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Rotor Current | NA
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Protection | 55
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Bearing NDE | 6206 ZZ
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Rotor Voltage | NA
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Rated Current | 5.1 Amp
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Duty | S1
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Winding Insulation Class | F - Class
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 |  | OIL PUMP MOTOR | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Make | CG
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Machine Sr. No. | 069626960J / KB2051
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Rated Power | 4.5 KW
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Rotor Current | 27 A
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | 6307 ZZ | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | 110 V
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Rated Current | 11.2 Amp
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Duty | S4
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  |  | Carbon Brush | 9 X 16 X 32 mm
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Make | CG
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Machine Sr. No. | 06962/6901J/J12183
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Rotor Voltage | 110 V
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Rated Power | 4 KW
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Duty | S4
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | 6307 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | 21 A
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Rated Current | 9.8 Amp
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | L.T MOTOR WEST SIDE | Carbon Brush | 9 X 16 X 32 mm
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Make | BBL
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Machine Sr. No. | LJ808378
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Rated RPM | 1470
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Frame | 225S
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Rated Power | 37 KW
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Rotor Current | NA
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Protection | 55
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Bearing NDE | 6213 C3
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Rotor Voltage | NA
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Rated Current | 63.8 Amp
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Winding Insulation Class | F/B - Class
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 |  | HYDRAULIC MOTOR | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Make | CG
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Machine Sr. No. | 069626949J / KA6923
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Rated Power | 4.5 KW
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Rotor Current | 27 A
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | 6307 ZZ | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | 110 V
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Rated Current | 11 Amp
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Duty | S4
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Make | CG
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Machine Sr. No. | I06962J / KK0881
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Rated RPM | 925
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Rotor Voltage | 110 V
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Rated Power | 4.5 KW
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Duty | S4
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | 6307 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | 27 A
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Rated Current | 11.2 Amp
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | L.T MOTOR EAST SIDE | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Make | CG
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Machine Sr. No. | 068621414J / J10150
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Rated RPM | 920
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Rotor Voltage | 110 V
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Rated Power | 3 KW
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Duty | S4
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | 6307 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | 15 A
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Rated Current | 7.7 Amp
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Frame | DW132S
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | C.T MOTOR | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Make
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Machine Sr. No. | 7CV32058
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Rated RPM | 1470
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Bearing DE | 6312 C3
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Frame | 200L
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Rated Power | 30 KW
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Rotor Current | NA
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Protection | 55
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Bearing NDE | 6212 C3
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Rotor Voltage | NA
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Rated Current | 57 Amp
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Duty | S1
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Winding Insulation Class | F/B - Class
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 |  | HYDRAULIC MOTOR | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Make | CG
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Machine Sr. No. | BDWG2661 / J5402
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Rotor Voltage | 110 V
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Rated Power | 4 KW
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Duty | S4
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | 6307 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | 19 A
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Rated Current | 9.9 Amp
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Make | CG
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Machine Sr. No. | 0DWJ56J / DKAM6168
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Rotor Voltage | 120 V
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Rated Power | 4.5 KW
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Duty | S4
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | 6307 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | 25 A
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Rated Current | 11 Amp
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | L.T MOTOR WEST SIDE | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Make | BBL
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Machine Sr. No. | L1808377
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Rated RPM | 1470
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Frame | 225S
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Rated Power | 37 KW
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Rotor Current | NA
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Protection | 55
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Bearing NDE | 6213 C3
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Rotor Voltage | NA
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Rated Current | 63.8 Amp
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Winding Insulation Class | F/B - Class
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | HYDRAULIC MOTOR | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Make | Havells
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Machine Sr. No. | 1180507483
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Rated RPM | 1435
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Bearing DE | 6206 ZZ
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Frame | 100L
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Rated Power | 2.2 KW
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Rotor Current | NA
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Protection | 55
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Bearing NDE | 6206 ZZ
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Rotor Voltage | NA
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Rated Current | 5.1 Amp
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Winding Insulation Class | F - Class
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 |  | OIL PUMP MOTOR | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Make | CG
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Machine Sr. No. | 069626952J KA6926
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Rotor Voltage | 110 V
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Rated Power | 4.5 KW
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Duty | S4
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | 6307 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | 27 A
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Rated Current | 11 Amp
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  |  | Carbon brush | 9 X 16 X 32 mm
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Make | CG
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Machine Sr. No. | BDWG26, 6 , / KC5552
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Rated RPM | 925
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Rotor Voltage | 110 V
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Rated Power | 4.5 KW
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Duty | S4
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Protection | 55
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Bearing NDE | 6307 ZZ
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Rotor Current | 21 A
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Rated Current | 11.2 Amp
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | L.T MOTOR WEST SIDE | Carbon brush | 9 X 16 X 32 mm
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Make | CG
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Machine Sr. No. | BDWG26, 6 , / KF4859
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Rotor Voltage | 110 V
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Rated Power | 4.5 KW
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Duty | S4
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | 6307 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | 21 A
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Rated Current | 11.2 Amp
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Frame | DW132M
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Winding Insulation Class | F/F - Class
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | C.T MOTOR | Carbon Brush | 9 X 16 X 32 mm
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | Make | Kirloskar
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | Rated RPM | 930
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | Frame
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | Rated Power | 24.5 KW
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | Rotor Current | Carbon brush
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | 16 X 20 X 32 mm | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | 6313 C3 | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | Rated Current | 40 Amp
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | Duty | S4
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | INS. | F - Class
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 |  | HOIST MOTOR | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Rated Power | 3150 KVA
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Rated Current H.V | 165.33A
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Volume of oil | 2620 Ltrs.
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Sr No. | 1712/1
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | LV1 WTI CT as per IS: 2705 | Ratio 420/1.6A, 15VA, CL-1
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Rated Voltage H.V | 11000V
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Rated Current L.V | 4200.1A
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Year of Manufacture | 2015
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Connection | Dyn11
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | LV NCT as per IS: 2705
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Ratio 5000/1A,CL- PS,Vk>850, RCT<20 ohms, @75°C, Imag<30mA@50%VK.
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Rated Voltage L.V | 433V
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Cooling Type | ONAN
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Mass of oil | 2290 Kg.
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 |  |  | Make | Delta
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Rated Power | 2500 KVA
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Rated Current H.V | 131.22A
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Volume of oil | 2905 Ltrs.
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Sr No. | 1715/1
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | HV WTI CT as per IS: 2705 | Ratio 132/1.6A, 15VA, CL-1
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Rated Voltage H.V | 11000V
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Rated Current L.V -1 | 1045.92A
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Year of Manufacture | 2015
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Connection | Dd0yn11
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | LV1 WTI CT as per IS: 2705 | Ratio 1046/1.6A, 15VA, CL-1
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Rated Voltage L.V-1 | 690V
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Rated Current L.V -2 | 1045.92A
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Mass of oil | 2540 Kg.
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Make | Delta
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | LV2 WTI CT as per IS: 2705 | Ratio 1046/1.6A, 15VA, CL-1
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Rated Voltage L.V-2 | 690V
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Cooling Type | ONAN
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | LV NCT as per IS: 2705
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Ratio 5000/1A,CL- PS,Vk>700, RCT<20 ohms, @75°C, Imag<30mA@50%VK. | LV2 NCT as per IS: 2705
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 |  |  | Ratio 1500/1A,CL- PS,Vk>700, RCT<10 ohms, @75°C, Imag<30mA@50%VK.
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Feeder No.1 | Main Incomer VCB
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | 3150 A
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Model | VD4 12.31.40
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | S/N | 1VYN020115001707
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Feeder No.2 | Shredder No.1
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | 1250A
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Model | VD4 12.12.40
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | S/N | 1VYN020114000812
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Feeder No.3 | Shredder No.2
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | 1250A
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Model | VD4 12.12.40
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | S/N | 1VY020113003135
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Feeder No.4 | Distillery
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | 1250A
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Model | VD4 12.12.40
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | S/N | 1VYN010115000136
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Feeder No.5 | Mill house 3.15 MVA , TR
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | 1250A
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Model | VD4 12.12.40
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | S/N | 1VYN020115000220
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Feeder No.6 | Mill house 2.5 MVA , TR
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | 1250A
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Model | VD4 12.12.40
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | S/N | 1VYN020115000214
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Feeder No.7 | Boiling house 3.15 MVA, TR
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | 1250A
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Model | VD4 12.12.40
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | S/N
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Feeder No.8 | Power house 2.5 MVA, TR
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | 1250A
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Model | VD4 12.12.40
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | S/N | 1VYN020115000255
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Feeder No.9 | Raw house 3.15 MVA, TR
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | 1250A
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Model | VD4 12.12.40
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | S/N | 1VYN020115000218
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Feeder No.10 | Raw house 4 MVA, TR
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | 1250A
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Model | VD4 12.12.40
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | S/N | 1VYN020115000217
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | H.T Capacitor Panel-1 | 800KVAR
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 |  |  | H.T Capacitor Panel-1 | 800KVAR
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Feeder No.1 | Main Incomer VCB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | 5000 A
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Model | SACE E6H 50
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | S/N | BF41028913
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Feeder No.2 | Mill House VFD Panel
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | 2000A
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Model | SACE E2N 20
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | S/N
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Feeder No.3 | Tie Feeder
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | 2000A
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Model | SACE E2N 20
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | S/N
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Feeder No.4 | 70 TPH Boiler
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | 1600A
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Model | SACE E1N 16
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | S/N
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Feeder No.5 | Capacitor Panel
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | 800A
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Model | SACE E1N 08
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | S/N
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Feeder No.6 | Air Comp. Aux. Cane carrier, Cane Yard
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | 1250A
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Model | SACE E1N 12
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | S/N
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Feeder No.7 | Cane Unloader
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | 800A
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Model | SACE E1N 08
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | S/N
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Feeder No.8 | Tie Feeder
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | 1250A
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Model | SACE E1N 12
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | S/N
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Feeder No.9 | Mill House MCC- II
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | 1000A
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Model | SACE E1N 10
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | S/N
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Feeder No.10 | Mill House MCC- I
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | 1000A
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Model | SACE E1N 10
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | S/N
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Feeder No.11 | Mill House Existing MCC- I
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | 1000A
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Model | SACE E1N 10
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | S/N
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Feeder No.12 | Mill House Existing MCC- II
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | 1000A
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Model | SACE E1N 10
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | S/N
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  |  | L.T Capacitor Panel-1 | 375KVAR
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  | OF MILL HOUSE MCC PANEL | Mill House MCC- II | Mill House MCC- I
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 |  | OF MILL HOUSE MCC PANEL | Mill House Existing MCC- I | Mill House Existing MCC- II
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.1 | Main Cane Carrier
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS580-363A
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.2 | Stand By
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS850-04-387A-5+J400
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.3 | Screen Juice Pump-1
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS850-04-260A-5+J400
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.4 | Screen Juice Pump-2
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS850-04-260A-5+J400
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.5 | Screen Juice Pump-3
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS850-04-260A-5+J400
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.6 | Drum Feeder
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS580-01-206A-4
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.7 | Imbibition Hot Water Pump
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS850-04-225A-5+J400
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.8 | Shredder Carrier
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS850-04-225A-5+J400
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.9 | Screen Juice Pump-4
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS850-04-225A-5+J400
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.10 | Shredder Cane Belt
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS850-04-144A-5+J400
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.11 | IRC-1
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS580-01-145A-4
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.12 | IRC-2
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS850-04-144A-5+J400
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.13 | IRC-3
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS850-04-144A-5+J400
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Feeder No.14 | IRC-4
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Model | ACS850-04-144A-5+J400
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  | OF MILL HOUSE MCC PANEL | Mill House MCC- II | Mill House MCC- I
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 |  | OF MILL HOUSE MCC PANEL | Mill House Existing MCC- I | Mill House Existing MCC- II
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | Rated RPM | 1480
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | Rated Power | 7.5 KW
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | 6208 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | Frame | Starter
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 |  |  | DOL
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | Make | KEC
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | Rated RPM | 1480
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | Bearing DE | NU319
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | Rated Power | 110 KW
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | 6319 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | Frame | SC315-5
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | Make | Baldor Reliencer
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | Rated RPM | 1480
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | Bearing DE | NU319 EM/C3
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | Rated Power | 110 KW
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | 6319 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | Frame | T3C315M
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | Make | Baldor Reliencer
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | Rated RPM | 1480
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | Bearing DE | 6316 C3
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | Rated Power | 75 KW
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | 6316 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | Frame | T3C315M
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 |  |  | Starter | S/D
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | Make | Baldor Reliencer
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | Rated RPM | 1480
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | Bearing DE | 6316 C3
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | Rated Power | 75 KW
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | 6316 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | Frame | T3C315M
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 |  |  | Starter | S/D
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | Rated RPM | 1480
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | Bearing DE | NU319
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | Rated Power | 110 KW
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | 6319 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | Frame | Starter
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 |  |  | S/D
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | Make | Baldor Reliencer
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | Rated RPM | 1480
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | Bearing DE | 6316 C3
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | Rated Power | 75 KW
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | 6316 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | Frame | T3C280M-4
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | Make | Baldor Reliencer
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | Rated RPM | 1480
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | Bearing DE | 6316 C3
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | Rated Power | 75 KW
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | 6316 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | Frame | T3C280M-4
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | Make | CG
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | Rated RPM | 1475
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | Rated Power | 37 KW
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | 6213 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | Frame | ND225-S
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | Rated RPM | 1325
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | Rated Power | 7.5 KW
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | 6208 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | Frame | 132S
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | Rated RPM | 1450
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | Bearing DE | 6315 C3
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | Rated Power | 55 KW
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | 6313 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | Frame | 250MB4
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | Make | Baldor Reliencer
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | Rated RPM | 1478
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | Rated Power | 45 KW
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | 6313 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | Rated Current | 75.4A
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | Frame | T3C225M-4B5DX-1
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | Make | Baldor Reliencer
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | Rated RPM | 1478
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | Rated Power | 45 KW
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | 6313 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | Rated Current | 75.4A
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | Frame | T3C225M-4B5DX-1
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | Make | Baldor Reliencer
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | Rated RPM | 1478
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | Rated Power | 45 KW
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | 6313 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | Rated Current | 75.4A
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | Frame | T3C225M-4B5DX-1
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | Rated RPM | 1450
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | Rated Power | 7.5 KW
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | 6208 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | Rated Current | 14A
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | Frame | 132M
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | Rated RPM | 1450
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | Rated Power | 7.5 KW
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | 6208 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | Rated Current | 14A
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | Frame | 132M
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | Rated RPM | 1480
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | Bearing DE | 6309 ZZ
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | Rated Power | 7.5 KW
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | 6309 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | Rated Current | 19A
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | Frame | 160M
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | Make | CG
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | Rated RPM | 1485
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | Bearing DE | 6319 C3
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | Rated Power | 110 KW
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | 6319 C3 MJ20AB C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | Frame | PC 315-S
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | Make | CG
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | Rated RPM | 1485
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | Bearing DE | 6319 C3
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | Rated Power | 110 KW
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | 6319 C3 MJ20AB C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | Frame | PC 315-S
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | Make | NGEF
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | Rated RPM | 1485
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | Bearing DE | NU320
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | Rated Power | 110 KW
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | 6320 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | Frame | Starter
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 |  |  | VFD
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | Make | CG
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | Rated RPM | 1485
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | Bearing DE | 6319 C3
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | Rated Power | 110 KW
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | 6319 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | Frame | PC 315-S
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | Rated RPM | 1485
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | Bearing DE | 6313 ZZ C3
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | Rated Power | 37 KW
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | 6313 ZZ C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | Frame | 225-S
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | Make | CG
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | Rated RPM | 960
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | Bearing DE | 6314 C3
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | Rated Power | 37 KW
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | 6314 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | Frame | ND 225-S
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 |  |  | Starter | VFD
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | Rated RPM | 1470
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | Rated Power | 30 KW
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | 6312 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | Rated Current | 52A
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | Frame | Starter
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 |  |  | DOL
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | Make | KEC
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | Rated RPM | 1470
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | Rated Power | 30 KW
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | 6312 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | Rated Current | 52A
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | Frame | Starter
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 |  |  | DOL
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | Rated RPM | 1450
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | Bearing DE | 6315 C3
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | Rated Power | 55 KW
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | 6313 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | Frame | Starter
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 |  |  | VFD
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | Make | KEC
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | Rated RPM | 1450
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | Bearing DE | NU314 EM/C3
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | Rated Power | 55 KW
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | 6314 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | Frame | 315-S
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | Make | Baldor Reliencer
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | Rated RPM | 985
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | Bearing DE | NU319 EM/C3
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | Rated Power | 75 KW
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | 6319 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | Rated Current | 128A
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | Frame | T3C315S-6
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | Make | Baldor Reliencer
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | Rated RPM | 985
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | Bearing DE | NU319 EM/C3
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | Rated Power | 75 KW
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | 6319 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | Rated Current | 128A
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | Frame | T3C315S-6
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | Make | B.B
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | Rated RPM | 985
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | Bearing DE | NU319 EM/C3
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | Rated Power | 75 KW
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | 6319 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | Rated Current | 128A
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | Frame | 315-S
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | Make | B.B
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | Rated RPM | 985
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | Bearing DE | NU319 EM/C3
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | Rated Power | 75 KW
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | 6319 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | Rated Current | 128A
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | Frame | 315-S
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | Make | B.B
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | Rated RPM | 985
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | Bearing DE | NU319 EM/C3
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | Rated Power | 75 KW
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | 6319 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | Rated Current | 128A
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | Frame | 315-S
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | Make | B.B
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | Rated RPM | 985
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | Bearing DE | NU319 EM/C3
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | Rated Power | 75 KW
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | 6319 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | Rated Current | 128A
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | Frame | 315-S
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | Make | CG
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | Rated RPM | 985
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | Bearing DE | 6314 C3
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | Rated Power | 37 KW
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | 6314 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | Rated Current | 68A
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | Frame | ND250M
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | Rated RPM | 985
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | Rated Power | 30 KW
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | 6312 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | Rated Current | 55A
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | Frame | Starter
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 |  |  | DOL
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | Rated RPM | 985
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | Rated Power | 30 KW
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | 6312 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | Rated Current | 55A
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | Frame | Hx225-S MB-6
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | Make | ABB
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | Rated RPM | 985
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | Bearing DE | 6313 C3
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | Rated Power | 30 KW
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | 6312 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | Rated Current | 55A
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | Frame | Hx225-S MB-6
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | Make | Baldor Reliencer
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | Rated RPM | 1485
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | Bearing DE | 6316 C3
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | Rated Power | 75 KW
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | 6316 C3 | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | Frame | T3C280 M4
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | Make | CG
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | Rated RPM | 1410
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | Bearing DE | 6204 ZZ
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | Rated Power | 0.75 KW
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | 6204 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | Rated Current | 1.8A
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | Frame | ND80
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | Make | Primo
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | Rated RPM | 1410
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | Bearing DE | 6205 ZZ
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | Rated Power | 1.5 KW
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | 6205 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | Frame | BPM90L
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | Rated RPM | 1425
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | Bearing DE | 6204 ZZ
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | Rated Power | 0.75 KW
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | 6204 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | Rated Current | 1.3A
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | Frame | 80
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | Make | Baldor Reliencer
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | Rated RPM | 1470
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | Bearing DE | 6206 ZZ
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | Rated Power | 2.2 KW
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | 6206 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | Rated Current | 4.7A
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | Frame | 3TC 315-5-8
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | Rated RPM | 1470
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | Bearing DE | 6208 ZZ
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | Rated Power | 5.5 KW
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | Duty | S1
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | 6208 ZZ | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | Rated Current | 7.5A
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | Frame | 132S
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 |  |  | Starter | DOL
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 |  |  | Rated RPM | Bearing DE
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 |  |  | Rated Power
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 |  |  | Duty
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 |  |  | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 |  |  | Frame | Starter
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 |  |  | Rated RPM | Bearing DE
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 |  |  | Rated Power
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 |  |  | Duty
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 |  |  | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 |  |  | Frame | Starter
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 |  |  | Make | Siemens
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 |  |  | Rated RPM | Bearing DE
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 |  |  | Rotor Voltage
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 |  |  | Rated Power
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 |  |  | Duty
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 |  |  | Protection | Bearing NDE
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 |  |  | Rotor Current
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 |  |  | Frame | Starter
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  |  | Make | Voltas
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  |  | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  |  | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  |  | Capacity | 11 Ton
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  |  | Rated Current
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  |  | Type of A.C | Ductable
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  |  | Type of Gas | Discharge Pressure
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  |  | Suction Pressure
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  |  | Year of Manufacture
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -2 | Make | Voltas
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -2 | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -2 | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -2 | Capacity | 11 Ton
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -2 | Rated Current
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -2 | Type of A.C | Ductable
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -2 | Type of Gas | Discharge Pressure
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -2 | Suction Pressure
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -2 | Year of Manufacture
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -3 | Make | Voltas
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -3 | Rated Voltage | 415 V
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -3 | Machine Sr. No.
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -3 | Capacity | 5.5 Ton
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -3 | Rated Current
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -3 | Type of A.C | Ductable
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -3 | Type of Gas | Discharge Pressure
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -3 | Suction Pressure
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 |  | UNIT -3 | Year of Manufacture
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 |  |  | Make
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 |  |  | Rated Voltage | 230 V
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 |  |  | Machine Sr. No.
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 |  |  | Capacity | 2 Ton
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 |  |  | Rated Current
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 |  |  | Type of A.C | Type of Gas
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 |  |  | Discharge Pressure | Suction Pressure
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 |  |  | Year of Manufacture
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | Make | BABAR
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | Rated RPM | 550
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | Motor Type | Sq.cage
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | Rated Power | 9.3 KW
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | Protection
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | Carbon Brush
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | Frame | 180L
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | Rated Current | 21 Amp
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 |  |  | DOL
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | Make | BABAR
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | Rated RPM | 550
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | Motor Type | Sq.cage
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | Rated Power | 9.3 KW
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | Protection
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | Carbon Brush
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | Frame | 180L
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | Rated Current | 21 Amp
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 |  |  | DOL
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | Make | ABB
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | Rated RPM | 1440
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | 6310 C3 | Motor Type
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | Sq.cage
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | Rated Power | 30 KW
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | Protection
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | 6310 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | Frame
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | Rated Current | 56 Amp
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 |  |  | S/D
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | Make | ABB
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | Rated RPM | 1440
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | 6312 C3 | Motor Type
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | Sq.cage
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | Rated Power | 30 KW
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | Protection
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | 6311 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | Frame
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | Rated Current | 54 Amp
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 |  |  | S/D
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | Make | Kirloskar
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | Rated RPM | 1440
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | 6313 C3 | Motor Type
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | Sq.cage
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | Rated Power | 37 KW
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | Protection
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | 6310 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | Frame | 200L
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | Rated Current | 68 Amp
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 |  |  | S/D
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | Make | Kirloskar
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | Rated RPM | 1440
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | 6315 C3 | Motor Type
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | Sq.cage
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | Rated Power | 55 KW
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | Protection
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | 6313 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | Frame | ND 250 M
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | Rated Current | 94 Amp
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 |  |  | S/D
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | Make | Siemens
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | Rated RPM | 1440
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | 6313 C3 | Motor Type
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | Sq.cage
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | Rated Power | 37 KW
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | Protection
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | 6313 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | Frame | 225S
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | Rated Current | 64 Amp
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 |  |  | DOL
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | Make | Kirloskar
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | Rated RPM | 1440
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | 6204 ZZ | Motor Type
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | Sq.cage
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | Rated Power | 0.75 KW
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | Protection
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | 6204 ZZ | Carbon Brush
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | Frame
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | Rated Current | 1.3 Amp
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 |  |  | DOL
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | Make | Kirloskar
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | Rated RPM | 1440
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | 6204 ZZ | Motor Type
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | Sq.cage
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | Rated Power | 0.75 KW
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | Protection
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | 6204 ZZ | Carbon Brush
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | Frame
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | Rated Current | 1.3 Amp
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 |  |  | DOL
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | Make | ABB
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | Rated RPM | 1440
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | 6312 C3 | Motor Type
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | Sq.cage
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | Rated Power | 22 KW
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | Protection
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | 6311 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | Frame
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | Rated Current | 42 Amp
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 |  |  | DOL
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | Make | ABB
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | Rated RPM | 1440
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | 6312 C3 | Motor Type
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | Sq.cage
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | Rated Power | 22 KW
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | Protection
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | 6311 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | Frame
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | Rated Current | 42 Amp
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 |  |  | DOL
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | Make | Siemens
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | Rated RPM | 1440
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | 6313 C3 | Motor Type
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | Sq.cage
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | Rated Power | 37 KW
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | Protection
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | 6313 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | Frame
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | Rated Current | 64 Amp
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 |  |  | DOL
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | Make | Kirloskar
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | Rated RPM | 2900
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | 6313 C3 | Motor Type
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | Slipring induction motor
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | Rated Power | 45 KW
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | Protection
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | 6313 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | Frame
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | Rated Current | 76 Amp
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 |  |  | DOL
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 |  |  | PCC Panel -1 | MCC-Panel-1
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 |  |  | Soot Blower Panel
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 |  |  | PCC Panel -2 | MCC-Panel-2
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 |  |  | VFD Panel
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | Make | Kirloskar
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | Rated RPM | 2900
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | 6310 C3 | Motor Type
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | Suirrel cage induction motor
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | Rated Power | 22 KW
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | Protection
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | 6309 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | Frame | L0180M MK11
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | Rated Current | 38 Amp
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 |  |  | DOL
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | Make | Siemens
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | Rated RPM | 1475
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | 6213 C3 | Motor Type
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | Suirrel cage induction motor
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | Rated Power | 45 KW
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | Protection
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | 6213 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | Frame | 250 M
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | Rated Current | 78 Amp
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 |  |  | DOL
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | Make | Siemens
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | Rated RPM | 1475
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | 6215 C3 | Motor Type
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | Suirrel cage induction motor
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | Rated Power | 55 KW
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | Protection
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | 6215 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | Frame | 250 M
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | Rated Current | Amp
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 |  |  | DOL
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | Make | Siemens
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | Rated RPM | 1485
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | 6317 C3 | Motor Type
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | Suirrel cage induction motor
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | Rated Power | 90 KW
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | Protection
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | 6317 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | Frame | 280 M
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | Rated Current | 151 Amp
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 |  |  | DOL
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | Make | Kirloskar
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | Rated RPM | 989
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | NU322 | Motor Type
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | Slipring induction motor
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | Rated Power | 132 KW
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | Protection
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | 6322 C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | 22 X32 X45 MM
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | Frame
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | Rated Current | 229 Amp
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 |  |  | DOL
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | Make
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | Rated RPM | 960
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | 6308 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | Rated Power | 3.7 KW
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | Protection
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | 6307 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | Frame
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | Rated Current | 7.5 Amp
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 |  |  | DOL
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | Make
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | Rated RPM | 960
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | 6308 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | Rated Power | 3.7 KW
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | Protection
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | 6208 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | Frame
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | Rated Current | 7.5 Amp
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 |  |  | DOL
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | Make
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | Rated RPM | 1440
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | 6308 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | Rated Power | 3.7 KW
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | Protection
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | 6307 C ZZ | Carbon Brush
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | Frame
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | Rated Current | 7.5 Amp
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 |  |  | DOL
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | Make | Siemens
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | Rated RPM | 2925
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | 6309 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | Rated Power | 15 KW
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | Protection
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | 6309 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | Frame | 160M
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | Rated Current | 26 Amp
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 |  |  | DOL
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | Make | ABB
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | Rated RPM | 1450
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | 6309 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | Rated Power | 15 KW
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | Protection
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | 6308 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | Frame | 160ML
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | Rated Current | 29 Amp
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 |  |  | DOL
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | Make | BBL
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | Rated RPM | 1450
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | 6309 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | Rated Power | 15 KW
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | Protection
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | 6209 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | Frame | 160L
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | Rated Current | 27.6 Amp
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 |  |  | DOL
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | Make | BBL
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | Rated RPM | 1450
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | 6309 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | Rated Power | 15 KW
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | Protection
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | 6209 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | Frame | 160L
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | Rated Current | 27.6 Amp
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 |  |  | DOL
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | Make | ABB
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | Rated RPM | 1450
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | 6309 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | Rated Power | 15 KW
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | Protection
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | 6308 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | Frame | 160ML
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | Rated Current | 29 Amp
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 |  |  | DOL
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | Make | BBL
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | Rated RPM | 1450
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | 6309 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | Rated Power | 15 KW
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | Protection
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | 6209 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | Frame | 160L
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | Rated Current | 27.6 Amp
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 |  |  | DOL
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | Make | BBL
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | Rated RPM | 1425
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | 6309 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | Rated Power | 15 KW
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | Protection
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | 6209 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | Frame | 160ML
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | Rated Current | 27.6 Amp
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 |  |  | DOL
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | Make
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | Rated RPM | 1425
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | 6204 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | Rated Power | 0.75 KW
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | Protection
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | 6204 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | Frame
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | Rated Current | Ins. CL
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 |  |  | Starter | DOL
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | Make
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | Rated RPM | 1425
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | 6204 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | Rated Power | 0.75 KW
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | Protection
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | 6204 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | Frame
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | Rated Current | Ins. CL
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 |  |  | Starter | DOL
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | Make
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | Rated RPM | 715
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | 6303 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | Rated Power | 0.75 KW
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | Protection
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | 6203 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | Frame
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | Rated Current | Ins. CL
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 |  |  | Starter | DOL
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | Make
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | Rated RPM | 715
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | 6303 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | Rated Power | 0.75 KW
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | Protection
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | 6203 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | Frame
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | Rated Current | Ins. CL
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 |  |  | Starter | DOL
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | Make
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | Rated RPM | 715
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | 6303 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | Rated Power | 0.75 KW
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | Protection
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | 6203 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | Frame
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | Rated Current | Ins. CL
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 |  |  | Starter | DOL
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | Make
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | Rated RPM | 715
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | 6303 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | Rated Power | 0.75 KW
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | Protection
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | 6203 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | Frame
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | Rated Current | Ins. CL
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 |  |  | Starter | DOL
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | Make
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | Rated RPM | 715
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | 6303 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | Rated Power | 0.75 KW
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | Protection
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | 6203 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | Frame
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | Rated Current | Ins. CL
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 |  |  | Starter | DOL
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | Make
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | Rated RPM | 715
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | 6303 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | Rated Power | 0.75 KW
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | Protection
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | 6203 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | Frame
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | Rated Current | Ins. CL
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 |  |  | Starter | DOL
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | Make
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | Rated RPM | 715
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | 6303 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | Rated Power | 0.75 KW
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | Protection
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | 6203 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | Frame
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | Rated Current | Ins. CL
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 |  |  | Starter | DOL
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | Make | ABB
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | Rated RPM | 715
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | 6309 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | Rated Power | 3.7 KW
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | Protection
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | 6308 ZZ C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | Frame | 160ML
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | Rated Current | 8.4 Amp
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 |  |  | DOL
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | Make | ABB
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | Rated RPM | 2925
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | 6310C3 | Motor Type
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | Rated Power | 22 KW
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | Protection
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | 6310C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | Frame | 180L
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | Rated Current | 37 Amp
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 |  |  | S/D
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | Make | Alostom
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | Rated RPM | 2900
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | 6310C3 | Motor Type
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | Rated Power | 22 KW
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | Protection
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | 6310C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | Frame | 180L
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | Rated Current | 37 Amp
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 |  |  | S/D
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | Make | KE
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | Rated RPM | 2978
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | NU-316C3 | Motor Type
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | Rated Power | 132 KW
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | Protection
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | 6316C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | Frame | LD315MMK13
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | Rated Current | 220 Amp
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 |  |  | S/D
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | Make | KE
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | Rated RPM | 2978
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | NU-316C3 | Motor Type
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | Rated Power | 132 KW
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | Protection
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | 6316C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | Frame | LD315MMK12
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | Rated Current | 220 Amp
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 |  |  | S/D
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | Make | KE
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | Rated RPM | 2978
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | NU-316C3 | Motor Type
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | Rated Power | 132 KW
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | Protection
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | 6316C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | Frame | LD315MMK11
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | Rated Current | 220 Amp
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 |  |  | S/D
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | Make | KE
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | Rated RPM | 1450
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | 6319 C3 | Motor Type
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | Slipring induction motor
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | Rated Power | 110 KW
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | Protection
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | 6316C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | Frame
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | Rated Current | 210 Amp
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 |  |  | DOL with Resistance
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | Make | Kirloskar
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | Rated RPM | 741
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | NU-324 | Motor Type
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | Slipring induction motor
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | Rated Power | 185 KW
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | Protection
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | 6321C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | 22 X32 X45 MM
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | Frame | KDW400
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | Rated Current | 342 Amp
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 |  |  | DOL with Resistance
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | Make | Kirloskar
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | Rated RPM | 741
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | NU-324 | Motor Type
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | Slipring induction motor
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | Rated Power | 185 KW
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | Protection
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | 6321C3 | Carbon Brush
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | 22 X32 X45 MM
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | Frame | KDW400
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | Rated Current | 342 Amp
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | Ins. CL | Starter
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  |  | DOL with Resistance
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 |  | STARTER | Starter | DOL ,Resistance
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | Make | ABB
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | Rated RPM | 960
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | 6308C3 | Motor Type
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | Rated Power | 3.7 KW
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | Protection
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | 6307ZZ
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | Frame
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | Rated Current | 8.3 Amp
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | Ins. CL | VFD
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 |  |  | ACS550-01-031A-4
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | Make | ABB
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | Rated RPM | 960
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | 6308C3 | Motor Type
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | Rated Power | 3.7 KW
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | Protection
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | 6307ZZ | VFD
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | ACS550-01-031A-4
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | Frame
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | Rated Current | 8.3 Amp
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 |  |  | Ins. CL
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | Make | ABB
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | Rated RPM | 1440
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | Machine Sr. No. | Bearing DE
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | 6308 ZZ C3 | Motor Type
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | Squirrel cage induction motor
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | Rated Power | 3.7 KW
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | Protection
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | Year of Manufacture | Bearing NDE
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | 6307 ZZ C3 | VFD
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | ACS550-01-031A-4
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | Rated Voltage | 415 V
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | Frame
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | Rated Current | 8.3 Amp
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 |  |  | Ins. CL
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Make | BHEL
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Machine Sr. No. | 44221A261-11-03
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Protection | IP 54
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Winding Insulation Class | F - Class
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | P.F | 0.8 Lag
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Rated Power | 3750 KVA / 3000 KW
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Year of Manufacture | 1996
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Frame | G 54904
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Duty | Continuous
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Weight | 16000 Kg.
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Rated Voltage | 420V
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Rated Current | 5155
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Connection | Star
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Specification | IS 4722
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Excitation Voltage | 95V
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Rated RPM | 1500
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | Bearings | Ambient Temp.
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | 45°C | Inlet Temp.
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | 50°C | Excitation Current
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  |  | 385A
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Make | BHEL
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Voltage | 108 V
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Rated RPM | 1500
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Specification | IS4722
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Field Resistance | 25.6, Ohm
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Rated Power | 45.9 KW
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Current | 425A
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Connection | Star
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Manufacturing Year | 1996
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Excitation Voltage | 160V
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Hz | 150
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Excitation Current | 4.5A
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | BRUSHLESS EXCITER | Sr. No. | 44221A261-11-03
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | AVR PANEL | Generator
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | AVR PANEL | Rating | 3000 KW
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | AVR PANEL | Excitation
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | AVR PANEL | Voltage | 110V
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | AVR PANEL | Make | Sanelec
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | AVR PANEL | Voltage | 415 V
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | AVR PANEL | Current | 3.7A
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | AVR PANEL | SN. | ECP No. 150705
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | AVR PANEL | Frequency | 50 Hz
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 |  | AVR PANEL | Phase | 3
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Make | BHEL
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Machine Sr. No. | 44221A261-11-03
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Protection | IP 54
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Winding Insulation Class | F - Class
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | P.F | 0.8 Lag
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Rated Power | 3750 KVA / 3000 KW
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Year of Manufacture | 1996
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Frame | G 54904
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Duty | Continuous
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Weight | 16000 Kg.
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Rated Voltage | 420V
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Rated Current | 5155
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Connection | Star
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Specification | IS 4722
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Excitation Voltage | 95V
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Rated RPM | 1500
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | Bearings | Ambient Temp.
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | 45°C | Inlet Temp.
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | 50°C | Excitation Current
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  |  | 385A
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Make | BHEL
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Voltage | 108 V
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Rated RPM | 1500
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Specification | IS4722
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Field Resistance | 25.6, Ohm
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Rated Power | 45.9 KW
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Current | 425A
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Connection | Star
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Manufacturing Year | 1996
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Excitation Voltage | 160V
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Hz | 150
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Excitation Current | 4.5A
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | BRUSHLESS EXCITER | Sr. No. | 44221A261-11-03
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | AVR PANEL | Generator
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | AVR PANEL | Rating | 3000 KW
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | AVR PANEL | Excitation
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | AVR PANEL | Voltage | 40V
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | AVR PANEL | Make | Sanelec
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | AVR PANEL | Voltage | 415 V
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | AVR PANEL | Current | 5.2A
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | AVR PANEL | SN. | ECP No. 230804
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | AVR PANEL | Frequency | 50 Hz
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 |  | AVR PANEL | Phase | 3
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-1, D.S House | SACE E4.2S, 4000A
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-5,Main I/C New T.G-1, 52A | SACE E4.2S, 4000A
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-8 Bus coupler | SACE E6H 50, 5000A
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-12, 70 TPH PCC-1 | FA2C-1600
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-17, Cane Yard & Capacitor Panel | CN-CS 1000C
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-2, Capacitor panel-1 | SACE E3N 32, 3200A
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-5,Main I/C New T.G-1, 52B | SACE E4.2S, 4000A
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-9 Power plant L.T | CN-CS 2500C
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-13, 70 TPH PCC-2 | FA2C-1600
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-18 Mill House L.T PCC | CN-CS 1000C
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-3 Mill House L.T PCC | SACE E2N 20, 2000A
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-6,Raw house PCC | SACE E3N 32, 3200A
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-10 Raw House VFD Panel | CN-CS 2000C
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-14 Power House Lighting | CN-CS 1000C
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-19 Colony | CN-CS 1000C
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-4 D.S House Injection | SACE E1N 10, 1000A
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-7 D.S House Injection | SACE E1N 16, 1600A
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-11 D.S House PCC-2 | CN-CS 4000C
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-16 D.S House ETP | CN-CS 1000C
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-20,Main I/C OLD, T.G, 52A | SACE E4.2H, 4000A
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-20,Main I/C OLD, T.G, 52B | SACE E4.2H, 4000A
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-21 Grid Tie | SACE E6H 50, 5000A
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 |  |  | Feeder-21 Grid Tie NIS | SACE E1N 10, 1000A
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Rated Power ONAN | 2500 KVA
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Rated Current ONAN H.V | 131.22A
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Volume of oil | 2900 Ltrs.
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Sr No. | 1713/1
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | HV WTI CT as per IS: 2705 | Ratio 166/1.6A, 15VA, CL-1
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Rated Power ONAF | 3150 KVA
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Rated Current ONAF H.V | 165.33A
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Year of Manufacture | 2014
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Connection | Dyn11
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | LV WTI CT as per IS: 2705 | Ratio 4383/1.6A, 15VA, CL-1
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Rated Voltage H.V | 11000V
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Rated Current ONAN L.V | 3478.01A
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Mass of oil | 2540 Kg.
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Make | Delta
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | LV NCT as per IS: 2705
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Ratio 5000/1A,CL- PS,Vk>700, RCT<20 ohms, @75°C, Imag<30mA@50%VK.
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Rated Voltage L.V | 415V
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Rated Current ONAF L.V | 4382.3A
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 |  |  | Cooling Type | ONAN
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 |  |  | Capcitor Panel -1 | 900 KVAR
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 |  |  | Capcitor Panel -1 | 375 KVAR
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  |  | Make
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  |  | Rated Voltage | 230 V
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  |  | Machine Sr. No.
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  |  | Capacity | 2 Ton
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  |  | Rated Current
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  |  | Type of A.C | Type of Gas
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  |  | Discharge Pressure | Suction Pressure
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  |  | Year of Manufacture
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Make
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Rated Voltage | 230 V
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Machine Sr. No.
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Capacity | 2 Ton
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Rated Current
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Type of A.C | Type of Gas
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Discharge Pressure | Suction Pressure
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Year of Manufacture
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Make
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Rated Voltage | 230 V
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Machine Sr. No.
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Capacity | 2 Ton
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Rated Current
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Type of A.C | Type of Gas
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Discharge Pressure | Suction Pressure
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 |  | UNIT-2 | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 |  |  | Make | ABB- AC SQ. CAGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 |  |  | Machine Sr. No. | 3G2J15430090060963
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 |  |  | Rated Power | 250 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 |  |  | Rated Current | 440 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 |  |  | Protection | IP55
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 |  |  | RPM | 740
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 |  |  | Frame No. | 355M
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 |  |  | Bearings | DE-6322C3,NDE-6319/C3VL0241
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Make | INTEGRATED ELECTRIC COMPANY-DC MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Machine Sr. No. | NOT CLEARED
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Rated Power | 145 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Year of Manufacture | 2007
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Rated Voltage Armature | 400 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Rated Current Armature | 418 Amp
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Rated Voltage Field | 220
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Rated Current Field | 17.6 - 3.7
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Winding | Shunt
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | RPM | 400 -1100
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Brush Size | 32x16
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Frame No. | IEFC-315L
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 |  |  | Bearings | DE-NU-222 C3 , NDE-6322 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 |  |  | Make | ABB- AC SQ. CAGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 |  |  | Machine Sr. No. | 3G2J25180090132786
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 |  |  | Rated Power | 250 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 |  |  | Rated Current | 454 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 |  |  | Protection | IP55
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 |  |  | RPM | 740
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 |  |  | Frame No. | 355M
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 |  |  | Bearings | DE-6322C3,NDE-6319/C3VL0241
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 |  |  | Make | SIEMENSE- 3-PH VERTICAL FLANGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 |  |  | Rated Power | 90 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 |  |  | Rated Current | 156 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 |  |  | Frame No. | 280 M
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 |  |  | Bearings | DE- NU317 , NDE-6317 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 |  |  | Make | SIEMENSE- 3-PH VERTICAL FLANGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 |  |  | Rated Power | 90 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 |  |  | Rated Current | 156 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 |  |  | Frame No. | 280 M
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 |  |  | Bearings | DE- NU317 , NDE-6317 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 |  |  | Make | SIEMENSE- 3-PH VERTICAL FLANGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 |  |  | Rated Power | 90 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 |  |  | Rated Current | 156 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 |  |  | Frame No. | 280 M
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 |  |  | Bearings | DE- NU317 , NDE-6317 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 |  |  | Make | SIEMENSE- 3-PH VERTICAL FLANGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 |  |  | Rated Power | 90 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 |  |  | Rated Current | 156 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 |  |  | Frame No. | 280 M
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 |  |  | Bearings | DE-NU316 , NDE-6316 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 |  |  | Make | KIRLOSKAR-3-PH SLIP RING MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 |  |  | Rated Power | 250 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 |  |  | Rated Current | 430 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 |  |  | RPM | 970
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 |  |  | Bearings | DE-6322C3,NDE-7320 B
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 |  |  | Make | ALSTOM-3-PH SLIP RING MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 |  |  | Rated Power | 250 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 |  |  | Rated Current | 430 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 |  |  | RPM | 970
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 |  |  | Bearings | DE-NU324 , NDE-QJ320N2
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 |  |  | Make | KIRLOSKAR-3-PH SLIP RING MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 |  |  | Rated Power | 110 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 |  |  | Rated Current | 190 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 |  |  | RPM | 970
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 |  |  | Bearings | DE- NU-321-E-XL , NDE- 6315 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 |  |  | Make | ALSTOM-3-PH SLIP RING MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 |  |  | Rated Power | 250 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 |  |  | Rated Current | 430 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 |  |  | RPM | 970
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 |  |  | Bearings | DE-NU324 E-M1,NDE-QJ320N2M
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 |  |  | Make | 3-PH VERTICAL FLANGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 |  |  | Rated Power | 55 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 |  |  | Rated Current | 95 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 |  |  | Bearings | DE-NU315 , NDE-6313 ZZC3
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 |  |  | Make | 3-PH VERTICAL FLANGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 |  |  | Rated Power | 55 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 |  |  | Rated Current | 95 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 |  |  | Bearings | DE-NU315 , NDE-6313 ZZC3
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 |  |  | Make | 3-PH VERTICAL FLANGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 |  |  | Rated Power | 55 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 |  |  | Rated Current | 95 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 |  |  | Bearings | DE-6315 C3 , NDE-6313 ZZC3
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 |  |  | Make | 3-PH VERTICAL FLANGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 |  |  | Rated Power | 55 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 |  |  | Rated Current | 95 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 |  |  | Bearings | DE-6215 C3 , NDE-6215 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 |  |  | Make | 3-PH VERTICAL FLANGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 |  |  | Rated Power | 55 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 |  |  | Rated Current | 95 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 |  |  | Bearings | DE-NU315, NDE-6313 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 |  |  | Make | 3-PH VERTICAL FLANGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 |  |  | Rated Power | 55 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 |  |  | Rated Current | 95 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 |  |  | Bearings | DE-NU315, NDE-6313 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 |  |  | Make | 3-PH VERTICAL FLANGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 |  |  | Rated Power | 55 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 |  |  | Rated Current | 95 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 |  |  | Bearings | DE-NU314, NDE-6314 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 |  |  | Make | 3-PH VERTICAL FLANGE MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 |  |  | Rated Power | 55 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 |  |  | Rated Current | 95 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 |  |  | Bearings | DE-NU315, NDE-6313 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 |  |  | Rated Power | 110 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 |  |  | Rated Current | 190 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 |  |  | Protection | IP55
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 |  |  | Bearings | DE-6318 C3, NDE-6314 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 |  |  | Rated Power | 110 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 |  |  | Rated Current | 190 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 |  |  | Protection | IP55
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 |  |  | Bearings | DE-NU318,NDE-6314 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 |  |  | Rated Power | 90 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 |  |  | Rated Current | 156 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 |  |  | Bearings | DE-6316 C3, NDE-6315 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 |  |  | Rated Power | 90 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 |  |  | Rated Current | 156 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 |  |  | RPM | 1470
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 |  |  | Bearings | DE-6316 C3, NDE-6315 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 |  |  | Rated Power | 75 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 |  |  | Rated Current | 129 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 |  |  | RPM | 1440
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 |  |  | Bearings | DE-NU316 , NDE-6315 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 |  |  | Rated Power | 75 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 |  |  | Rated Current | 129 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 |  |  | RPM | 1440
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 |  |  | Bearings | DE-NU315 , NDE-6313 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR(ABB)
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 |  |  | Rated Power | 55 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 |  |  | Rated Current | 95 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 |  |  | Protection | IP55
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 |  |  | Frame No. | 250MB4
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 |  |  | Bearings | DE-6315 C3,NDE-6313 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR(ABB)
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 |  |  | Rated Power | 55 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 |  |  | Rated Current | 95 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 |  |  | Protection | IP55
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 |  |  | Frame No. | 250MB4
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 |  |  | Bearings | DE-6315 C3,NDE-6313 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 |  |  | Rated Power | 90 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 |  |  | Rated Current | 156 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 |  |  | Bearings | DE-6316 C3,NDE-6315 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 |  |  | Rated Power | 90 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 |  |  | Rated Current | 156 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 |  |  | Bearings | DE-NU318,NDE-6318 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 |  |  | Rated Power | 30 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 |  |  | Rated Current | 54 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 |  |  | Bearings | DE-6312 C3,NDE-6310 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 |  |  | Rated Power | 30 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 |  |  | Rated Current | 54 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 |  |  | Bearings | DE-6312 C3,NDE-6310 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 |  |  | Rated Power | 37 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 |  |  | Rated Current | 67 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 |  |  | Bearings | DE-6313 C3,NDE-6313 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 |  |  | Rated Power | 37 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 |  |  | Rated Current | 67 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 |  |  | Bearings | DE-6313 C3,NDE-6313 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 |  |  | Rated Power | 37 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 |  |  | Rated Current | 67 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 |  |  | Bearings | DE-6313 C3,NDE-6313 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 |  |  | Rated Power | 37 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 |  |  | Rated Current | 67 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 |  |  | Bearings | DE-6313 C3,NDE-6312 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR(ABB)
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 |  |  | Rated Power | 37 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 |  |  | Rated Current | 67 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 |  |  | Bearings | DE-6313 C3,NDE-6312 C3
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR(ABB)
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 |  |  | Rated Power | 37 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 |  |  | Rated Current | 67 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 |  |  | Bearings | DE-6313 ZC3,NDE-6312 ZC3
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 |  |  | Make | 3-PH SQ.CAGE INDUCTION MOTOR(ABB)
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 |  |  | Machine Sr. No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 |  |  | Rated Power | 37 KW
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 |  |  | Year of Manufacture
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 |  |  | Rated Voltage | 415 ±10% KV
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 |  |  | Rated Current | 67 Amp.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 |  |  | Protection | NA
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 |  |  | Winding Insulation Class | F - Class
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 |  |  | RPM | 1475
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 |  |  | Duty | S1
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 |  |  | Frame No.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 |  |  | Bearings | DE-6313 ZC3,NDE-6312 ZC3
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' |  |  | Make | ABB
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' |  |  | VFD Sr. No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' |  |  | VFD Rating | 12A
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' |  |  | Year of Manufacture
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' |  |  | Rated Voltage | 415 ±10%V
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' |  |  | Model | ACS550-01-12A-4
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' |  |  | Feeder No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' |  |  | VFD Feeder Name | OC filter 14'x36' VFD PANEL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' |  |  | Make | ABB
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' |  |  | VFD Sr. No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' |  |  | VFD Rating | 15A
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' |  |  | Year of Manufacture
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' |  |  | Rated Voltage | 415 ±10%V
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' |  |  | Model | ACS550-01-15A-4
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' |  |  | Feeder No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' |  |  | VFD Feeder Name | OC filter 14'x30' VFD PANEL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 |  |  | Make | ABB
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 |  |  | VFD Sr. No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 |  |  | VFD Rating | 87A
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 |  |  | Year of Manufacture
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 |  |  | Rated Voltage | 415 ±10%V
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 |  |  | Model | ACS880-01-087A-3+0J400+P944
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 |  |  | Feeder No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 |  |  | VFD Feeder Name | Distillery Syrup weightment Pump no.1 VFD
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 |  |  | Make | ABB
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 |  |  | VFD Sr. No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 |  |  | VFD Rating | 87A
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 |  |  | Year of Manufacture
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 |  |  | Rated Voltage | 415 ±10%V
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 |  |  | Model | ACS880-01-087A-3+0J400+P944
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 |  |  | Feeder No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 |  |  | VFD Feeder Name | Distillery Syrup weightment Pump no.2 VFD
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) |  |  | Make | ABB
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) |  |  | VFD Sr. No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) |  |  | VFD Rating | 6A
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) |  |  | Year of Manufacture
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) |  |  | Rated Voltage | 415 ±10%V
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) |  |  | Model | ACS550-01-06A9-4
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) |  |  | Feeder No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) |  |  | VFD Feeder Name | Molten Sulphur Dosing pump(E) VFD PANEL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) |  |  | Make | ABB
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) |  |  | VFD Sr. No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) |  |  | VFD Rating | 6A
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) |  |  | Year of Manufacture
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) |  |  | Rated Voltage | 415 ±10%V
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) |  |  | Model | ACS550-01-06A9-4
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) |  |  | Feeder No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) |  |  | VFD Feeder Name | Molten Sulphur Dosing pump(W) VFD PANEL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER |  |  | Make | ABB
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER |  |  | VFD Sr. No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER |  |  | VFD Rating | 59A
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER |  |  | Year of Manufacture
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER |  |  | Rated Voltage | 415 ±10%V
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER |  |  | Model | ACS550-01-059A-4
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER |  |  | Feeder No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER |  |  | VFD Feeder Name | AIR BLOWER NO.3 VFD PANEL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 |  |  | Make | ABB
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 |  |  | VFD Sr. No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 |  |  | VFD Rating | 430A
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 |  |  | Year of Manufacture
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 |  |  | Rated Voltage | 415 ±10%V
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 |  |  | Model | ACS580-01-430A-4
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 |  |  | Feeder No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 |  |  | VFD Feeder Name | CLEAR JUICE PUMP-1 VFD PANEL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 |  |  | Make | ABB
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 |  |  | VFD Sr. No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 |  |  | VFD Rating | 505A
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 |  |  | Year of Manufacture
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 |  |  | Rated Voltage | 415 ±10%V
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 |  |  | Model | ACS580-04-505A-4+E208+E210+J400+J410
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 |  |  | Feeder No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 |  |  | VFD Feeder Name | INJECTION PUMP NO.5 VFD PANEL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | Make | ABB
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | VFD Panel Code
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | VFD Rating | 470A
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | Year of Manufacture
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | Rated Voltage | 415 ±10%V
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | Module-1 choke unit
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | Code No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | Module-2 Line Converter unit | ACS880-104-0470A-3+C188+E205
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | Code No. / SN.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | Module-3 Inverter unit | ACS880-104-0640A-3+E205+P904+V112
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | Code No. / SN.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | Feeder No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 |  |  | VFD Feeder Name | DS 1750 WIL AC VFD PANEL-1
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 |  |  | Make | ABB
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 |  |  | VFD Sr. No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 |  |  | VFD Rating | 400A
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 |  |  | Year of Manufacture
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 |  |  | Rated Voltage | 415 ±10%V
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 |  |  | Model | DCS800
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 |  |  | Feeder No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 |  |  | VFD Feeder Name | DS 1750 NHEC(DC) VFD PANEL-2
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | Make | ABB
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | VFD Panel Code
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | VFD Rating | 470A
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | Year of Manufacture
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | Rated Voltage | 415 ±10%V
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | Module-1 choke unit | BLCL-13-5+C183+C188+V112+V991
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | Code No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | Module-2 Line Converter unit | ACS880-104-0470A-3+E205+V112
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | Code No. / SN.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | Module-3 Inverter unit | ACS880-104-0470A-3+E205+V112
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | Code No. / SN.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | Feeder No.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 |  |  | VFD Feeder Name | DS 1750 WIL AC VFD PANEL-3

## MAINTENANCE SCHEDULE
source file | sheet id | sheet name | EQUIPMENT TAG NO | Sr.No. | Name of Equipment | Maintenance / Inspection Activities | Daily | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years | 4 - Years | Remarks
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | 1 | Stator | 1) Clean & Check of winding , Supports & Bandages. 2) Checking of Busbar terminal & Joints. 3) Cleaning of Stator winding and Connection. 4) Measure IR of Stator winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | 2 | Rotor | 1) Measure IR of Field winding. 2) Check whether all fastening elements are tight. 3) Visual Inspection of Rotor. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | 3 | Generator Bearing | 1) Check Quality of bearing oil. 2) Extended visual inspection of end shields. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | 4 | Brushless Exciter | 1) Measure IR of Rotor winding. 2) Measure IR of Stator winding. 3) Functional Test of Diode. 4) Check whether all fastening elements are tight. 5) Visual Inspection of Exciter. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | 5 | Oil System | Visual inspection on all oil - conveying pipes | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | 6 | Cooling System | 1)Visual inspection of Air - Water Cooler. 2)Hydraulic Test of Air - Water Cooler. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | 8 | Monitoring Instruments | 1) Inspection of Monitoring Instrument. 2) Check slip ring brushes for the ground fault detection |  | Yes
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 | 1 | Stator | 1) Clean & Check of winding , Supports & Bandages. 2) Checking of Busbar terminal & Joints. 3) Cleaning of Stator winding and Connection. 4) Measure IR of Stator winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 | 2 | Rotor | 1) Measure IR of Field winding. 2) Check whether all fastening elements are tight. 3) Visual Inspection of Rotor. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 | 3 | Motor Bearing | 1) Check Quality of bearing oil. 2) Extended visual inspection of end shields. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 | 6 | Cooling System | 1) Visual inspection of Air - Water Cooler. 2) Hydraulic Test of Air - Water Cooler. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 | 8 | Monitoring Instruments | 1) Inspection of Monitoring Instrument. 2) Check slip ring brushes for the ground fault detection. |  | Yes
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | 1 | Stator | Checking of Busbar terminal & Joints.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | 1 | Stator | Checking of Busbar terminal & Joints.
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | 1 | Panel | Clean & Check of busbar, Supports & Bandages | [5 empty] | Yes | Yes
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | 1 | Panel | Checking of Busbar terminal & Joints.
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | 1 | Panel | Cleaning of Panel
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | 2 | Breaker | Checking of Fix & moving contact. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | 2 | Breaker | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | 2 | Breaker | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | 3 | Oil status | Check Quality of oil. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | 3 | Oil status | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | 6 | Cooling System | External Fan | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | 1 | Panel | Clean & Check of busbar, Supports & Bandages | [5 empty] | Yes | Yes
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | 1 | Panel | Checking of Busbar terminal & Joints.
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | 1 | Panel | Cleaning of Panel
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | 2 | Breaker | Checking of Fix & moving contact. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | 2 | Breaker | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | 2 | Breaker | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | 3 | Oil status | Check Quality of oil. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | 3 | Oil status | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | 6 | Cooling System | External Fan | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | 1 | Panel | Clean & Check of busbar, Supports & Bandages | [5 empty] | Yes | Yes
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | 1 | Panel | Checking of Busbar terminal & Joints.
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | 1 | Panel | Cleaning of Panel
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | 2 | Breaker | Checking of Fix & moving contact. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | 2 | Breaker | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | 2 | Breaker | Visual Inspection of Contactors.
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | 3 | Terminal | Checking & Tightening. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | 3 | Terminal | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | 6 | Cooling System | Internal Fan | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | 1 | Panel | Clean & Check of busbar, Supports & Bandages | [5 empty] | Yes | Yes
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | 1 | Panel | Checking of Busbar terminal & Joints.
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | 1 | Panel | Cleaning of Panel
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | 2 | Breaker | Checking of Fix & moving contact. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | 2 | Breaker | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | 2 | Breaker | Visual Inspection of Contactors.
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | 3 | Terminal | Checking & Tightening. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | 3 | Terminal | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | 6 | Cooling System | Internal Fan | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | 1 | Panel | Clean & Check of busbar, Supports & Bandages | [5 empty] | Yes | Yes
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | 1 | Panel | Checking of Busbar terminal & Joints.
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | 1 | Panel | Cleaning of Panel
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | 2 | Breaker | Checking of Fix & moving contact. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | 2 | Breaker | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | 2 | Breaker | Visual Inspection of Contactors.
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | 3 | Terminal | Checking & Tightening. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | 3 | Terminal | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | 6 | Cooling System | Internal Fan | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 1 | Stator | Checking of motor terminal.
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 1 | Stator | Cleaning of Stator winding and Connection
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 1 | Stator | Measure IR of Stator winding.
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 2 | Rotor | Check whether all fastening elements are tight.
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 2 | Rotor | Visual Inspection of Rotor.
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 3 | Motor Bearing | Check Quality of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 3 | Motor Bearing | Extended visual inspection of end shields.
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 8 | Monitoring Instruments | Carbon brush |  | Yes
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 8 | Monitoring Instruments | Carbon Holder
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 8 | Monitoring Instruments | Resistance box
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | 8 | Monitoring Instruments | Winding Temprature
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | 1 | Out Door Unit | Clean & Check of cleaning. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | 1 | Out Door Unit | Checking of terminal & Joints.
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | 1 | Out Door Unit | Cleaning of Coil fins and Connection
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | 2 | Indoor Unit | Clean & Check of cleaning. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | 2 | Indoor Unit | Checking of terminal & Joints.
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | 2 | Indoor Unit | Cleaning of Coil fins and Connection
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | 3 | Fan | Check of bearing. | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | 3 | Fan | Extended visual inspection.
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | 1 | Out Door Unit | Clean & Check of cleaning. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | 1 | Out Door Unit | Checking of terminal & Joints.
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | 1 | Out Door Unit | Cleaning of Coil fins and Connection
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | 2 | Indoor Unit | Clean & Check of cleaning. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | 2 | Indoor Unit | Checking of terminal & Joints.
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | 2 | Indoor Unit | Cleaning of Coil fins and Connection
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | 3 | Fan | Check of bearing. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | 3 | Fan | Extended visual inspection.
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | 1 | Panel | Clean & Check of busbar, Supports & Bandages | [5 empty] | Yes | Yes
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | 1 | Panel | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | 1 | Panel | Cleaning of Panel
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | 2 | Breaker | Checking of Fix & moving contact. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | 2 | Breaker | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | 2 | Breaker | Visual Inspection of Contactors.
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | 3 | Terminal | Checking & Tightening. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | 3 | Terminal | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | 6 | Cooling System | Internal Fan | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | 1 | Stator | Checking of Busbar terminal & Joints.
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | 1 | Stator | Cleaning of Stator winding and Connection
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | 1 | Stator | Measure IR of Stator winding.
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | 2 | Rotor | Check whether all fastening elements are tight.
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | 2 | Rotor | Visual Inspection of Rotor.
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | 3 | Motor Bearing | Check Quality of bearing oil. | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | 3 | Motor Bearing | Extended visual inspection of end shields.
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes | Yes
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | 1 | Stator | Checking of Busbar terminal & Joints.
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | 1 | Stator | Cleaning of Stator winding and Connection
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | 1 | Stator | Measure IR of Stator winding.
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | 2 | Rotor | Check whether all fastening elements are tight.
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | 2 | Rotor | Visual Inspection of Rotor.
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | 3 | Exciter | Check Quality of bearing oil. | [5 empty] | Yes
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | 3 | Exciter | Extended visual inspection of end shields.
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | 6 | Cooling System | Internal Fan | [5 empty] | Yes
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes | Yes
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | 1 | Stator | Checking of Busbar terminal & Joints.
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | 1 | Stator | Cleaning of Stator winding and Connection
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | 1 | Stator | Measure IR of Stator winding.
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | 2 | Rotor | Check whether all fastening elements are tight.
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | 2 | Rotor | Visual Inspection of Rotor.
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | 3 | Exciter | Check Quality of bearing oil. | [5 empty] | Yes
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | 3 | Exciter | Extended visual inspection of end shields.
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | 6 | Cooling System | Internal Fan | [5 empty] | Yes
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | 1 | Panel | Clean & Check of busbar, Supports & Bandages | [5 empty] | Yes | Yes
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | 1 | Panel | Checking of Busbar terminal & Joints.
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | 1 | Panel | Cleaning of Panel
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | 2 | Breaker | Checking of Fix & moving contact. | [5 empty] | Yes
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | 2 | Breaker | Check whether all fastening elements are tight.
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | 2 | Breaker | Visual Inspection of Contactors.
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | 3 | Terminal | Checking & Tightening. | [5 empty] | Yes
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | 3 | Terminal | Extended visual inspection of end shields.
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | 6 | Cooling System | Internal Fan | [5 empty] | Yes
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | 1 | Panel | Clean & Check of busbar, Supports & Bandages | [5 empty] | Yes | Yes
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | 1 | Panel | Checking of Busbar terminal & Joints.
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | 1 | Panel | Cleaning of Panel
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | 2 | Breaker | Checking of Fix & moving contact. | [5 empty] | Yes
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | 2 | Breaker | Check whether all fastening elements are tight.
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | 2 | Breaker | Visual Inspection of Measuring instrument.
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | 3 | Oil status | Check Quality of oil. | [5 empty] | Yes
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | 3 | Oil status | Extended visual inspection of end shields.
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | 6 | Cooling System | External Fan | [5 empty] | Yes
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | 1 | Panel | Clean & Check of busbar, Supports & Bandages | [5 empty] | Yes | Yes
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | 1 | Panel | Checking of Busbar terminal & Joints.
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | 1 | Panel | Cleaning of Panel
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | 2 | Breaker | Checking of Fix & moving contact. | [5 empty] | Yes
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | 2 | Breaker | Check whether all fastening elements are tight.
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | 2 | Breaker | Visual Inspection of contactors.
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | 3 | Terminal | Checking & Tightening. | [5 empty] | Yes
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | 3 | Terminal | Extended visual inspection of end shields.
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | 6 | Cooling System | Internal Fan | [5 empty] | Yes
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | 1 | Out Door Unit | Clean & Check of cleaning. | [5 empty] | Yes
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | 1 | Out Door Unit | Checking of terminal & Joints.
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | 1 | Out Door Unit | Cleaning of Coil fins and Connection
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | 2 | Indoor Unit | Clean & Check of cleaning. | [5 empty] | Yes
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | 2 | Indoor Unit | Checking of terminal & Joints.
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | 2 | Indoor Unit | Cleaning of Coil fins and Connection
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | 3 | Fan | Check of bearing. | [5 empty] | Yes
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | 3 | Fan | Extended visual inspection.
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | 6 | Cooling System | External Fan Motor | [5 empty] | Yes
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | 7 | Heating system | Check function of heating system | [5 empty] | Yes
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | 8 | Monitoring Instruments | Winding Temprature |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | 4 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | 1 | Stator | Clean & Check of winding , Supports & Bandages | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | 1 | Stator | Checking of motor cable terminal & Joints. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | 1 | Stator | Cleaning of Stator winding and Connection
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | 1 | Stator | Measure IR of Stator winding.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | 2 | Rotor | Measure IR of Field winding. | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | 2 | Rotor | Check whether all fastening elements are tight. |  |  | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | 2 | Rotor | Visual Inspection of Rotor.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | 3 | Motor Bearing | Checked bearing grease & top up | [5 empty] | Yes
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | 3 | Motor Bearing | Extended visual inspection of end shields.
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | 6 | Cooling System (Blower fan) | Forced air colled | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | 1 | DS VACUUM filter 14'x36' VFD PANEL | VFD feeder physicaly status. | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | 1 | DS VACUUM filter 14'x36' VFD PANEL | VFD feeder cleaning by blower.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | 1 | DS VACUUM filter 14'x36' VFD PANEL | VFD and by pass control scheme checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | 1 | DS VACUUM filter 14'x36' VFD PANEL | Control & power connection tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | 1 | DS VACUUM filter 14'x36' VFD PANEL | Feeder Incoming & out going bus bar tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | 1 | DS VACUUM filter 14'x36' VFD PANEL | Feeder charging status after maintenance.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | 1 | DS VACUUM filter 14'x36' VFD PANEL | Feeder On, Off and trip indication checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | 1 | DS VACUUM filter 14'x30' VFD PANEL | VFD feeder physicaly status. | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | 1 | DS VACUUM filter 14'x30' VFD PANEL | VFD feeder cleaning by blower.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | 1 | DS VACUUM filter 14'x30' VFD PANEL | VFD and by pass control scheme checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | 1 | DS VACUUM filter 14'x30' VFD PANEL | Control & power connection tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | 1 | DS VACUUM filter 14'x30' VFD PANEL | Feeder Incoming & out going bus bar tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | 1 | DS VACUUM filter 14'x30' VFD PANEL | Feeder charging status after maintenance.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | 1 | DS VACUUM filter 14'x30' VFD PANEL | Feeder On, Off and trip indication checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | 1 | DS Distillery Syrup weightment Pump no.1 VFD PANEL | VFD feeder physicaly status. | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | 1 | DS Distillery Syrup weightment Pump no.1 VFD PANEL | VFD feeder cleaning by blower.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | 1 | DS Distillery Syrup weightment Pump no.1 VFD PANEL | VFD and by pass control scheme checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | 1 | DS Distillery Syrup weightment Pump no.1 VFD PANEL | Control & power connection tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | 1 | DS Distillery Syrup weightment Pump no.1 VFD PANEL | Feeder Incoming & out going bus bar tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | 1 | DS Distillery Syrup weightment Pump no.1 VFD PANEL | Feeder charging status after maintenance.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | 1 | DS Distillery Syrup weightment Pump no.1 VFD PANEL | Feeder On, Off and trip indication checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | 1 | DS Distillery Syrup weightment Pump no.2 VFD PANEL | VFD feeder physicaly status. | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | 1 | DS Distillery Syrup weightment Pump no.2 VFD PANEL | VFD feeder cleaning by blower.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | 1 | DS Distillery Syrup weightment Pump no.2 VFD PANEL | VFD and by pass control scheme checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | 1 | DS Distillery Syrup weightment Pump no.2 VFD PANEL | Control & power connection tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | 1 | DS Distillery Syrup weightment Pump no.2 VFD PANEL | Feeder Incoming & out going bus bar tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | 1 | DS Distillery Syrup weightment Pump no.2 VFD PANEL | Feeder charging status after maintenance.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | 1 | DS Distillery Syrup weightment Pump no.2 VFD PANEL | Feeder On, Off and trip indication checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | 1 | DS Molten Sulphur Dosing pump(E) VFD PANEL | VFD feeder physicaly status. | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | 1 | DS Molten Sulphur Dosing pump(E) VFD PANEL | VFD feeder cleaning by blower.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | 1 | DS Molten Sulphur Dosing pump(E) VFD PANEL | VFD and by pass control scheme checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | 1 | DS Molten Sulphur Dosing pump(E) VFD PANEL | Control & power connection tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | 1 | DS Molten Sulphur Dosing pump(E) VFD PANEL | Feeder Incoming & out going bus bar tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | 1 | DS Molten Sulphur Dosing pump(E) VFD PANEL | Feeder charging status after maintenance.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | 1 | DS Molten Sulphur Dosing pump(E) VFD PANEL | Feeder On, Off and trip indication checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | 1 | Molten Sulphur Dosing pump(W) VFD PANEL | VFD feeder physicaly status. | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | 1 | Molten Sulphur Dosing pump(W) VFD PANEL | VFD feeder cleaning by blower.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | 1 | Molten Sulphur Dosing pump(W) VFD PANEL | VFD and by pass control scheme checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | 1 | Molten Sulphur Dosing pump(W) VFD PANEL | Control & power connection tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | 1 | Molten Sulphur Dosing pump(W) VFD PANEL | Feeder Incoming & out going bus bar tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | 1 | Molten Sulphur Dosing pump(W) VFD PANEL | Feeder charging status after maintenance.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | 1 | Molten Sulphur Dosing pump(W) VFD PANEL | Feeder On, Off and trip indication checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | 1 | DS AIR BLOWER NO.3 VFD PANEL | VFD feeder physicaly status. | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | 1 | DS AIR BLOWER NO.3 VFD PANEL | VFD feeder cleaning by blower.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | 1 | DS AIR BLOWER NO.3 VFD PANEL | VFD and by pass control scheme checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | 1 | DS AIR BLOWER NO.3 VFD PANEL | Control & power connection tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | 1 | DS AIR BLOWER NO.3 VFD PANEL | Feeder Incoming & out going bus bar tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | 1 | DS AIR BLOWER NO.3 VFD PANEL | Feeder charging status after maintenance.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | 1 | DS AIR BLOWER NO.3 VFD PANEL | Feeder On, Off and trip indication checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | 1 | DS CLEAR JUICE PUMP-1 VFD PANEL | VFD feeder physicaly status. | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | 1 | DS CLEAR JUICE PUMP-1 VFD PANEL | VFD feeder cleaning by blower.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | 1 | DS CLEAR JUICE PUMP-1 VFD PANEL | VFD and by pass control scheme checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | 1 | DS CLEAR JUICE PUMP-1 VFD PANEL | Control & power connection tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | 1 | DS CLEAR JUICE PUMP-1 VFD PANEL | Feeder Incoming & out going bus bar tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | 1 | DS CLEAR JUICE PUMP-1 VFD PANEL | Feeder charging status after maintenance.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | 1 | DS CLEAR JUICE PUMP-1 VFD PANEL | Feeder On, Off and trip indication checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | 1 | DS INJECTION PUMP NO.5 VFD PANEL | VFD feeder physicaly status. | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | 1 | DS INJECTION PUMP NO.5 VFD PANEL | VFD feeder cleaning by blower.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | 1 | DS INJECTION PUMP NO.5 VFD PANEL | VFD and by pass control scheme checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | 1 | DS INJECTION PUMP NO.5 VFD PANEL | Control & power connection tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | 1 | DS INJECTION PUMP NO.5 VFD PANEL | Feeder Incoming & out going bus bar tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | 1 | DS INJECTION PUMP NO.5 VFD PANEL | Feeder charging status after maintenance.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | 1 | DS INJECTION PUMP NO.5 VFD PANEL | Feeder On, Off and trip indication checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | 1 | DS 1750 WIL AC VFD PANEL-1 | VFD feeder physicaly status. | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | 1 | DS 1750 WIL AC VFD PANEL-1 | VFD feeder cleaning by blower.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | 1 | DS 1750 WIL AC VFD PANEL-1 | VFD and by pass control scheme checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | 1 | DS 1750 WIL AC VFD PANEL-1 | Control & power connection tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | 1 | DS 1750 WIL AC VFD PANEL-1 | Feeder Incoming & out going bus bar tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | 1 | DS 1750 WIL AC VFD PANEL-1 | Feeder charging status after maintenance.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | 1 | DS 1750 WIL AC VFD PANEL-1 | Feeder On, Off and trip indication checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | 1 | DS 1750 NHEC(DC) VFD PANEL-2 | VFD feeder physicaly status. | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | 1 | DS 1750 NHEC(DC) VFD PANEL-2 | VFD feeder cleaning by blower.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | 1 | DS 1750 NHEC(DC) VFD PANEL-2 | VFD and by pass control scheme checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | 1 | DS 1750 NHEC(DC) VFD PANEL-2 | Control & power connection tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | 1 | DS 1750 NHEC(DC) VFD PANEL-2 | Feeder Incoming & out going bus bar tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | 1 | DS 1750 NHEC(DC) VFD PANEL-2 | Feeder charging status after maintenance.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | 1 | DS 1750 NHEC(DC) VFD PANEL-2 | Feeder On, Off and trip indication checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 | 1 | DS 1750 WIL AC VFD PANEL-3 | VFD feeder physicaly status. | [5 empty] | Yes
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 | 1 | DS 1750 WIL AC VFD PANEL-3 | VFD feeder cleaning by blower.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 | 1 | DS 1750 WIL AC VFD PANEL-3 | VFD and by pass control scheme checked.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 | 1 | DS 1750 WIL AC VFD PANEL-3 | Control & power connection tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 | 1 | DS 1750 WIL AC VFD PANEL-3 | Feeder Incoming & out going bus bar tightness.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 | 1 | DS 1750 WIL AC VFD PANEL-3 | Feeder charging status after maintenance.
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 | 1 | DS 1750 WIL AC VFD PANEL-3 | Feeder On, Off and trip indication checked.

## EQUIPMENT MAINTENANCE HISTORY
source file | sheet id | sheet name | EQUIPMENT TAG NO | Season / OFF Season | Year | Date of Start | Date of Finish | Outage/ Observation | Action Taken | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | Off-Season -2023 | 2023 |  |  | Repair Maintenance | Complete Motor overhauling done |  | External Party by M/S Durga Construction | P.K.Maurya
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 2023-07-25 |  |  | IR Value before dismantling | Stator - 5000 V upto 30 sec. E-R = 480 MΩ E-Y = 570 MΩ E-B = 300 MΩ R-Y = 580 MΩ Y-B = 546 MΩ B-R = 636 MΩ Rotor - 1000 V upto 30 sec. E-R = 10.9 GΩ E-Y = 16.0 GΩ E-B = 09.4 GΩ R-Y = 16.0 GΩ Y-B = 19.0 GΩ B-R = 14.5 GΩ SLIP RING - 1000 V upto 30 sec. E-R = 103 MΩ E-Y = 1180 MΩ E-B = 635 MΩ R-Y = 948 MΩ Y-B = 225 MΩ B-R = 610 MΩ
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  |  |  | Resistence of Coil | Staor - R Phase - 309 m ohm Y Phase - 310 m ohm B Phase - 314 m ohm Rotor - R Phase - 9.9 m ohm Y Phase - 9.9 m ohm B Phase - 9.9 m ohm
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  |  |  |  | Dismantling | Rotor taken out. Stator and Rotor cleaning done.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 26.07.2023 |  |  | Varnishing | Stator and rotor varnishing done.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 27.07.2023 |  |  | Heating | Stator and rotor both kept in heat.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 28.07.2023 |  |  | Assembling | 1. DE Side Bearing NU 240 C3 Worn-out spot on rollar observed, So New NSK Make NU240 C3 Bearing replaced. 2. IR Value after overhauling - Stator - 5000 V upto 30 sec. E-R = 5.6 GΩ E-Y = 6.3 GΩ E-B = 5.1 GΩ R-Y = 3.1 GΩ Y-B = 2.9 GΩ B-R = 4.1 GΩ Rotor - 1000 V upto 30 sec. E-R = 3.8 GΩ E-Y = 4.4 GΩ E-B = 7.1 GΩ R-Y = 13.2 GΩ Y-B = 14.2 GΩ B-R = 11.5 GΩ
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 01.08.2023 |  |  | Slip ring and carbon holder fitting | IR Value of Slip Ring - SLIP RING - 1000 V upto 30 sec. E-R = 460 MΩ E-Y = 1550 MΩ E-B = 1570 MΩ R-Y = 2.1 GΩ Y-B = 1.8 GΩ B-R = 1.4 GΩ
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 03.08.2023 |  |  | Cooler Cleaning and Hydraulic Testing. | Cleaning and testing done upto 5.0 kg/Cm2 hydraulic pressure.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 05.08.2023 |  |  | Trial Taken | Successfully trial taken
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | Season -2023-24 | 2023-12-02 |  |  | NDE SIDE BEARING HAD SOME LINING ON INNER SURFACE . | BOTH BEARING OF NDE SIDE, NU236C3 & 6236 C3 SKF MAKE, HAS BEEN REPLACED |  | INHOUSE | P. K. Maurya
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | Off-Season - 2024 | 31.08.2024 |  |  | Dismantling | Slip Ring and Holder removed. Cooler Removed. Rotor taken out. |  | External Party M/S C&G Ltd.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 01.09.2024 |  |  | Overhauling | Both bearing cleaning done.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 01.09.2024 |  |  | Overhauling | Stator and Rotor Dry Ice cleaning done and kept in heat.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 02.09.2024 |  |  | Varnishing | Stator epoxy gel coating done of shredder Motor 1. Cooler cleaning done by nylon brush.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 03.09.2024 |  |  | Varnishing and bearing fitting | Rotor epoxy gel coating done . Both bearing fitted, regreasing done with Omega 85.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 03.09.2024 |  |  | Rotor fitting | Rotor fitted and both cover tighten and cooler fitted..
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 07.09.2024 |  |  | Slip Ring Fitting | Slipring and slip ring holder fitted by proper cleaning. IR Value after overhauling - 1. Stator - 5630 V upto 1 Minut. E-R = 12.1 GΩ E-Y = 11.8 GΩ E-B = 12.7 GΩ R-Y = 23.7 GΩ Y-B = 26.0 GΩ B-R = 25.0 GΩ 2.Rotor - 1000 V upto 30 sec. E-R = infinitive E-Y = infinitive E-B = infinitive R-Y = infinitive Y-B = infinitive B-R = infinitive 3. SlipRing- 1000 V upto 30 Sec Ring to Ring - Infinitive Ring to earth - infinitive
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 09.09.2024 |  |  | Connection and Painting | Motor connection done and external painting done.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 10.09.2024 |  |  | Trial | Motor trial successfully done.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | Off-Season 2025 | 01.07.2025 |  |  | Dismantaling | Slip Ring, Carbon Brush Holder dismantling and removind work done. Rotor connection and Stator connection opened. |  | Internal | P.K.Maurya Dilip Pandey Kamlesh
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 01.07.2025 |  |  | Testing | IR Value taken- Stator (With 5000 V upto 30 Sec.) Earth to R - 7 G Ohm , Earth to Y - 6 G Ohm, Earth to B - 7 G Ohm Y - B - 20 G OHM R - Y - 14 G OHM B - R - 30 G OHM Rotor (With 1000 V upto 30 Sec.) Earth to R - 600 M Ohm, Earth to Y - 650 M Ohm, Earth to B - 640 M Ohm, R - Y - 660 M Ohm Y - B - 570 M Ohm B - R - 600 M Ohm
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 02.07.2025 |  |  | Dismantaling | NDE Cover opened and observed grease had spread on Rotor and stator, so inform to M/S CG for observation and action required.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 08.07.2025 |  |  | observation | M/S Shiv Electrical GKP has visited the site and he checked the Bearing end plate cover clearance and found it 0.25 mm and this is normal. And suggest that excess grease has spread during first starting of motor.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 10.07.2025 |  |  | internal | over stator and rotor grease cleaning done by clothes.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 10.07.2025 |  |  | NDE Bearing | Both Bearing cleaned and checked, found normal. 6236 & NU236.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 10.07.2025 |  |  | NDE Cover fitting | NDE Cover fitted by using Grease omega -85.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 11.07.2025 |  |  | DE Side | DE COVER OPENED AND VISUAL INSPECTION DONE AND FOUND OK
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 11.07.2025 |  |  | DE Bearing | Bearing cleaning done and checked found ok.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 11.07.2025 |  |  | DE Cover | DE Cover fitted by using Grease omega -85.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 12.07.2025 |  |  | Cleaning of Slipring assembly | Cleaning of Carbon holder, Ring and Slip Ring has been done.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 14.07.2025 |  |  | Fitting of Slip Ring assembly | 1) Slip Ring Fitted and it's ovality has been checked and found B phase Ring has 4division, Y phase has 3 division and R phase has 5 division which is normal. 2) IR Value of SlipRing taken at 1000 V Megger- R-Y - 750 Mohm, Y-B - 810 M Ohm, B-R - 700 Mohm. R - Earth - 850 Mohm, Y - Earth - 900 M ohm B - Earth 800 m Ohm. 3) 6 Nos. new holder and all 12 Nos. New carbon brush has been fitted by numbering. (3 Nos. Old holder and all 6 Nos. New carbon brush has been fitted with numbering. After proper cleaning)
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 26.07.2025 |  |  | Cooler Cleaning and Hydraulic Testing. | Cooler dismantlled and external cleaning done. |  | Internal |  | Pappu Singh + Helper
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 28.07.2025 |  |  |  | Cooler cleaning done by nylon brush.
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 30.07.2025 |  |  |  | Assembling and fitting done, hydraulic testing taken upto 7 KG/CM2 UPTO 30 MINUT .
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | Off-Season 2025 | 18.09.2025 |  |  | Existing old motor removed from position | Due to purchased spare motor Sr. No. 2241047 is to be trialed
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 | Season 2025 | 06.11.2025 |  |  | General Checking and cleaning done during scheduled stoppage | Carbon brush, Slipring and slip ring holder proper cleaning done by compressed air and petrol. All Lead of carbon brush has been tightening done. |  | Internal | P.K.Maurya Dilip Pandey Kamlesh
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 06.11.2025 |  |  | One No. Carbon Brush found stuck in holder | Carbon removed by hammering and new carbon brush fitted with small finishing by emery paper
electrical Mill house life history Data-30072026.xlsx | 88f7926d1273 | SHREDDER MOTOR No. 1 | ZIL/GSM/SP/ELECT/MH/01 |  | 03.12.2025 |  |  | General Checking and cleaning done during scheduled stoppage. | Carbon brush, Slipring and slip ring holder proper cleaning done by compressed air and petrol. All Lead of carbon brush has been tightening done. Found all is normal. |  | Internal | P.K.Maurya Dilip Pandey Kamlesh
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 | Off-Season -2023 | 2023 |  |  | Repair Maintenance | Complete Motor overhauling done |  | External Party by M/S Durga Construction | P.K.Maurya
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 2023-07-30 |  |  | IR Value before dismantling | Stator - 5000 V upto 30 sec. E-R = 5.4 GΩ E-Y = 6.3 GΩ E-B = 5.7 GΩ R-Y = 5.5 GΩ Y-B = 3.3 GΩ B-R = 5.3 GΩ Rotor - 1000 V upto 30 sec. E-R = 8.6 GΩ E-Y = 7.4 GΩ E-B = 7.2 GΩ R-Y = 8.1 GΩ Y-B = 8.4 GΩ B-R = 7.5 GΩ SLIP RING - 1000 V upto 30 sec. E-R = 30 GΩ E-Y = 30 GΩ E-B = 27 GΩ R-Y = 3.7 GΩ Y-B = 8.0 GΩ B-R = 1.2 GΩ
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  |  |  |  | Resistence of Coil | Staor - R Phase - 310 m ohm Y Phase - 310 m ohm B Phase - 310 m ohm Rotor - R Phase - 10.3 m ohm Y Phase - 10.3 m ohm B Phase - 10.3 m ohm
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 31.07.2023 |  |  | Dismantling | Rotor taken out. Stator and Rotor cleaning done.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 31.07.2023 |  |  | Varnishing | Stator and rotor varnishing done.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 31.07.2023 |  |  | Heating | Stator and rotor both kept in heat.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 03.08.2023 |  |  | Assembling | 1. IR Value after overhauling - Stator - 5000 V upto 30 sec. E-R = 2.1 GΩ E-Y = 2.4 GΩ E-B = 3.1 GΩ R-Y = 1.3 GΩ Y-B = 2.5 GΩ B-R = 1.2 GΩ Rotor - 1000 V upto 30 sec. E-R = 4.4 GΩ E-Y = 4.7 GΩ E-B = 5.4 GΩ R-Y = 6.2 GΩ Y-B = 6.1 GΩ B-R = 6.4 GΩ
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 02.08.2023 |  |  | Cleaning of Holder | Cleaning of Slipring holder has been done.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 02.08.2023 |  |  | Bearing cleaning | Both Side bearing cleaning done visual inspected and found DE Bearing NU240 C3 was worn out and has been replaced with new.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 03.08.2023 |  |  | Slip ring | SLIPRING Machining, cleaning and polishing done. IR Value of Slip Ring - SLIP RING - 1000 V upto 30 sec. E-R = 40 GΩ E-Y = 79 GΩ E-B = 29 GΩ R-Y = 47 GΩ Y-B = 36 GΩ B-R = 42 GΩ
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 03.08.2023 |  |  | Cooler Cleaning and Hydraulic Testing. | Cleaning and testing done upto 5.0 kg/Cm2 hydraulic pressure.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 05.08.2023 |  |  | Trial Taken | Successfully trial taken
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 | Season -2023-24 | 30.03.2024 |  |  | NDE SIDE BEARING HAD SEIZED . | SIEZED BEARING HAS BEEN REMOVED BY CUTTING AND NEW BEARING OF NDE SIDE, NU236C3 & 6236 C3 NSK MAKE, HAS BEEN FITTED. |  | INHOUSE | P. K. Maurya
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 | Off-Season - 2024 | 27.08.2024 |  |  | Dismantling | Slip Ring and Holder removed. |  | Out Side Party M/S C&G Ltd.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 28.08.2024 |  |  | Dismantaling | Cooler Removed. Rotor taken out.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 29.08.2024 |  |  | Cleaning of stator and rotor | Dry ice cleaning done of Stator and Rotor and both kept in heat.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 30.08.2024 |  |  | Bearing cleaning and checking | NDE Side Both bearing cleaned and inspected, some jamming observed. Clearance checked, 6236 - 0.045mm and NU 236 - 0.05mm. So both bearing taken out.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 02.09.2024 |  |  | Rotor Shaft trueness checking | Shredder Motor no. 2 Rotor NDE shaft ture ness checked on Big lathe machine and polished at ovality portion.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 04.09.2024 |  |  | Varninshing | Stator & Rotor epoxy gel coating done
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 04.09.2024 |  |  | DE Bearing replaced | DE Side New Bearing NU-240 fitted by heating through Induction heater.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 04.09.2024 |  |  | Grease plate more gapping observed | NDE Side grease plate (inside) welding done by machinable CI Rod.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 04.09.2025 |  |  | Cooler Cleaning and Hydraulic Testing. | cooler cleaning and testing done.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 05.09.2025 |  |  | Assembling | Rotor fitted and DE cover tighten.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 05.09.2024 |  |  |  | NDE Side 6236 bearing fitted.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 06.09.2024 |  |  |  | Shredder Motor no. 2 NDE Side NU236 bearing fitted.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 06.09.2024 |  |  |  | NDE Side bearing regeasing done with omega 85.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 09.09.2024 |  |  | Slip Ring Fitting | Slipring and slip ring holder fitted by proper cleaning.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 09.09.2024 |  |  |  | Cooler fitted and painting done.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 10.09.2024 |  |  | Trial Testing | Motor connection done and trial takeken.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 | Off-Season 2025 | 2025-07-03 |  |  | Dismantling | Slip Ring, Carbon Brush Holder dismantling work done. |  | In House | P.K.Maurya | Dilip Pandey + Kamlesh
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 2025-07-03 |  |  | Dismantling | Rotor connection and Stator connection opened.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 2025-07-03 |  |  | Testing | IR Value taken- Stator (With 5000 V upto 30 Sec.) Earth to R -17 G Ohm , Earth to Y - 11 G Ohm, Earth to B - 8 G Ohm Y - B - 10.5 G OHM R - Y - 11 G OHM B - R - 9 G OHM Rotor (With 1000 V upto 30 Sec.) Earth to R - INFINITIVE , Earth to Y - INFINITIVE , Earth to B - INFINITIVE , R - Y - INFINITIVE Y - B - INFINITIVE B - R - INFINITIVE
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 04.07.2025 |  |  | overhauling and assembling | NDE Cover opend, Stator & Rotor inspection done, found ok. Bearing re-greasing done with Omega -85 and bearing housing box-up AND nde Cover fitted.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 05.07.2025 |  |  | overhauling and assembling | DE Cover opend, Stator & Rotor inspection done, found ok. DE Bearing NU240 cleaning done, and inspected, found some places lining spot, So it has been decided to replace it.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 07.07.2025 |  |  | overhauling and assembling | Faulty Bearing has beenTaken Out, and New FAG Make NU 240 EM C3 Bearing has been fitted by heating in Taransformer Oil. DE cover has been fiitted , using Omega 85 Grease.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 15.07.2025 |  |  | overhauling and assembling | Slip Ring and its cover cleaning done by Washing Petrol, and Bectol Red applied. All holder cleaning done by washing Petrol.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 16.07.2025 |  |  | overhauling and assembling | Slip Ring fitted at motor. IR Value of SlipRing taken at 1000 V Megger- R-Y - Infinitive, Y-B - Infinitive, B-R - Infinitive. R - Earth - Infinitive, Y - Earth - Infinitive B - Earth Infinitive.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 17.07.2025 |  |  | overhauling and assembling | All holder and Carbon brush fitted and set right after numbering.
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 | Season 2025 | 06.11.2025 |  |  | General Checking and cleaning done during scheduled stoppage | Carbon brush, Slipring and slip ring holder proper cleaning done by compressed air and petrol. All Lead of carbon brush has been tightening done. |  | Internal | P.K.Maurya Dilip Pandey Kamlesh
electrical Mill house life history Data-30072026.xlsx | ddef4dd1cd11 | SHREDDER MOTOR No. 2 | ZIL/GSM/SP/ELECT/MH/02 |  | 03.12.2025 |  |  | General Checking and cleaning done during scheduled stoppage. | Carbon brush, Slipring and slip ring holder proper cleaning done by compressed air and petrol. All Lead of carbon brush has been tightening done. Found all is normal. |  | Internal | P.K.Maurya Dilip Pandey Kamlesh
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | Off-Season-2023 | 24.07.2023 |  |  | Testing before dismantaling | IR Value - (1000 v UPTO 30Sec) EARTH TO PHASE- E -W2 = TB1 - 4.8 GΩ and TB2- 5.7 GΩ E -U2 =TB1 - 4.9 GΩ,and TB2 - 4.5 GΩ E -V2 = TB1 - 5.9 GΩ. and TB2 - 4.9 GΩ PAHSE TO PHASE- W2 -U2 = TB1 - 8.6 GΩ. and TB2 - 8.7 GΩ U2 -V2 = TB1 - 8.7 GΩ. and TB2 - 10.6 GΩ V2 -W2 = TB1 - 7.1 GΩ. and TB2 - 9.7 GΩ COIL TO COIL - U2-U2 = 8.7 GΩ, W2-W2 = 8.7 GΩ, V2-V2 = 8.9 GΩ |  | External Party M/S Durga Construction | P.K.Maurya
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 25.07.2023 |  |  | Dismantaling | Both cover opened and rotor taken out. Cleaning of rotor and staotr has been done. Stator kept heat.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 26.07.2023 |  |  | Varnishing | Stator and Rotor varnishing done by Bectol Red.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 27.07.2023 |  |  | Assembling | Both bearing cleaning done and checked both bearing DE 6330 C3 and NDE Insulated 6330 C3 found in good condition. Motor has been assembled by using Omega -85 grease.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 31.07.2023 |  |  | IR Value after overhauling | IR Value - (1000 v UPTO 30Sec) EARTH TO PHASE- E -W2 = TB1 - 4.8 GΩ and TB2- 5.7 GΩ E -U2 =TB1 - 4.1 GΩ,and TB2 - 4.3 GΩ E -V2 = TB1 - 6.4 GΩ. and TB2 - 4.3 GΩ PAHSE TO PHASE- W2 -U2 = TB1 - 5.9 GΩ. and TB2 - 5.1 GΩ U2 -V2 = TB1 - 6.4 GΩ. and TB2 - 6.4 GΩ V2 -W2 = TB1 - 4.9GΩ. and TB2 - 4.3 GΩ
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 02.08.2023 |  |  | trial testing | No Load trial of motor successfully done.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | Off-Season-2024 | 08.07.2024 |  |  | Dismantaling | Motor blower dismantaled, and motor external cleaning done by water. |  | Internal | P.K.Maurya | Dilip Pandey + Kamlesh
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 09.07.024 |  |  | Dismantaling | Motor NDE cover opened and stator visual inspection done found OK. Bearing 6330 C3 cleaning done and checked found ok so NDE cover fitted by using Omega 85 Grease.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 10.07.2024 |  |  | Blower Fan | Blower Fan Motor overhauling done by dismantaling, cleaning and heating.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 11.07.2024 |  |  | Overhauling | DE Cover opened, Bearing washed and inspected, DE Bearing has abnormal sound.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 12.07.2024 |  |  | Bearing replacement | Old Bearing removed by Puller and New Bearing FAG 6330 M C3 has been fitted by pipe and hammering. Regreasing done by omega 85 and cover fitted.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 | Off-Season-2025 | 11.06.2025 |  |  | IR Value Testing before dismantaling | IR Value -1000 V 30 Sec. EARTH TO PHASE- E -W2 = TB1 - 390 MΩ and TB2- 270 MΩ E -U2 =TB1 - 870MΩ,and TB2 -270MΩ E -V2 = TB1 - 750MΩ. and TB2 - 200MΩ PAHSE TO PHASE- W2 -U2 = TB1 - 1000MΩ. and TB2 - 400MΩ U2 -V2 = TB1 - 1200MΩ. and TB2 - 410MΩ V2 -W2 = TB1 - 970MΩ. and TB2 - 450MΩ |  | Internal | P.K.Maurya | Dilip Pandey+Kamlesh
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 14.06.2025 |  |  | Dismantaling | Washing of Motor has been done by water.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 16.06.2025 |  |  | Dismantaling | Motor NDE cover opened and stator visual inspection done found OK. Bearing 6330 C3 cleaning done and checked found ok so NDE cover fitted by using Omega 85 Grease.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 17.06.2025 |  |  | Dismantaling | Motor DE cover opened bearing opened with diesel and inspected found abnormal sound, so bearing taken by puller, and New Bearing NKS make has been fitted by Pipe and hammering.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 18.06.2025 |  |  | Blower Fan | Blower Fan Motor overhauling done by dismantaling, cleaning and heating.
electrical Mill house life history Data-30072026.xlsx | 88e72bf6e174 | Zero Mill Drive Motor No.3 | ZIL/GSM/SP/ELECT/MH/03 |  | 30.07.2025 |  |  | DE Bearing grease replaced | As per suggested omega Grease Team Omega 51 grease is special for current leakage bearing so DE Side Grease replaced with omega 51.
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | Off-Season 2023 | 2023 |  |  | Repair Maintenance | Complete Motor overhauling done |  | External Party M/S Durga Construction
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  | 27.07.2023 |  |  | IR Vaue before dismantaling | IR Value - (1000 v UPTO 30Sec) EARTH TO PHASE- E -W2 = TB1 - 604 MΩ and TB2- 280MΩ E -U2 =TB1 - 715 MΩ,and TB2 - 232 MΩ E -V2 = TB1 - 506MΩ. and TB2 - 198MΩ PAHSE TO PHASE- W2 -U2 = TB1 - 1130MΩ. and TB2 -324MΩ U2 -V2 = TB1 - 1296MΩ. and TB2 - 451MΩ V2 -W2 = TB1 - 1504MΩ. and TB2 - 491MΩ COIL TO COIL - U2-U2 = 1033MΩ, W2-W2 = 640MΩ, V2-V2 = 811 MΩ
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  | 27.07.2023 |  |  | dismantaling | Motor dismantalled and rotor taken out. Cleaning done and heated.
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  | 28.07.2023 |  |  | Overhauling | Stator and Rotor varnished with Bectol Red. Both bearing cleaning done and inspected, found DE Bearing has abnormal 6232 C3 .Note - Due to frequent failure of DE bearing it has been decided to replaced ball bearing with Roller Bearing and replaced with Nu232 C3. DE Bearing insulated 6228C3 is in good condition. Both cover has been fitted using Omega 85 Grease.
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  | 01.08.2023 |  |  | IR Value after overhauling | IR Value - (1000 v UPTO 30Sec) EARTH TO PHASE- E -W2 = TB1 - 1.02GΩ and TB2- 960MΩ E -U2 =TB1 - 1.45GΩ,and TB2 -472 MΩ E -V2 = TB1 - 1.30GΩ. and TB2 - 690MΩ PAHSE TO PHASE- W2 -U2 = TB1 - 2.3GΩ. and TB2 -1.05GΩ U2 -V2 = TB1 - 2.3GΩ. and TB2 - 1.15GΩ V2 -W2 = TB1 - 2.7GΩ. and TB2 - 1.78GΩ COIL TO COIL - U2-U2 = 1.3GΩ, W2-W2 = 1.79GΩ, V2-V2 = 2.2GΩ
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  | 02.08.2023 |  |  | Motor trial | After operation 50 RPM DE bearing creat noise. So motor dismantalled and roller bearing replaced with ball bearing 6232 C3, regreasing done with omega 85.
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | Off -Season 2024 | 2024 |  |  | Overhauling and Repairing | Motor external cleaning done by water. Motor both cover opened and bearing cleaning done by diesel and inspected, found ok, so regreasing done with omega 85 and both cover fitted. |  | Internal | P.K.Maurya | Dilip Pandey + Kamlesh
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 | Off-Season 2025 | 21.06.2025 |  |  | Overhauling and Repairing | Motor external cleaning done by water. |  | Internal | P.K.Maurya | Dilip Pandey + Kamlesh
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  | 22.06.2025 |  |  | Overhauling and Repairing | Motor NDE Cover dismantalled, Bearing 6228 C3 insulated washed and inspected found ok. So Re-greasing done by omega 85 and cover fitted.
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  | 23.06.2025 |  |  | Overhauling and Repairing | Motor DE Cover dismantalled, Bearing 6232 C3 washed and inspected found ok. So Re-greasing done by omega 85 and cover fitted.
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  | 24.06.2025 |  |  | Blower Motor | Blower Motor overhauling done by dismantaling heating and regreasing.
electrical Mill house life history Data-30072026.xlsx | 1d004acba7b9 | 4rth Mill Drive Motor No.4 | ZIL/GSM/SP/ELECT/MH/04 |  | 30.07.2025 |  |  | DE Bearing grease replaced | As per suggested omega Grease Team Omega 51 grease is special for current leakage bearing so DE Side Grease replaced with omega 51.
electrical Mill house life history Data-30072026.xlsx | 3b203dd8600f | CU-No.1 | ZIL/GSM/SP/ELECT/MH/05 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | L.T motor terminal plate replaced (west side)
electrical Mill house life history Data-30072026.xlsx | b582619592fb | CU-No. 2 | ZIL/GSM/SP/ELECT/MH/06 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | Oil pump motor 6206 ZZ bearing replaced.
electrical Mill house life history Data-30072026.xlsx | 5b60e82f9a72 | CU-No. 3 | ZIL/GSM/SP/ELECT/MH/07 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | L.T 6208 ZZ bearing replaced (East side) L.T 6307 ZZ bearing replaced (West side)
electrical Mill house life history Data-30072026.xlsx | c92e585550a9 | CU-No.4 | ZIL/GSM/SP/ELECT/MH/08 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | C.T 6208 ZZ bearing replaced
electrical Mill house life history Data-30072026.xlsx | 5b46d0d4e790 | CU-No.5 | ZIL/GSM/SP/ELECT/MH/09 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | L.T motor terminal plate replaced (west side)
electrical Mill house life history Data-30072026.xlsx | f450390a23e9 | CU-No.6 | ZIL/GSM/SP/ELECT/MH/10 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | Terminal Plate Replaced
electrical Mill house life history Data-30072026.xlsx | 57f6157ec7b8 | Transformer 3.15 MVA | ZIL/GSM/SP/ELECT/MH/11 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete overhauling done
electrical Mill house life history Data-30072026.xlsx | 05701eb041bb | Transformer 2.5 MVA | ZIL/GSM/SP/ELECT/MH/12 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete overhauling done
electrical Mill house life history Data-30072026.xlsx | 6d80d2dcc874 | Mill house H.T PCC | ZIL/GSM/SP/ELECT/MH/13 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete overhauling done
electrical Mill house life history Data-30072026.xlsx | 4f98e76a1452 | Mill house L.T PCC & MCC PANEL | ZIL/GSM/SP/ELECT/MH/14 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete overhauling done
electrical Mill house life history Data-30072026.xlsx | dbc83d23d4df | Mill house VFD PANEL | ZIL/GSM/SP/ELECT/MH/15 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete overhauling done
electrical Mill house life history Data-30072026.xlsx | 6b536c59ab7e | Fourth Mill Blower Motor | ZIL/GSM/SP/ELECT/MH/16 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 78cac24605c7 | Aux. Cane Carier | ZIL/GSM/SP/ELECT/MH/17 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | a12171d74d5d | Main Cane Carier | ZIL/GSM/SP/ELECT/MH/18 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 31262d78a3d7 | Cardian Drum-1 | ZIL/GSM/SP/ELECT/MH/19 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | c20f5995596a | Cardian Drum-2 | ZIL/GSM/SP/ELECT/MH/20 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 42ee48a19e25 | Cane Kicker | ZIL/GSM/SP/ELECT/MH/21 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | d94be2fb6a44 | Feeder Drum | ZIL/GSM/SP/ELECT/MH/22 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 73320a1d47e6 | Shredder Carier | ZIL/GSM/SP/ELECT/MH/23 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | bf0c8551629e | Shredder Belt | ZIL/GSM/SP/ELECT/MH/24 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 570c5a68d64e | Cane Equalizer | ZIL/GSM/SP/ELECT/MH/25 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 87e5104868ca | IRC-No.1 | ZIL/GSM/SP/ELECT/MH/26 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | a108a3d17e24 | IRC-No.2 | ZIL/GSM/SP/ELECT/MH/27 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 1b63820ad211 | IRC-No.3 | ZIL/GSM/SP/ELECT/MH/28 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | c40eb57afda6 | IRC-No.4 | ZIL/GSM/SP/ELECT/MH/29 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 835390f402a0 | Secondary Rotary Screen No-2 | ZIL/GSM/SP/ELECT/MH/30 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 7ea20abab10d | Secondary Rotary Screen No-1 | ZIL/GSM/SP/ELECT/MH/31 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | d5a12edd9a99 | Primary Rotary Screen | ZIL/GSM/SP/ELECT/MH/32 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | d4cf174640b3 | Screen Juice Pump-1 Ref. | ZIL/GSM/SP/ELECT/MH/33 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 40874a1f5235 | Screen Juice Pump-2 Ref. | ZIL/GSM/SP/ELECT/MH/34 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 949391122c0b | DS Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/35 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | ef91aabd20cb | DS Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/36 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 2a026b1dd4a3 | 1 st Stage Screen Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/37 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | c08c6c21f044 | 1 st Stage Screen Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/38 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 583ef04a018e | Cooling Tower Pump-1 Motor | ZIL/GSM/SP/ELECT/MH/39 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 5c12aeaa8129 | Cooling Tower Pump-2 Motor | ZIL/GSM/SP/ELECT/MH/40 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | ee6618a17ff5 | Hot Water Imbibition Pump-1 | ZIL/GSM/SP/ELECT/MH/41 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 475510cf7f1f | Hot Water Imbibition Pump-2 | ZIL/GSM/SP/ELECT/MH/42 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 49d4599fd86d | Zero Mill Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/43 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | d3ea4afed584 | Zero Mill Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/44 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 94c1f1f0811e | Mill No-1 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/45 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 4f456ea36610 | Mill No-1 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/46 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 924949997c40 | Mill No-2 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/47 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 0266594cbb2b | Mill No-2 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/48 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 8f4e613ac91d | Mill No-3 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/49 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 8b4673274358 | Mill No-3 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/50 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | aae7e67deecc | Mill No-4 Juice Pump-1 | ZIL/GSM/SP/ELECT/MH/51 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | f3d0135cbb25 | Mill No-4 Juice Pump-2 | ZIL/GSM/SP/ELECT/MH/52 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 58991dbdb665 | Hot Water Pump-3 | ZIL/GSM/SP/ELECT/MH/53 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 6883ad88637e | Aux. Cane Carier oil Pump 1 &2 | ZIL/GSM/SP/ELECT/MH/54 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | c8f3734afe11 | Main Cane Carrier Oil Pump | ZIL/GSM/SP/ELECT/MH/55 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 65b767b4f650 | Shredder Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/56 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 75eedf0781a5 | Zero Mill Oil Pump 1 & 2 | ZIL/GSM/SP/ELECT/MH/57 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 61b6b133d3bf | Slate Cleaning Brush Motor | ZIL/GSM/SP/ELECT/MH/58 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 7ca7e0834751 | MILL EOT 50 MT | ZIL/GSM/SP/ELECT/MH/59 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 278a6bafc3d8 | MILL EOT 25 MT | ZIL/GSM/SP/ELECT/MH/60 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | 2ae969efa411 | Truck Tripler | ZIL/GSM/SP/ELECT/MH/61 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
electrical Mill house life history Data-30072026.xlsx | b65b65e052d9 | Air Conditioner | ZIL/GSM/SP/ELECT/MH/62 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | be4f92f1b6f3 | Control Room A.C | ZIL/GSM/SP/ELCT/70 TPH/52 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | d0376042701f | C.T Fan-2 | ZIL/GSM/SP/ELCT/MH/50 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | 03cee6cd6ee8 | C.T Fan-1 | ZIL/GSM/SP/ELCT/MH/49 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | a3950a24a73f | Cooling Tower Pump-2 | ZIL/GSM/SP/ELCT/MH/48 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | b8caff109e6d | Cooling Tower Pump-1 | ZIL/GSM/SP/ELCT/MH/47 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | 24485eebd568 | UGR Pump NO-3 | ZIL/GSM/SP/ELCT/MH/46 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | b0daab9b6718 | UGR Pump NO-2 | ZIL/GSM/SP/ELCT/MH/45 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | 9f1f45dca11b | UGR Pump NO-1 | ZIL/GSM/SP/ELCT/MH/44 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | f9848ed33ca0 | CHEMICAL DOSING PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/43 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | 85294b29c704 | CHEMICAL DOSING PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/42 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | 905c352537a7 | BAGAS BLOWER-3 | ZIL/GSM/SP/ELCT/BH/41 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | 46336f87db96 | BAGAS BLOWER-2 | ZIL/GSM/SP/ELCT/BH/40 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | e3445e6f2460 | BAGAS BLOWER-1 | ZIL/GSM/SP/ELCT/BH/39 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | b1b37c55efce | S.A Fan-2 | ZIL/GSM/SP/ELCT/70 TPH/38 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
2_70 TPH boiler life history.xlsx | 9bd6cf49ab16 | PCC & MCC PANEL | ZIL/GSM/SP/ELCT/70 TPH/37 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete overhauling done
2_70 TPH boiler life history.xlsx | 8ef4fc57a116 | Transfer pump | ZIL/GSM/SP/ELCT/70 TPH/36 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 7.9, 8.2 & 8.9 Amp.
2_70 TPH boiler life history.xlsx | 92768fde2ff6 | Bagas Elevator | ZIL/GSM/SP/ELCT/70 TPH/35 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 26.2, 27.1 & 26.5 Amp.
2_70 TPH boiler life history.xlsx | bbd72cd93434 | RBC | ZIL/GSM/SP/ELCT/70 TPH/34 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current
2_70 TPH boiler life history.xlsx | 9f2862f2d79e | MBC | ZIL/GSM/SP/ELCT/70 TPH/33 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current
2_70 TPH boiler life history.xlsx | 3acf66164a31 | F.D Fan | ZIL/GSM/SP/ELCT/70 TPH/32 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current
2_70 TPH boiler life history.xlsx | 0eaf8221f4e5 | Bagas Feeder-6 | ZIL/GSM/SP/ELCT/70 TPH/31 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 3.1 ,2.7 & 3.5 Amp
2_70 TPH boiler life history.xlsx | ed04e2fdd164 | Bagas Feeder-2 | ZIL/GSM/SP/ELCT/70 TPH/30 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 3.2 ,4.1 & 4.5 Amp
2_70 TPH boiler life history.xlsx | 3eaa98fe3cea | Bagas Feeder-1 | ZIL/GSM/SP/ELCT/70 TPH/29 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 4.5 ,4.6 & 4.9 Amp
2_70 TPH boiler life history.xlsx | 2e4ccad4bc6c | Back Wash Pump Motor | ZIL/GSM/SP/ELCT/70 TPH/28 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 8 ,7.5 & 7.7 Amp
2_70 TPH boiler life history.xlsx | b828d471a785 | Shellery Pump No-3 Motor | ZIL/GSM/SP/ELCT/70 TPH/27 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 11.5 , 12.1 & 11.7 Amp
2_70 TPH boiler life history.xlsx | fc1541a9339d | Shellery Pump No-2 Motor | ZIL/GSM/SP/ELCT/70 TPH/26 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 16.9 , 17.1 & 17.5 Amp
2_70 TPH boiler life history.xlsx | 1b21cdcf1a5a | Shellery Pump No-1 Motor | ZIL/GSM/SP/ELCT/70 TPH/25 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 9.9 , 9.4 & 8.2 Amp
2_70 TPH boiler life history.xlsx | 96cd42fc75e9 | Injection Pump No.3 Motor | ZIL/GSM/SP/ELCT/70 TPH/24 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 15.7 , 14.5 & 16.2 Amp
2_70 TPH boiler life history.xlsx | 0c0623c999d2 | Injection Pump No.2 Motor | ZIL/GSM/SP/ELCT/70 TPH/23 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 15.2 , 14.7 & 14.9 Amp
2_70 TPH boiler life history.xlsx | 2646a29ad079 | Injection Pump No.1 Motor | ZIL/GSM/SP/ELCT/70 TPH/22 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 10.1 , 9.5 & 10 Amp
2_70 TPH boiler life history.xlsx | b191a8de1096 | Soot blower LRSB No.-2 | ZIL/GSM/SP/ELCT/70 TPH/21 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 1.4 , 1.5 & 1.3 Amp
2_70 TPH boiler life history.xlsx | 7060d351d647 | Soot blower LRSB No.-1 | ZIL/GSM/SP/ELCT/70 TPH/20 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 1.1 , 1 & 1.3 Amp
2_70 TPH boiler life history.xlsx | 6c5eb0dc3ce0 | Soot blower No.-7 | ZIL/GSM/SP/ELCT/70 TPH/19 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 0.53,0.5 & 0.52 Amp
2_70 TPH boiler life history.xlsx | 393ef88b14aa | Soot blower No.-6 | ZIL/GSM/SP/ELCT/70 TPH/18 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 0.47,0.51 & 0.53 Amp
2_70 TPH boiler life history.xlsx | 62d49f38a125 | Soot blower No.-5 | ZIL/GSM/SP/ELCT/70 TPH/17 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 0.83,0.84 & 0.85 Amp
2_70 TPH boiler life history.xlsx | 8bae9acec9f2 | Soot blower No.-4 | ZIL/GSM/SP/ELCT/70 TPH/16 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 0.87,0.83 & 0.89 Amp
2_70 TPH boiler life history.xlsx | 29b933d4f4e9 | Soot blower No.-3 | ZIL/GSM/SP/ELCT/70 TPH/15 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 0.81,0.8 & 0.8 Amp
2_70 TPH boiler life history.xlsx | ada2db5c822b | Soot blower No.-2 | ZIL/GSM/SP/ELCT/70 TPH/14 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 0.51,0.51 & 0.5 Amp
2_70 TPH boiler life history.xlsx | 0be4ee47fed1 | Soot blower No.-1 | ZIL/GSM/SP/ELCT/70 TPH/13 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 0.21,0.23 & 0.21 Amp
2_70 TPH boiler life history.xlsx | 38c19e29aeac | Ash Convayer-1 | ZIL/GSM/SP/ELCT/70 TPH/12 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 5.2,5.5 & 4.9 Amp
2_70 TPH boiler life history.xlsx | dcba26f84010 | D-SUPPER HEATER PUMP-2 | ZIL/GSM/SP/ELCT/70 TPH/11 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 16.7,16.5 & 15.5 Amp
2_70 TPH boiler life history.xlsx | 48dd28b6b829 | D-SUPPER HEATER PUMP-1 | ZIL/GSM/SP/ELCT/70 TPH/10 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 13.7,14.1 & 13.5 Amp
2_70 TPH boiler life history.xlsx | 3f56fc77602f | Feed Pump Motor No.3 | ZIL/GSM/SP/ELCT/70 TPH/09 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 57,49 & 48 Amp DE side Bearing NU-316C3 Replaced Date: 14/05/2026
2_70 TPH boiler life history.xlsx | 0429b063f4dc | Feed Pump Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/08 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 50,49 & 47 Amp DE side Bearing NU-316C3 Replaced Date: 12/05/2026
2_70 TPH boiler life history.xlsx | 81be79503174 | Feed Pump Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/07 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current
2_70 TPH boiler life history.xlsx | 0e87c9ccca02 | S.A Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/06 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 78, 78 & 79 Amp. 6319 C3 Bearing DE side Replaced 18/05/2026
2_70 TPH boiler life history.xlsx | fd2130ee1788 | I.D Fan Motor No.1 | ZIL/GSM/SP/ELCT/70 TPH/05 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current
2_70 TPH boiler life history.xlsx | e4e65237b99a | I.D Fan Motor No.2 | ZIL/GSM/SP/ELCT/70 TPH/04 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current
2_70 TPH boiler life history.xlsx | 186fc1810911 | Bagas Feeder No.3 | ZIL/GSM/SP/ELCT/70 TPH/03 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 2.5, 2.7, 2.4 Amp
2_70 TPH boiler life history.xlsx | b3330b85cff6 | Bagas Feeder No. 5 | ZIL/GSM/SP/ELCT/70 TPH/02 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 4.4, 4.7, 4.5 Amp
2_70 TPH boiler life history.xlsx | 0613e2cb4be0 | Bagas Feeder No. 4 | ZIL/GSM/SP/ELCT/70 TPH/01 | Off-Season 2026 | 2026 |  |  |  | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari | No Load current 4.6, 4.7, 4.7 Amp
3_Power House life history.xlsx | 45e977a5faac | 3 MW Old alternator No.1 | ZIL/GSM/SP/ELECT/PH/01 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete overhauling done
3_Power House life history.xlsx | 2d4ca4f1c78d | 3 MW Old alternator No. 2 | ZIL/GSM/SP/ELECT/PH/02 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | External Party M/S Durga Construction
3_Power House life history.xlsx | 6b2a710f86a6 | Power house PCC | ZIL/GSM/SP/ELECT/PH/03 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete overhauling done
3_Power House life history.xlsx | 88c61735fc65 | Power house Transformer | ZIL/GSM/SP/ELECT/PH/04 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete overhauling done
3_Power House life history.xlsx | 36d90941b60e | Capacitor Panel | ZIL/GSM/SP/ELECT/PH/05 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete overhauling done
3_Power House life history.xlsx | 38607a69f3d2 | Air Conditioner | ZIL/GSM/SP/ELCT/PH/06 | Off-Season 2026 | 2026 |  |  | Repair Maintenance | Complete Motor overhauling done |  | Internal Service | Akhilesh Chaudhari
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | Season | 2023-24 |  |  | OK | OK | NO | NO | Bharat Verma / Akhilesh Yadav | Motor Stator-200 M-Ohm
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Akhilesh Yadav | Motor Stator-200 M-Ohm
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7cfff294592a | DS BATCH MC-1 | ZIL/GSM/SP/ELECT/DS/BATCH/M-01 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Akhilesh Yadav | Motor Stator-200 M-Ohm
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | OFF -Season | 2020-21 |  |  | Motor(Rotor) rewinding offer got from Kanpur, Bharat Electric work in the month of Sept.-21 | Motor Armature rewinded from Bharat Electr | 140000 | External | Bharat Verma / Akhilesh Yadav | Armature -200 M-Ohm, Field -150 M-Ohm,
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | OFF -Season | 2021-22 |  |  | OK | OK | NO | NO | Bharat Verma / Akhilesh Yadav | Armature -200 M-Ohm Field -200 M-Ohm,
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | Season | 2022-23 |  |  | Megger Value -with E-Zero | Two times motor wash with water & heating done then checked Armature megger value found Zero ofter that Motor Armature rewinded from Bharat Electrical Kanpur,in the month of OCT-2023. | 140000 | External | Vijay Chaudhary / Akhilesh Yadav | Armature -0 M-Ohm, Field -200 M-Ohm,
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | OFF -Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Akhilesh Yadav | Armature -200 M-Ohm Field -200 M-Ohm,
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | Season | 2024-25 |  |  | Spark at commutator found 03 nos carbon brush out of order. | Cleaning done and 03 nos carbon brush replaced & started. | NO | internal | Vijay Chaudhary / Akhilesh Yadav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6def177440b5 | DS BATCH MC-2 DC MOTOR | ZIL/GSM/SP/ELECT/DS/BATCH/M-02 | Season | 2025-26 |  |  | Motor(Stator) burnt during season | Motor(Stator) rewinding from Banswar Electrical,Lakhimpur | NO | NO | Vijay Chaudhary / Akhilesh Yadav | Motor Rewinding Under progress.
4_DS Electrical Equipment Life History - MOTORS.xlsx | ad2746d8f458 | DS BATCH MC-3 | ZIL/GSM/SP/ELECT/DS/BATCH/M-03 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Akhilesh Yadav | New WIL M/C installed -2025
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | Season | 2023-24 |  |  | One lead Y-phase heated at termial out side. | Repaired. | NO | Internal | Vijay Chaudhary / Abhaylal
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | Off Season | 2024 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | Off Season | 2025 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 522941d634f7 | B-CONTI MC-1 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-01 | Off Season | 2026 |  |  | Sound observed. | Both bearing replaced due to sound observed. | NO | Internal | Vijay Chaudhary / Pappu Singh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | Season | 2023-24 |  |  | One lead R-phase heated at termial out side. | Repaired. | NO | Internal | Vijay Chaudhary / Abhaylal
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | Season | 2024-25 |  |  | One lead B-phase heated at termial out side. | Repaired. | NO | Internal | Vijay Chaudhary / Abhaylal
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | Off Season | 2025 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 35fcb418488d | B-CONTI MC-2 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-02 | Off Season | 2026 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Pappu Singh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | Off Season | 2023 |  |  | Ok | Ok | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | Off Season | 2024 |  |  | Ok | Ok | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | Off Season | 2025 |  |  | Ok | Ok | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 54a769fa40d7 | B-CONTI MC-3 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-03 | Off Season | 2026 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Pappu Singh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | Off Season | 2023 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | Off Season | 2024 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | Off Season | 2025 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6788c926e1d7 | B-CONTI MC-4 | ZIL/GSM/SP/ELECT/DS/B-CONTI/M-04 | Off Season | 2026 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Pappu Singh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | Season | 2022-23 |  |  | Slip ring short link cut(B) and 03 nos carbon brush out of order | One shorting lead and 03 nos carbon brush replaced. | NO | Internal | Bharat Verma / Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | Season | 2023-24 |  |  | Slip ring one shorting lead(Y) over heated. | Repaired. | NO | Internal | Vijay Chaudhary / Abhaylal
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | Season | 2024-25 |  |  | Slip ring short link heated(Y) and 02 nos carbon brush out of order | One shorting lead and 02 nos carbon brush replaced. | NO | Internal | Vijay Chaudhary / Abhaylal
4_DS Electrical Equipment Life History - MOTORS.xlsx | 67cc6f53d340 | SPRAY-1 | ZIL/GSM/SP/ELECT/DS/SPRAY/M-01 | Season | 2025-26 |  |  | Slip ring out of order(Slip Ring 02 nos stud broken) | Slip ring stud repaired. | NO | Internal | Vijay Chaudhary / Pappu singh
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Akhilesh yadav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | Season | 2024-25 |  |  | Spark at slip ring. | Slip ring,carbon brush & carbon holder cleaning done with petrol and air & started. | NO | Internal | Vijay Chaudhary / Akhilesh yadav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec13bcd72998 | INJECTION-1 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-01 | Season | 2025-26 |  |  | Motor Burnt(Only one coil) Due to rotor rubbing in stator(Bearing sheet cut NDE side) & also bearing replaced(QJ 320 N2) | Motor repaired and bearing sheet also repaired. |  | Internal/External | Vijay Chaudhary / Akhilesh yadav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Akhilesh yadav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | Season | 2024-25 |  |  | Power cable one lead(B) heated at terminal. | Repaired. | NO | Internal | Vijay Chaudhary / Akhilesh yadav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8a1370e488c0 | INJECTION-4 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-04 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Akhilesh yadav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Akhilesh yadav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Akhilesh yadav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 294b34b0d597 | INJECTION-5 | ZIL/GSM/SP/ELECT/DS/INJECTION/M-05 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary / Akhilesh yadav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ec89beb0f12b | C-CONTI-1 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-01 | Off Season | 2026 |  |  | Sound observed DE side. | Bearing replaced. |  | Internal | Vijay Chaudhary/ Bhupendra
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | Season | 2025-26 |  |  | Motor shaft broken | Another motor provided & motor shaft repaired. | NO | Internal | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | bb397fb51401 | C-CONTI-3 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-03 | Off Season | 2026 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Bhupendra
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | Season | 2023-24 |  |  | Motor shaft broken | Another motor provided & motor shaft repaired. | NO | Internal | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | Season | 2024-25 |  |  | One lead B-phase heated at termial | Repaired. | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | d035ca63a238 | C-CONTI-4 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-04 | Off Season | 2026 |  |  | Sound observed NDE side. | Bearing replaced. |  | Internal | Vijay Chaudhary/ Bhupendra
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae9191c2f449 | C-CONTI-5 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-05 | Off Season | 2026 |  |  | Bearing inner race spot(NDE) | Bearing replaced. |  | Internal | Vijay Chaudhary/ Bhupendra
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 7f894c1cfcff | C-CONTI-6 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-06 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 297e27c093cd | C-CONTI-7 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-07 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | 06069ef28f45 | C-CONTI-9 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-09 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | Season | 2021-22 |  |  | OK | OK | NO | NO | Bharat Verma / Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | Season | 2022-23 |  |  | OK | OK | NO | NO | Bharat Verma / Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | ae1bea521916 | C-CONTI-10 | ZIL/GSM/SP/ELECT/DS/C-CONTI/M-10 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash Srivastav
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | d8508e86acff | CLEAR JUICE PUMP MOTOR-1 | ZIL/GSM/SP/ELECT/DS/CJ/M-01 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 6d1e304f8f8b | CLEAR JUICE PUMP MOTOR-2 | ZIL/GSM/SP/ELECT/DS/CJ/M-02 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 616a3e706daa | SEMI KESTNER JUICE TRANSFER -1 | ZIL/GSM/SP/ELECT/DS/SK/M-01 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 150d14d6e2b1 | SEMI KESTNER JUICE TRANSFER -2 | ZIL/GSM/SP/ELECT/DS/SK/M-02 | Off Season | 2026 |  |  | Sound observed DE side. | Bearing replaced. |  | Internal | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | Season | 2023-24 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 9ea41d709fd3 | Vapour cell juice TF pump-1 | ZIL/GSM/SP/ELECT/DS/VC/M-01 | Off Season | 2026 |  |  | Sound observed DE side. | Bearing replaced. |  | Internal | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8bfe573ffe41 | Vapour cell juice TF-2 | ZIL/GSM/SP/ELECT/DS/VC/M-02 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | bd45edf4260a | COMMON CONDENSATE-1 | ZIL/GSM/SP/ELECT/DS/CC/M-01 | Off Season | 2026 |  |  | Sound observed NDE side. | Bearing replaced. |  | Internal | Vijay Chaudhary/ Rajiv
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Akhilesh
4_DS Electrical Equipment Life History - MOTORS.xlsx | 68491d7f2ee9 | COMMON CONDENSATE-2 | ZIL/GSM/SP/ELECT/DS/CC/M-02 | Off Season | 2026 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Rajiv
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 776f1fe47a51 | FFE(2500)-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-01 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | c2527a93343d | FFE(2500)-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)/M-02 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | f7f5138c0071 | FFE(2500)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-01 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | fb6b0fce857c | FFE(2500)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(2500)T/M-02 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 3ea7585630eb | FFE(1250)-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-01 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 8b9f5f930d8c | FFE(1250)-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)/M-02 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 475d22660434 | FFE(1250)T-1 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-01 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | b6d6708cc8ad | FFE(1250)T-2 | ZIL/GSM/SP/ELECT/DS/FFE(1250)T/M-02 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Vikash
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Surendra
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Surendra
4_DS Electrical Equipment Life History - MOTORS.xlsx | 1cb9bc6f28c9 | ETP COMPRESSOR-1 | ZIL/GSM/SP/ELECT/DS/ETP C/M-01 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Surendra
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Surendra
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Surendra
4_DS Electrical Equipment Life History - MOTORS.xlsx | cddbe671aa0e | ETP COMPRESSOR-2 | ZIL/GSM/SP/ELECT/DS/ETP C/M-02 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Surendra
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | Season | 2023-24 |  |  | OK | OK | NO | Internal | Vijay Chaudhary/ Surendra
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | Season | 2024-25 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Surendra
4_DS Electrical Equipment Life History - MOTORS.xlsx | 59dff8d3563e | ETP COMPRESSOR-3 | ZIL/GSM/SP/ELECT/DS/ETP C/M-03 | Season | 2025-26 |  |  | OK | OK | NO | NO | Vijay Chaudhary/ Surendra
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | Off Season | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | Off Season | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | Off Season | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 507848044fc6 | VACUUM FILTER 14'x36' | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | Off Season | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | Off Season | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | Off Season | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | Off Season | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | ebc2f73d2f54 | VACUUM FILTER 14'x30 | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | Off Season | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | Off Season | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | Off Season | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | Off Season | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0e6b1d866a20 | Distillery W S Pump-1 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | Off Season | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | Off Season | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | Off Season | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | Off Season | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 144b3a144cb8 | Distillery W S Pump-2 | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | Off Season | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | Off Season | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | Off Season | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | Off Season | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | Season | 2025-26 |  |  | Control card out of order. | Other old VFD installed(Raw spare VFD). | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL/AKASH
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | c6c9b109879f | MOLTEN SULPHUR DOSING PUMP(E) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | Off Season | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | Off Season | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | Off Season | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | Off Season | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | be61d63bf5d0 | MOLTEN SULPHUR DOSING PUMP(W) | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | Off Season | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | Off Season | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | Off Season | 2034 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | Off Season | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 9d66c4e44b79 | AIR BLOWER NO.3 | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | Off Season | 2026 |  |  |  |  | NO | NO | Akhilesh Chaudhari/charanjit
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | Off Season | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | Off Season | 2034 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | Off Season | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 7f66c3ac4739 | CLEAR JUICE PUMP-1 | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | Off Season | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | Off Season | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | Off Season | 2034 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | Off Season | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | dfdb59e34766 | Injection Pump No.5 | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | Off Season | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | Off Season | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /VIKASH
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | Off Season | 2024 |  |  | Drive tripped at fault-short ckt-2340,two phase IGBT & BGDR card faulty(During Trial). | Replaced with new ISU module. | NO | NO | VIJAY KR CHAUDHARY /VIKASH
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | Off Season | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /VIKASH
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 0d325cf72b67 | DS 1750 WIL AC-1 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | Off Season | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL/AKASH
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | Off Season | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /VIKASH
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | Off Season | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /VIKASH
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | Off Season | 2025 |  |  | PLC out of order(During trial). | PLC ageing and DC drive control panel absoluted in market hence retrofitting of existing DC drive control panel into ABB Make with HMI,PLC and new control wiring. | NO | NO | VIJAY KR CHAUDHARY /VIKASH
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | Season | 2025-26 |  |  | Thyristor out of order. | Fault 502 Armature over current, so replaced with new and started. | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL/AKASH
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | 193d0a777007 | DS 1750 NHEC DC-2 | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | Off Season | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL/AKASH
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 | Off Season | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /Vikash | New 1750 M/C installed - 2025
5_DS Electrical Equipment Live History - VFD PANEL.xlsx | f140f6187093 | DS 1750 WIL AC-3 | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 | Off Season | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL/AKASH