## Power stopage Data
Date | start_time | end_Time | section | sub_section | machinery | category | remarks | created_at | timestamp
2023-12-14 | 2023-12-14 05:31 | 2023-12-14 05:32 | Others | 132 KV TRANSMISSION LINE | Others | Electrical | A - 30 MW STG Grid breaker auto tripped at 05:31 AM due to heavy jerk observed from grid side, STG sync. with grid at 05:32 AM. | 2023-12-15 11:16 | 2023-12-15 11:16
2023-12-25 | 2023-12-25 10:27 | 2023-12-25 19:05 | 3MW Turbine (Old) | OTHERS | Others | Other | 3 MW Old_STG set stopped at 10:27 AM due to Schedule General Cleaning of Mill. STG set started and synch. with Grid at 07:05PM | 2023-12-26 18:00 | 2023-12-26 18:00
2023-12-25 | 2023-12-25 10:25 | 2023-12-25 19:30 | 3MW Turbine (New) | OTHERS | Others | Other | 3 MW NEW_STG set stopped at 10:25 AM due to Schedule General Cleaning of Mill. STG set started and taken in load at 07:30PM | 2023-12-26 18:01 | 2023-12-26 18:01
2023-12-31 | 2023-12-31 03:18 | 2023-12-31 03:22 | Others | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 03:18 AM due to heavy jerk observed from grid side, STG sync. with grid at 03:22 AM. | 2024-01-01 18:07 | 2024-01-01 18:07
2024-01-03 | 2024-01-03 08:36 | 2024-01-03 08:38 | 30.85 MW Turbine | OTHERS | Sub-Station | Electrical | 30 MW STG Grid breaker auto tripped at 08:36 AM due to heavy jerk observed from Grid on a/c of tripping of 33 KV Beltuwa feeder from Dhaurahara Substation, Again STG sync. with Grid at 08:38 AM. | 2024-01-06 11:16 | 2024-01-06 11:16
2024-01-04 | 2024-01-04 13:19 | 2024-01-04 13:24 | Grid | 132 KV TRANSMISSION LINE | Sub-Station | Electrical | 30 MW STG Grid breaker manually opened at 01:19PM to 01:24PM due to Grid changeover from Dhaurahara S/S on a/c of Shutdown taken by UPPTCL for B - Phase Line Isolator Jaw Contact replacement of 132 KV Dhaurahara - Nighashan Tr. Line at Nighashan Substation. | 2024-01-06 13:10 | 2024-01-06 13:10
2024-01-04 | 2024-01-04 14:36 | 2024-01-04 14:39 | Grid | 132 KV TRANSMISSION LINE | Sub-Station | Electrical | 30 MW STG Grid breaker manually opened at 02:36PM to 02:39PM due to Grid changeover from Dhaurahara S/S on a/c of Shutdown taken by UPPTCL for B - Phase Line Isolator Jaw Contact replacement of 132 KV Dhaurahara - Nighashan Tr. Line at Nighashan S/S. | 2024-01-06 13:12 | 2024-01-06 13:12
2024-01-04 | 2024-01-04 22:43 | 2024-01-04 22:49 | Grid | 132 KV TRANSMISSION LINE | Sub-Station | Electrical | 30 MW STG Grid breaker auto tripped at 10:43PM due to grid failed on a/c of tripping of 132KV Dhaurahara - GSMA Tr. line from Dhaurahar Substation, Grid resumed & Synch with GRID at 10:49PM. | 2024-01-06 13:14 | 2024-01-06 13:14
2024-01-04 | 2024-01-04 22:48 | 2024-01-04 23:05 | 150 TPH Boiler | OTHERS | Others | Other | 150TPH Boiler tripped at 10:48 PM on negative furnace draft (-80mmWC) and all bagasse feeder tripped caused Boiler steam pressure low resulting stoppage of Mill for 17Mts. | 2024-01-06 13:20 | 2024-01-06 13:20
2024-01-04 | 2024-01-04 07:48 | 2024-01-04 07:49 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 07:48 AM due to heavy jerk observed from Grid side, Again STG sync. with Grid at 07:49 AM. | 2024-01-06 13:23 | 2024-01-06 13:23
2024-01-07 | 2024-01-07 09:18 | 2024-01-07 09:19 | Grid | OTHERS | Others | Electrical | 30 MW STG GRID breaker auto tripped at 09:18 AM due to heavy jerk observed from Grid on a/c of tripping of 132 KV Bajaj Energy Gola Tr. Line from Nighashan Substation, Again STG sync. with Grid at 09:19 AM. | 2024-01-08 12:00 | 2024-01-08 12:00
2024-01-13 | 2024-01-14 07:43 | 2024-01-14 07:44 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 07:43 AM due to heavy jerk observed from grid side on a/c of tripping of 33KV Kailashpuri feeder from Dhaurahra substation , Again STG sync. with grid at 07:44 AM. | 2024-01-14 15:54 | 2024-01-14 15:54
2024-01-16 | 2024-01-16 10:38 | 2024-01-16 15:05 | 35 TPH Boiler & 4MW Turbine | FURNACE | Others | Other | 4 MW STG set manually tripped at 10:38 AM due to main steam pressure low on a/c of disturbance in furnace due to slop, again STG sync. with Grid at 03:05 PM. | 2024-01-20 13:02 | 2024-01-20 13:02
2024-01-17 | 2024-01-17 12:33 | 2024-01-17 16:51 | 35 TPH Boiler & 4MW Turbine | BOILER FANS | ID Fan | Mechanical | 4.0 MW STG set & Boiler stopped at 12:33 PM due to ID Fan impeller cleaning & checking , Again STG Set Sync with Grid at 04:51 PM. | 2024-01-20 13:05 | 2024-01-20 13:05
2024-01-17 | 2024-01-17 09:35 | 2024-01-20 00:24 | 150 TPH Boiler | OTHERS | Others | Mechanical | 30MW STG set stopped at 09:35 AM due to shutdown of 150TPH Boiler to attend flue gas leakage and STG set started & Synch. with GRID on dated 20/01/2024 at 12:24AM. | 2024-01-20 13:10 | 2024-01-20 13:10
2024-01-21 | 2024-01-21 11:02 | 2024-01-21 11:04 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 11:02 AM due to heavy jerk observed from grid side , Again STG sync. with grid at 11:04 AM. | 2024-01-22 11:53 | 2024-01-22 11:53
2024-01-23 | 2024-01-23 16:55 | 2024-01-23 16:56 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 04:55 PM due to heavy jerk observed from grid side on a/c of tripping of 33KV Kailashpuri feeder from Dhaurahra substation , Again STG sync. with grid at 04:56 PM. | 2024-01-27 12:50 | 2024-01-27 12:50
2024-01-25 | 2024-01-25 13:46 | 2024-01-25 13:47 | Grid | OTHERS | Others | Electrical | 30MW STG Grid breaker auto tripped at 01:46 PM due to heavy jerk observed from grid side on a/c of tripping of 33KV Kailashpuri feeder from Dhaurahra substation , Again STG sync. with grid at 01:47 PM. | 2024-01-27 12:58 | 2024-01-27 12:58
2024-01-25 | 2024-01-26 02:20 | 2024-01-26 02:21 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 02:20 AM due to heavy jerk observed from grid side Again STG sync. with grid at 02:21AM. | 2024-01-27 13:00 | 2024-01-27 13:00
2024-01-29 | 2024-01-29 09:30 | 2024-01-29 05:04 | 35 TPH Boiler | BOILER FANS | ID Fan | Mechanical | 4MW STG set & Boiler stopped at 09:30 AM due to ID Fan Vibration level increased on a/c of slop ash deposited on ID Fan Impeller caused unbalanced & abnormal sound at bearing , Again STG Set Sync with Grid at 05:04 AM. | 2024-02-01 19:59 | 2024-02-01 19:59
2024-02-01 | 2024-02-01 17:13 | 2024-02-01 17:15 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 05:13 PM due to heavy jerk observed from grid side on a/c of bad weather condition, STG sync. with grid at 05:15 PM. | 2024-02-04 18:00 | 2024-02-04 18:00
2024-02-05 | 2024-02-05 10:18 | 2024-02-05 10:19 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 10:18 AM due to heavy jerk observed from grid on a/c of tripping of 33KV beltua-Khamariya feeder from Dhaurahra Substtation , Again STG sync. with grid at 10:19 AM. | 2024-02-08 20:30 | 2024-02-08 20:30
2024-02-06 | 2024-02-06 19:57 | 2024-02-06 19:58 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 07:57 PM due to heavy jerk observed from grid on a/c of tripping of 33KV beltua-Khamariya feeder from Dhaurahra Substation , Again STG sync. with grid at 07:58 PM. | 2024-02-08 20:32 | 2024-02-08 20:32
2024-02-08 | 2024-02-08 09:59 | 2024-02-08 06:06 | 150 TPH Boiler | OTHERS | Others | Mechanical | 30 MW STG set & 150 TPH Boiler manually stopped at 09:59AM due to DA Fan air duct connectivity , again STG set started & synced with grid at 06:06PM . | 2024-02-09 19:28 | 2024-02-09 19:28
2024-02-12 | 2024-02-13 00:21 | 2024-02-13 00:33 | Grid | OTHERS | Others | Electrical | 30MW STG set GRID breaker auto tripped at 12:21AM due to 132KV Dhaurahara Substation blackout on a/c of tripping of 132KV Dhaurahara - Nighasan Tr. line from Nighashan S/S, Again STG Sync with GRID at 12:33AM. | 2024-02-16 18:47 | 2024-02-16 18:47
2024-02-15 | 2024-02-15 11:34 | 2024-02-15 15:29 | 35 TPH Boiler | BOILER FANS | ID Fan | Mechanical | 4 MW STG Set & Boiler stopped at 11:34 AM due to ID Fan Vibration level increased on a/c of slop ash deposited on ID Fan Impeller, Again STG Set Sync with Grid at 03:29 PM. | 2024-02-16 18:50 | 2024-02-16 18:50
2024-02-16 | 2024-02-17 03:20 | 2024-02-17 03:21 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 03:20AM due to heavy jerk observed from grid side on a/c of tripping of 33KV Beltuwa feeder from Dhaurahra substation , Again STG sync. with grid at 03:21AM. | 2024-02-17 18:32 | 2024-02-17 18:32
2024-02-19 | 2024-02-19 15:35 | 2024-02-19 19:25 | 35 TPH Boiler | BAGASSE FEEDING SYSTEM | Screw Feeder-1 | Mechanical | 4MW STG Set manually Stopped at 03:35PM due to LSP on a/c of bagasse feeder no -1 & 2 jammed and steam given to distillery for process from 150TPH Boiler. Again STG synch with grid at 07:25PM | 2024-02-24 18:22 | 2024-02-24 18:22
2024-02-21 | 2024-02-22 01:02 | 2024-02-22 01:11 | Grid | OTHERS | Others | Electrical | 30 MW GRID breaker auto tripped at 01:02AM due to Dhaurahra substation blackout on account of 132KV Dhaurahra - Nighasan Tr. Line tripped. Grid resumed at 01:11AM & STG synch with grid at 01:13AM | 2024-02-24 18:25 | 2024-02-24 18:25
2024-02-21 | 2024-02-22 00:10 | 2024-02-22 03:20 | 35 TPH Boiler | BOILER FANS | ID Fan | Mechanical | 4 MW STG Set & Boiler stopped at 12:10 AM due to ID Fan Vibration level increased on a/c of slop ash deposited on ID Fan Impeller, Again STG Set started and Sync with Grid at 03:20 AM. | 2024-02-24 18:28 | 2024-02-24 18:28
2024-02-27 | 2024-02-27 09:51 | 2024-02-27 11:52 | 35 TPH Boiler | BOILER FANS | ID Fan | Mechanical | 4 MW STG Set & 35 TPH Boiler stopped at 09:51 AM due to ID Fan Vibration level increased on a/c of slop ash deposited on ID Fan Impeller, Again STG Set started and Sync with Grid at 01:33 PM. | 2024-03-07 11:55 | 2024-03-07 11:55
2024-03-01 | 2024-03-01 10:16 | 2024-03-01 10:18 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 10:16AM due to heavy jerk observed from grid side on a/c of tripping of 33KV Kailaspuri Rural feeder , Again STG set sync. with grid at 10:18AM. | 2024-03-07 11:59 | 2024-03-07 11:59
2024-03-01 | 2024-03-01 08:20 | 2024-03-01 22:10 | 3MW Turbine (Old) | MILL - GENERAL CLEANING | Others | Electrical | 3MW_ Old STG set stopped at 08:20 AM due to Schedule General cleaning of Mill & attending of 70TPH Boiler Economiser tube leakage , Again STG set started & Sync with grid at 10:10PM. | 2024-03-07 12:02 | 2024-03-07 12:02
2024-03-01 | 2024-03-01 08:06 | 2024-03-01 22:40 | 3MW Turbine (New) | MILL - GENERAL CLEANING | Others | Electrical | 3MW_ New STG set stopped at 08:06 AM due to Schedule General cleaning of Mill & attending of 70TPH Boiler Economiser tube leakage , Again STG set started & taken at load at 10:40PM. | 2024-03-07 12:04 | 2024-03-07 12:04
2024-03-02 | 2024-03-02 16:05 | 2024-03-02 16:08 | Grid | OTHERS | Others | Electrical | 30MW STG GRID Breaker manually opened at 04:05 PM tripping system checking by UPPTCL staff of ZIL feeder , Again STG set synced with grid at 04:08PM . | 2024-03-07 12:06 | 2024-03-07 12:06
2024-03-03 | 2024-03-03 15:03 | 2024-03-03 16:47 | 35 TPH Boiler | BOILER FANS | ID Fan | Mechanical | 4 MW STG Set & 35 TPH Boiler stopped at 03:03 PM due to ID Fan Vibration level increased on a/c of slop ash deposited on ID Fan Impeller, Again STG Set started and Sync with Grid at 04:47 PM. | 2024-03-07 12:08 | 2024-03-07 12:08
2024-03-07 | 2024-03-07 15:15 | 2024-03-07 15:18 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 03:15 PM due to heavy jerk observed from grid on a/c of tripping of 33KV Beltuwa feeder from Dhaurahra substation , Again STG sync. with grid at 03:18 PM. | 2024-03-09 17:53 | 2024-03-09 17:53
2024-03-07 | 2024-03-07 15:23 | 2024-03-07 15:24 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 03:23 PM due to heavy jerk observed from grid on a/c of tripping of 33KV Beltuwa feeder from Dhaurahra substation , Again STG sync. with grid at 03:24 PM. | 2024-03-09 17:54 | 2024-03-09 17:54
2024-03-07 | 2024-03-07 14:29 | 2024-03-07 16:44 | 35 TPH Boiler | BOILER FANS | ID Fan | Mechanical | 4 MW STG Set & 35 TPH Boiler stopped at 02:29 PM due to ID Fan Vibration level increased on a/c of slop ash deposited on ID Fan Impeller, Again STG Set started and Sync with Grid at 04:44 PM. | 2024-03-09 17:56 | 2024-03-09 17:56
2024-03-08 | 2024-03-08 11:25 | 2024-03-09 08:00 | 35 TPH Boiler | OTHERS | Others | Mechanical | 35TPH Boiler and 4MW STG set Stopped at 11:25 AM for Boiler internal cleaning. | 2024-03-09 18:10 | 2024-03-09 18:10
2024-03-09 | 2024-03-09 08:00 | 2024-03-10 08:00 | 35 TPH Boiler | OTHERS | Others | Mechanical | 35TPH Boiler and 4MW STG set Stopped for Boiler internal cleaning. | 2024-03-10 11:55 | 2024-03-10 11:55
2024-03-10 | 2024-03-10 08:00 | 2024-03-11 08:00 | 35 TPH Boiler | OTHERS | Others | Mechanical | 35TPH Boiler and 4MW STG set Stopped for Boiler internal cleaning. | 2024-03-13 11:25 | 2024-03-13 11:25
2024-03-11 | 2024-03-11 08:00 | 2024-03-12 08:00 | 35 TPH Boiler | OTHERS | Others | Mechanical | a) 35TPH Boiler light up at 1:25AM & Steam Given to Distillery at 6:45AM. b) Steam given to Distillery Plant at 6:45AM. | 2024-03-13 11:31 | 2024-03-13 11:31
2024-03-12 | 2024-03-12 08:00 | 2024-03-12 08:10 | 35 TPH Boiler | OTHERS | Others | Mechanical | 4MW STG Set Started & Sync with Grid at 8:10AM. | 2024-03-13 11:32 | 2024-03-13 11:32
2024-03-16 | 2024-03-16 23:07 | 2024-03-16 23:08 | Grid | OTHERS | Others | Electrical | 30 MW STG Tie breaker auto tripped at 11:07 PM due to heavy jerk observed from grid side , STG sync. with grid at 11:08 PM. | 2024-03-18 10:18 | 2024-03-18 10:18
2024-03-20 | 2024-03-20 13:19 | 2024-03-20 13:20 | Grid | OTHERS | Others | Electrical | 30 MW STG Tie breaker auto tripped at 01:19 PM due to heavy jerk observed from grid side , STG sync. with grid at 01:20 PM. | 2024-04-14 16:27 | 2024-04-14 16:27
2024-03-20 | 2024-03-20 16:02 | 2024-03-20 16:03 | Grid | OTHERS | Others | Electrical | 30 MW STG Tie breaker auto tripped at 04:02 PM due to heavy jerk observed from grid side , STG sync. with grid at 04:03 PM. | 2024-04-14 16:28 | 2024-04-14 16:28
2024-03-27 | 2024-03-27 08:58 | 2024-03-28 01:03 | 35 TPH Boiler & 4MW Turbine | FURNACE | ID Fan | Mechanical | 4MW STG Breaker manually opened at 08:58AM for cleaning of choked second pass hopper of 35 TPH slop fired Boiler. STG set started after cleaning hopper & ID Fan Impeller and Sync. with GRID at 01:03AM. | 2024-04-14 16:34 | 2024-04-14 16:34
2024-04-02 | 2024-04-02 19:57 | 2024-04-08 10:57 | 35 TPH Boiler | OTHERS | Others | Mechanical | 35TPH Boiler and 4MW STG stopped at 07:57pm for Schedule cleaning of Boiler . | 2024-04-14 16:39 | 2024-04-14 16:39
2024-04-06 | 2024-04-06 11:29 | 2024-04-06 11:30 | Grid | OTHERS | Others | Electrical | 30 MW STG Tie breaker auto tripped at 11:29 AM due to heavy jerk observed from grid side , STG sync. with grid at 11:30 AM. | 2024-04-14 16:41 | 2024-04-14 16:41
2024-04-08 | 2024-04-09 00:20 | 2024-04-09 00:21 | Grid | OTHERS | Others | Electrical | 30MW STG GRID breaker auto tripped at 12:20AM due to heavy jerk from grid side, again STG set sync with GRID at 12:21AM . | 2024-04-14 16:44 | 2024-04-14 16:44
2024-04-10 | 2024-04-10 18:57 | 2024-04-10 18:58 | Grid | OTHERS | Others | Electrical | 30 MW STG GRID breaker auto tripped at 06:57 PM due to heavy jerk observed from grid side , Again STG set sync. with grid at 06:58 PM. | 2024-04-14 16:45 | 2024-04-14 16:45
2024-04-13 | 2024-04-14 02:30 | 2024-04-14 02:35 | Grid | OTHERS | Others | Electrical | 30.85 STG Grid breaker auto tripped at 02:30AM due to heavy jerk observed from grid side and again sync with grid at 02:35AM . | 2024-04-14 16:47 | 2024-04-14 16:47
2024-04-05 | 2024-04-06 04:21 | 2024-04-06 05:08 | Grid | 132 KV TRANSMISSION LINE | Transmission Line | Electrical | 30 MW GRID breaker auto tripped at 04:21AM due to 132 KV Dhaurhar S/S blackout on a/c of tripping of 132KV Dhaurahra - Nighasan Tr. Line from Nighasan s/s. Grid resumed at 05:08AM & STG synch with grid at 05:08AM | 2024-04-14 16:50 | 2024-04-14 16:50
2024-11-24 | 2024-11-24 19:29 | 2024-11-24 19:33 | Grid | OTHERS | Others | Electrical | GRID Breaker auto tripped at 07:29PM due to grid fluctuation on account of tripping of 33 KV Beltua feeder from Dhaurahra substation. Again STG synch with grid at 07:33PM. | 2024-11-25 11:48 | 2024-11-25 11:48
2024-11-20 | 2024-11-20 11:43 | 2024-11-20 14:28 | 30.85 MW Turbine | TURBINE & GENERATOR | LP Actuator | Instrumentation | 30 MW STG set manually stopped at 11:43AM due to LP Actuator replacement, STG sync with Grid at 02:28PM. | 2024-11-25 11:53 | 2024-11-25 11:53
2024-11-19 | 2024-11-19 20:38 | 2024-11-19 20:39 | Grid | OTHERS | Others | Electrical | 30MW GRID Breaker auto tripped at 08:38PM due to heavy jerk observed from grid ,Again STG Sync. with Grid at 08:39PM. | 2024-11-25 11:55 | 2024-11-25 11:55
2024-11-18 | 2024-11-18 19:10 | 2024-11-18 19:11 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | 30MW STG Set GRID Breaker auto tripped at 07:10PM.due to heavy jerk observed from Grid on a/c of 132KV Palia Tr. Line tripped from Nighasan substation.Again STG Sync. with Grid at 07:11PM. | 2024-11-25 11:56 | 2024-11-25 11:56
2024-11-17 | 2024-11-17 09:04 | 2024-11-17 09:48 | 35 TPH Boiler | FUEL HANDLING SYSTEM | Dist Belt Conveyor-1 (DBC-1) | Mechanical | 4MW STG Breaker manually open at 09:04AM due to Bagasse jammed DBC-1 discharge chute ,again STG synch.with GRID at 09:48AM. | 2024-11-25 11:59 | 2024-11-25 11:59
2024-11-17 | 2024-11-18 04:38 | 2024-11-18 04:39 | Grid | OTHERS | Others | Electrical | 30MW GRID Breaker auto tripped at 04:38AM due to heavy jerk observed from grid ,Again STG Sync. with Grid at 04:39AM. | 2024-11-25 12:00 | 2024-11-25 12:00
2024-11-13 | 2024-11-13 11:13 | 2024-11-13 11:22 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | 30MW GRID Breaker manually tripped at 11:13AM to 11:22AM due to grid changeover from Dhaurahra substation. | 2024-11-25 12:02 | 2024-11-25 12:02
2024-11-13 | 2024-11-13 17:57 | 2024-11-13 18:07 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | 30MW GRID Breaker manually tripped at 05:57PM to 06:07PM due to grid changeover from Dhaurahra substation. | 2024-11-25 12:04 | 2024-11-25 12:04
2024-11-13 | 2024-11-13 23:10 | 2024-11-14 00:02 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | 30MW GRID Breaker Auto tripped at 11:10PM due to GSML transmission line tripped from dhaurahra substation. Grid supply resumed at 12:01AM and again STG Sync. with Grid at 12:02AM. | 2024-11-25 12:05 | 2024-11-25 12:05
2024-11-12 | 2024-11-13 06:39 | 2024-11-13 06:50 | Grid | OTHERS | Others | Electrical | 30MW GRID Breaker auto tripped at 06:39AM due to heavy jerk observed from grid ,Again STG Sync. with Grid at 06:50AM. | 2024-11-25 12:07 | 2024-11-25 12:07
2024-11-10 | 2024-11-11 06:00 | 2024-11-11 06:02 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | 30MW STG Set GRID Breaker auto tripped at 06:00AM due to heavy jerk observed from Grid on a/c of 220KV kandauli Tr. Line tripped from Nighasan substation. | 2024-11-25 12:08 | 2024-11-25 12:08
2024-11-07 | 2024-11-08 04:56 | 2024-11-08 05:19 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | 30MW STG Set GRID Breaker auto tripped at 04:56AM due to 132KV Dhaurhara Substation blackout on a/c of 132KV Dhaurhara -Nighasan Tr. Line tripped from Nighasan substation ,Grid Resume & STG Sync. With Grid at 05:19AM. | 2024-11-25 12:10 | 2024-11-25 12:10
2024-11-04 | 2024-11-05 01:17 | 2024-11-05 16:07 | 35 TPH Boiler | OTHERS | Furnace Tubes | Mechanical | 35TPH Boiler and 4MW STG stopped at 01:17AM due to Boiler tube leakage. | 2024-11-25 12:14 | 2024-11-25 12:14
2024-11-02 | 2024-11-02 18:24 | 2024-11-02 18:25 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 06:24PM due to heavy jerk observed from grid side, STG synch. with grid at 06:25PM. | 2024-11-25 12:15 | 2024-11-25 12:15
2024-11-01 | 2024-11-02 06:24 | 2024-11-02 06:26 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 06:24AM due to heavy jerk observed from grid side, STG synch. with grid at 06:26AM. | 2024-11-25 12:16 | 2024-11-25 12:16
2024-10-28 | 2024-10-28 17:13 | 2024-10-30 13:00 | 150 TPH Boiler | OTHERS | Furnace Tubes, Boiler Bank, super Heater & Eco | Mechanical | 30 MW STG set & 150TPH Boiler manually stopped at 05:13 PM due to Tube Leakage ecnomiser outlet below LTSH Header. | 2024-11-25 12:20 | 2024-11-25 12:20
2024-10-29 | 2024-10-29 22:15 | 2024-10-29 23:26 | 35 TPH Boiler | FUEL HANDLING SYSTEM | Dist Belt Conveyor-1 (DBC-1) | Mechanical | 4MW STG manually Open at 10:15PM due to Bagasse Jamm in DBC-1 ,again STG synch.with GRID at 11:26 PM. | 2024-11-25 12:25 | 2024-11-25 12:25
2024-10-27 | 2024-10-28 01:11 | 2024-10-28 01:13 | Grid | OTHERS | Others | Electrical | 30 MW STG Grid breaker auto tripped at 01:11 AM to 01:13AM due to heavy jerk observed from grid side. | 2024-11-25 12:27 | 2024-11-25 12:27
2024-11-25 | 2024-11-26 03:08 | 2024-11-26 03:09 | Grid | OTHERS | Others | Electrical | GRID Breaker auto tripped at 03:08AM to 03:09AM due to heavy jerk observed from grid side. | 2024-11-29 12:22 | 2024-11-29 12:22
2024-11-25 | 2024-11-26 06:34 | 2024-11-26 06:35 | Grid | OTHERS | Others | Electrical | GRID Breaker auto tripped at 6:34AM to 06:35AM due to heavy jerk observed from grid side. | 2024-11-29 12:23 | 2024-11-29 12:23
2024-11-26 | 2024-11-27 03:07 | 2024-11-27 03:08 | Grid | OTHERS | Others | Electrical | 30MW GRID Breaker auto tripped at 03:07AM due to heavy jerk observed from grid ,Again STG Sync. with Grid at 03:08AM. | 2024-11-29 12:25 | 2024-11-29 12:25
2024-11-29 | 2024-11-29 17:39 | 2024-11-29 17:40 | Grid | OTHERS | Others | Electrical | 30MW GRID Breaker auto tripped at 05:39PM due to heavy jerk observed from grid ,Again STG Sync. with Grid at 05:40PM. | 2024-11-30 17:49 | 2024-11-30 17:49
2024-12-06 | 2024-12-07 01:16 | 2024-12-07 01:28 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | 30MW GRID Breaker auto tripped at 01:16AM due to GSMA Transmission line tripped from Dhaurahra substation. Grid supply resumed & STG Sync. with Grid at 01:28AM. | 2024-12-07 17:11 | 2024-12-07 17:11
2024-12-07 | 2024-12-07 09:39 | 2024-12-07 11:15 | 3MW Turbine (Old) | OTHERS | Others | Electrical | 3MW old STG set tripped at 09:39AM due to Voltage fluctuation which was synch with grid ,STG set started & synch with GRID at 11:15AM . | 2024-12-10 11:00 | 2024-12-10 11:00
2024-12-07 | 2024-12-07 11:39 | 2024-12-07 12:15 | 3MW Turbine (New) | OTHERS | Others | Electrical | 3MW old STG set & 2.5MVA Transformer tripped at 11:39AM on overload due to which 3MW New STG set tripped because of 70TPH boiler Aux equipments supply failure, system restore at 12:15PM. | 2024-12-10 11:02 | 2024-12-10 11:02
2024-12-11 | 2024-12-12 00:18 | 2024-12-12 00:19 | Grid | OTHERS | Others | Electrical | 30MW GRID Breaker auto tripped at 12:18AM due to heavy jerk observed from grid ,Again STG Sync. with Grid at 12:19AM. | 2024-12-15 18:49 | 2024-12-15 18:49
2024-12-12 | 2024-12-12 09:42 | 2024-12-12 16:20 | 3MW Turbine (Old) | MILL - GENERAL CLEANING | Others | Other | 3 MW Old_STG set stopped at 09:42 AM due to Schedule General Cleaning of Mill. STG set started and synch. with Grid at 04:20PM | 2024-12-15 18:51 | 2024-12-15 18:51
2024-12-12 | 2024-12-12 09:18 | 2024-12-12 17:13 | 3MW Turbine (New) | OTHERS | Others | Other | 3 MW NEW_STG set stopped at 09:18 AM due to Schedule General Cleaning of Mill. STG set started and taken in load at 05:13PM | 2024-12-15 18:52 | 2024-12-15 18:52
2024-12-15 | 2024-12-15 10:46 | 2024-12-15 12:30 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | 30.85 MW GRID Breaker manually tripped at 10:46AM to 12:30PM due to grid changeover from Dhaurahra substation and also during grid changeover 132KV Nanpara End SF6 breaker failure caused delay to resume grid supply. | 2024-12-16 10:56 | 2024-12-16 10:56
2024-12-18 | 2024-12-19 06:20 | 2024-12-19 07:10 | 30.85 MW Turbine | OIL PUMP | Auxillery Oil Pump-2 (AOP-2) | Other | 30MW STG SET Turbine Auto Tripped at 06:20AM due to Control oil pressure Low. Again STG set Sync with Grid at 07:10 AM. | 2024-12-21 18:53 | 2024-12-21 18:53
2024-12-30 | 2024-12-30 19:30 | 2024-12-30 19:40 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | 30MW GRID Breaker auto tripped at 07:30PM due to Dhaurahra- Nighasan Transmission line tripped from Dhaurahra substation. Grid supply resumed & STG .Sync. with Grid at 07:40PM. | 2025-01-02 18:54 | 2025-01-02 18:54
2024-12-31 | 2024-12-31 13:48 | 2024-12-31 13:58 | Grid | OTHERS | Others | Electrical | GRID Breaker auto tripped at 01:48PM to 01:58PM due to heavy jerk observed from grid side. | 2025-01-02 18:55 | 2025-01-02 18:55
2024-12-31 | 2024-12-31 17:29 | 2024-12-31 17:30 | Grid | OTHERS | Others | Electrical | GRID Breaker auto tripped at 05:29PM to 05:30PM due to heavy jerk observed from grid side. | 2025-01-02 18:56 | 2025-01-02 18:56
2025-01-01 | 2025-01-01 18:15 | 2025-01-01 19:53 | 3MW Turbine (Old) | OTHERS | Others | Electrical | 3MW_OLD STG auto tripped at 06:15Pm at Voltage control over current relay acted due to GRID fluctuation . Again STG started & synch with grid at 07:53PM. | 2025-01-02 18:59 | 2025-01-02 18:59
2025-01-01 | 2025-01-01 19:06 | 2025-01-01 20:29 | 3MW Turbine (New) | FUEL HANDLING SYSTEM | Main Bagasse Carrier (MBC) | Electrical | 3MW_NEW STG manually stopped at 07:06PM due to 70TPH Boiler steam pressure low on account of MBC conveyor tripped during 3MW_old STG set synchronization. Again STG taken in line at 08:29PM. | 2025-01-02 19:01 | 2025-01-02 19:01
2024-12-23 | 2024-12-24 05:46 | 2024-12-24 05:48 | Grid | OTHERS | Others | Electrical | Grid Breaker auto tripped at 05:46AM due to heavy jerk observed from grid side. Again STG synced with grid at 05:48AM . | 2025-01-02 19:05 | 2025-01-02 19:05
2025-01-02 | 2025-01-03 05:03 | 2025-01-03 07:30 | 3MW Turbine (Old) | OTHERS | Others | Electrical | 3MW_OlD STG stopped at 05:03AM due to Boiler LSP low on account of cable fault of boiler MCC panel occurs boiler auxiliary failed, Again 3MW_OLD STG started & synch with grid at 07:30AM. | 2025-01-05 12:49 | 2025-01-05 12:49
2025-01-02 | 2025-01-03 05:10 | 2025-01-03 19:26 | 3MW Turbine (New) | OTHERS | Others | Electrical | 3MW_NEW STG stopped at 05:10AM due to Boiler LSP low on account of cable fault of boiler MCC panel occurs boiler auxiliary failed. 3 MW NEW_STG set started and taken on load at 07:26PM | 2025-01-05 12:51 | 2025-01-05 12:51
2025-01-03 | 2025-01-03 09:40 | 2025-01-03 14:43 | 150 TPH Boiler | FUEL HANDLING SYSTEM | Slat chain Conveyor | Mechanical | 30.85MW STG manually stopped at 09:04AM due to bagasse accumulated at slate chain conveyor on a/c of fluid coupling failure , again STG set started & synch with GRID at 02:43PM . | 2025-01-05 12:53 | 2025-01-05 12:53
2025-01-03 | 2025-01-03 13:40 | 2025-01-03 19:03 | 3MW Turbine (Old) | MILL - GENERAL CLEANING | Others | Electrical | 3 MW Old_STG set stopped at 01:40 PM to 07:03PM for Schedule General Cleaning of Mill. | 2025-01-05 12:54 | 2025-01-05 12:54
2025-01-07 | 2025-01-08 03:39 | 2025-01-08 03:46 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | 30.85MW GRID breaker auto tripped at 03:39AM due to 132 KV GSMA Tr. line tripped from Dhaurhara Substation, again STG Sync. with GRID at 03:46AM . | 2025-01-09 16:10 | 2025-01-09 16:10
2025-01-07 | 2025-01-08 04:47 | 2025-01-08 05:01 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | 30.85MW STG GRID breaker auto tripped at 04:47AM due to Grid failure from Nighasan Substation because 132KV Dhaurahra Nighasan Tr. line tripped . Grid resumed and STG sync with Grid at 05:01 AM . | 2025-01-09 16:11 | 2025-01-09 16:11
2025-01-09 | 2025-01-09 16:20 | 2025-01-09 17:06 | 3MW Turbine (Old) | TURBINE & GENERATOR | Others | Electrical | 3MW_OLD STG stopped at 04:20PM due to Governor KW Transducer replacement , Again 3MW_OLD STG started & sync. with grid at 05:06PM. | 2025-01-10 12:48 | 2025-01-10 12:48
2025-01-14 | 2025-01-15 03:56 | 2025-01-15 03:58 | Grid | OTHERS | Others | Electrical | 30.85 MW STG set Grid Breaker auto tripped at 03:56AM due to heavy jerk observed from grid side. Again STG synced with grid at 03:58AM . | 2025-01-16 09:52 | 2025-01-16 09:52
2025-01-28 | 2025-01-28 13:12 | 2025-01-28 13:13 | Grid | OTHERS | Others | Electrical | 30MW GRID Breaker auto tripped at 01:12PM due to heavy jerk observed from grid side ,Again STG Sync. with Grid at 01:13PM. | 2025-01-29 13:34 | 2025-01-29 13:34
2025-01-28 | 2025-01-28 09:48 | 2025-01-28 17:11 | 3MW Turbine (Old) | MILL - GENERAL CLEANING | Others | Other | 3 MW Old_STG set stopped at 09:48 AM to 05:11PM for Schedule General Cleaning of Mill. | 2025-01-29 13:36 | 2025-01-29 13:36
2025-01-28 | 2025-01-28 09:19 | 2025-01-28 17:31 | 3MW Turbine (New) | MILL - GENERAL CLEANING | Others | Other | 3 MW NEW_STG set stopped at 09:19AM to 05:31PM for Schedule General Cleaning of Mill. | 2025-01-29 13:37 | 2025-01-29 13:37
2025-01-29 | 2025-01-29 21:15 | 2025-01-30 12:02 | 4MW Turbine | COOLING WATER SYSTEM | Others | Mechanical | 4MW STG set Stopped at 09:15PM due to Generator cooler leakage and Sync with grid at 12:02PM | 2025-02-01 16:50 | 2025-02-01 16:50
2025-02-14 | 2025-02-15 04:48 | 2025-02-15 05:01 | 35 TPH Boiler & 4MW Turbine | FUEL HANDLING SYSTEM | Dist Belt Conveyor-1 (DBC-1) | Mechanical | 4MW STG Breaker manually opened at 04:48AM due to LSP on a/c of Bagasse jammed on DBC-1 discharge chute ,again STG set synch.with GRID at 05:10AM. | 2025-02-16 11:29 | 2025-02-16 11:29
2025-03-02 | 2025-03-02 12:59 | 2025-03-02 13:01 | Grid | OTHERS | Others | Electrical | 30.85 MW GRID Breaker auto tripped at 12:59PM due to heavy jerk observed from grid on a/c of 33kv Kailashpuri rural feeder tripped at Dhaurhara s/s ,Again STG Sync. with Grid at 01:01PM. | 2025-03-05 18:54 | 2025-03-05 18:54
2025-03-05 | 2025-03-05 16:17 | 2025-03-05 16:18 | Grid | OTHERS | Others | Electrical | 30.85MW GRID Breaker auto tripped at 04:17PM due to heavy jerk observed from grid side ,Again STG Sync. with Grid at 04:18PM. | 2025-03-10 11:29 | 2025-03-10 11:29
2025-03-10 | 2025-03-10 17:24 | 2025-03-10 17:58 | 30.85 MW Turbine | TURBINE & GENERATOR | Temp. Monitoring System | Instrumentation | 30.85MW STG Set Turbine Auto Tripped at 05:24PM due to Alternator DE Side Bearing RTD Malfunctioning , Again STG set Started & Sync with Grid at 05:58 PM. | 2025-03-12 16:28 | 2025-03-12 16:28
2025-03-14 | 2025-03-15 05:45 | 2025-03-15 12:45 | 3MW Turbine (Old) | OTHERS | Others | Other | NO Cane | 2025-03-18 12:20 | 2025-03-18 12:20
2025-03-14 | 2025-03-15 05:30 | 2025-03-15 13:07 | 3MW Turbine (New) | OTHERS | Others | Other | NO Cane | 2025-03-18 12:21 | 2025-03-18 12:21
2025-03-16 | 2025-03-17 06:29 | 2025-03-17 06:30 | Grid | OTHERS | Others | Electrical | 30.85 MW_STG set Grid Breaker auto tripped at 06:29AM due to heavy jerk observed from grid side & STG Sync with Grid at 06:30AM . | 2025-03-18 12:23 | 2025-03-18 12:23
2025-04-21 | 2025-04-20 10:39 | 2025-04-20 10:39 | 30.85 MW Turbine | BOILER FEED WATER STATION | Auxillery Oil Pump-1 (AOP-1) | Electrical | ok | 2025-04-21 10:41 | 2025-04-21 10:41
2025-11-01 | 2025-11-02 01:48 | 2025-11-02 01:50 | Grid | OTHERS | Others | Electrical | GRID breaker auto tripped due to GRID fluctuation . | 2025-11-02 13:11 | 2025-11-02 13:11
2025-11-01 | 2025-11-02 04:47 | 2025-11-02 04:57 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | GRID Breaker auto tripped due to GRID Failure on a/c of tripping of 132KV Tr. line from Nighasahan Substation. | 2025-11-02 13:13 | 2025-11-02 13:13
2025-10-30 | 2025-10-30 18:47 | 2025-10-30 18:48 | Grid | OTHERS | Others | Electrical | GRID breaker auto tripped due to GRID fluctuation. | 2025-11-02 13:15 | 2025-11-02 13:15
2025-10-30 | 2025-10-30 08:41 | 2025-09-30 11:17 | 35 TPH Boiler | FURNACE | Furnace Tubes, Boiler Bank, super Heater & Eco | Mechanical | 4MW STG set and 35TPH Boiler manually stopped due to Boiler Tube leakage. | 2025-11-02 13:18 | 2025-11-02 13:18
2025-10-29 | 2025-10-29 20:55 | 2025-10-29 20:56 | Grid | OTHERS | Others | Electrical | GRID Breaker auto tripped due to GRID fluctuation. | 2025-11-02 13:19 | 2025-11-02 13:19
2025-10-28 | 2025-10-28 22:18 | 2025-10-28 22:29 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | GRID breaker auto tripped due to GRID failure o/c of tripping of 132KV Dhaurahar Tr. line from Nighashan Substation | 2025-11-02 13:22 | 2025-11-02 13:22
2025-10-28 | 2025-10-28 22:32 | 2025-10-28 22:41 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | GRID breaker auto tripped due to GRID failure o/c of tripping of 132KV Dhaurahar Tr. line from Nighashan Substation | 2025-11-02 13:23 | 2025-11-02 13:23
2025-10-28 | 2025-10-29 00:38 | 2025-10-29 12:48 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | GRID breaker auto tripped due to GRID failure o/c of tripping of 132KV GSMA Tr. line from Dhaurahara Substation | 2025-11-02 13:24 | 2025-11-02 13:24
2025-10-28 | 2025-10-29 06:02 | 2025-10-29 06:16 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | GRID breaker auto tripped due to GRID failure o/c of tripping of 132KV Dhaurahar Tr. line from Nighashan Substation | 2025-11-02 13:25 | 2025-11-02 13:25
2025-10-27 | 2025-10-28 00:17 | 2025-10-28 00:30 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | GRID breaker auto tripped due to GRID failure o/c of tripping of 132KV GSMA Tr. line from Dhaurahar Substation | 2025-11-02 13:26 | 2025-11-02 13:26
2025-10-27 | 2025-10-28 05:11 | 2025-10-28 05:24 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | GRID breaker auto tripped due to GRID failure o/c of tripping of 132KV Dhaurahar Tr. line from Nighashan Substation | 2025-11-02 13:27 | 2025-11-02 13:27
2025-10-26 | 2025-10-27 04:51 | 2025-10-27 04:52 | Grid | OTHERS | Others | Electrical | GRID breaker auto tripped due to GRID fluctuation. | 2025-11-02 13:28 | 2025-11-02 13:28
2025-11-03 | 2025-11-03 21:07 | 2025-11-03 21:08 | Grid | OTHERS | Others | Electrical | GRID breaker auto tripped due to GRID Fluctuation. | 2025-11-04 11:32 | 2025-11-04 11:32
2025-11-04 | 2025-11-04 23:56 | 2025-11-04 23:57 | Grid | OTHERS | Others | Electrical | 30.85 MW Grid breaker auto tripped due to GRID fluctuation. | 2025-11-05 12:42 | 2025-11-05 12:42
2025-11-05 | 2025-11-05 22:17 | 2025-11-05 22:18 | Grid | OTHERS | Others | Electrical | 30.85 MW Grid breaker auto tripped at 10:17PM due to GRID Fluctuation and STG synced with grid at 10:18PM. | 2025-11-06 13:41 | 2025-11-06 13:41
2025-11-05 | 2025-11-05 21:49 | 2025-11-06 01:21 | 35 TPH Boiler | BOILER FANS | ID Fan | Electrical | 4MW STG set & 35TPH Boiler manually stopped to ID fan Motor Power Cable found Earthed , Then Spare Cable taken in line. | 2025-11-06 13:43 | 2025-11-06 13:43
2025-11-11 | 2025-11-12 07:50 | 2025-11-12 08:00 | 3MW Turbine (New) | MILL - GENERAL CLEANING | Others | Other | 3MW New STG Stopped at 07:50AM due to mill stopped for Mill general cleaning | 2025-11-16 11:35 | 2025-11-16 11:35
2025-11-12 | 2025-11-12 08:15 | 2025-11-12 11:05 | 3MW Turbine (Old) | MILL - GENERAL CLEANING | Others | Other | 3MW Old STG Manually stopped due to mill General Cleaning. | 2025-11-16 11:37 | 2025-11-16 11:37
2025-11-12 | 2025-11-12 08:00 | 2025-11-12 11:48 | 3MW Turbine (New) | MILL - GENERAL CLEANING | Others | Other | 3MW New STG set manually stopped for mill general cleaning. | 2025-11-16 11:38 | 2025-11-16 11:38
2025-11-16 | 2025-11-17 03:07 | 2025-11-17 03:09 | Grid | OTHERS | N/A | Electrical | 30.85 MW Tie breaker auto tripped due to grid fluctuation. | 2025-11-17 09:58 | 2025-11-17 09:58
2025-11-18 | 2025-11-18 11:30 | 2025-11-18 14:40 | 3MW Turbine (New) | TURBINE & GENERATOR | AVR Panel | Electrical | 3MW New STG set Stopped for Digital AVR installation. | 2025-11-24 12:11 | 2025-11-24 12:11
2025-11-18 | 2025-11-18 18:53 | 2025-11-18 19:51 | 3MW Turbine (New) | BOILER FEED WATER STATION | Feed Water Pump-C | Mechanical | 3MW New manually tripped due to low steam pressure on a/c of drum level very low. | 2025-11-24 12:16 | 2025-11-24 12:16
2025-11-18 | 2025-11-18 18:53 | 2025-11-18 19:28 | 3MW Turbine (Old) | BOILER FEED WATER STATION | Feed Water Pump-C | Mechanical | 3MW Old TG manually tripped due to low steam pressure on a/c of boiler steam drum level low. | 2025-11-24 12:19 | 2025-11-24 12:19
2025-11-19 | 2025-11-19 13:30 | 2025-11-19 13:32 | Grid | OTHERS | N/A | Electrical | Grid Breaker auto tripped due to grid fluctuation. | 2025-11-24 12:22 | 2025-11-24 12:22
2025-11-22 | 2025-11-23 05:37 | 2025-11-23 05:47 | Grid | 132 KV TRANSMISSION LINE | N/A | Electrical | Grid breaker auto tripped due to Grid failure from Nighasan Substation. | 2025-11-24 12:25 | 2025-11-24 12:25
2025-11-24 | 2025-11-24 13:06 | 2025-11-24 13:08 | Grid | OTHERS | Others | Electrical | 30.85 MW Grid breaker auto tripped from 01:06PM to 01:08PM due to Grid fluctuation. | 2025-11-25 09:59 | 2025-11-25 09:59
2025-11-24 | 2025-11-24 20:30 | 2025-11-24 20:31 | Grid | OTHERS | DCS Controller & IO cards | Electrical | 30.85 MW Grid breaker auto tripped from 08:30PM to 08:31PM due to grid fluctuation. | 2025-11-25 10:00 | 2025-11-25 10:00
2025-12-03 | 2025-12-03 14:45 | 2025-12-03 17:04 | 30.85 MW Turbine | FUEL HANDLING SYSTEM | Slat chain Conveyor | Mechanical | 30.85 MW STG set manually Stopped due to problem in slat chain Fluid Coupling issue. | 2025-12-14 11:39 | 2025-12-14 11:39
2025-12-03 | 2025-12-03 10:20 | 2025-12-03 15:58 | 3MW Turbine (New) | MILL - GENERAL CLEANING | Others | Other | 3MW New STG manually Stopped due to Mill Schedule General Cleaning. | 2025-12-14 11:42 | 2025-12-14 11:42
2025-12-03 | 2025-12-03 10:30 | 2025-12-03 15:38 | 3MW Turbine (Old) | MILL - GENERAL CLEANING | Others | Other | Old STG manually Stopped due to mill Schedule General Cleaning. | 2025-12-14 11:43 | 2025-12-14 11:43
2025-12-03 | 2025-12-03 08:45 | 2025-12-03 15:58 | 4MW Turbine | FURNACE | Furnace Tubes | Mechanical | 4.00 MW STG Set manually Stopped due to LHS water Wall panel leakage. | 2025-12-14 11:46 | 2025-12-14 11:46
2025-12-07 | 2025-12-07 21:00 | 2025-12-07 21:10 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | Grid breaker auto tripped due to Grid failed from Nighasan Substation. | 2025-12-14 11:48 | 2025-12-14 11:48
2025-12-14 | 2025-12-14 14:24 | 2025-12-14 14:26 | Grid | OTHERS | Others | Electrical | Grid breaker auto tripped due to Heavy jerk observed from grid side then Grid resumed and STG synced with grid. | 2025-12-20 10:15 | 2025-12-20 10:15
2025-12-18 | 2025-12-18 19:31 | 2025-12-18 19:39 | Grid | OTHERS | Others | Electrical | Grid breaker auto tripped due to Grid Failed from Dhaurhara Substation ,Grid resumed and STG synced with grid. | 2025-12-20 10:17 | 2025-12-20 10:17
2025-12-20 | 2025-12-20 18:48 | 2025-12-20 18:49 | Grid | OTHERS | Others | Electrical | Grid breaker auto tripped due to GRID fluctuation. | 2025-12-21 10:24 | 2025-12-21 10:24
2025-12-20 | 2025-12-20 18:48 | 2025-12-20 18:49 | Grid | OTHERS | Others | Electrical | Grid breaker auto tripped due to heavy jerk observed from grid side ,Again STG synced with grid. | 2025-12-22 10:24 | 2025-12-22 10:24
2025-12-22 | 2025-12-23 05:43 | 2025-12-23 05:52 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | Grid breaker auto tripped due to Grid Failure from Nighasan Substation, Grid resumed. | 2025-12-23 10:21 | 2025-12-23 10:21
2025-12-23 | 2025-12-23 14:14 | 2025-12-23 14:39 | Grid | 132 KV SWITCHYARD | SF-6 Breaker | Electrical | Grid breaker manually tripped due to SF6 breaker testing purpose at dhaurahra substation. | 2025-12-24 17:52 | 2025-12-24 17:52
2025-12-26 | 2025-12-26 20:00 | 2025-12-26 20:01 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | Grid breaker auto tripped due to heavy jerk observed from Grid side. | 2025-12-27 10:41 | 2025-12-27 10:41
2025-12-28 | 2025-12-29 06:28 | 2025-12-29 06:38 | Grid | OTHERS | Others | Electrical | Grid breaker auto tripped due to heavy jerk observed from Grid side. | 2025-12-29 14:54 | 2025-12-29 14:54
2026-01-03 | 2026-01-03 10:12 | 2026-01-03 03:20 | 3MW Turbine (New) | MILL - GENERAL CLEANING | Others | Other | 3MW New STG manually Stopped at 10:12AM due to Schedule Mill General cleaning , again synced at 03:20PM | 2026-01-04 12:06 | 2026-01-04 12:06
2026-01-03 | 2026-01-03 12:08 | 2026-01-03 15:34 | 3MW Turbine (Old) | MILL - GENERAL CLEANING | Others | Other | 3MW Old TG manually stopped at 12:08 PM due to Schedule Mill General cleaning , again synced at 03:34 PM | 2026-01-04 12:08 | 2026-01-04 12:08
2026-01-03 | 2026-01-03 10:17 | 2026-01-03 14:40 | 35 TPH Boiler & 4MW Turbine | FUEL HANDLING SYSTEM | New Belt Conveyor-4 (NBC-4) | Mechanical | 4.00 MW STG Set manually stopped due to attend scheduled Maintenance work of 35TPH Boiler. | 2026-01-04 12:09 | 2026-01-04 12:09
2026-01-07 | 2026-01-08 00:07 | 2026-01-08 00:08 | Grid | OTHERS | Others | Electrical | Grid breaker auto tripped due to heavy jerk observed from Grid side. | 2026-01-08 11:04 | 2026-01-08 11:04
2026-01-14 | 2026-01-14 22:59 | 2026-01-14 23:17 | Grid | OTHERS | Others | Electrical | Grid Failed from Dhaurhara Substation. | 2026-01-15 11:06 | 2026-01-15 11:06
2026-01-14 | 2026-01-15 00:05 | 2026-01-15 00:18 | Grid | OTHERS | Others | Electrical | Grid Failed from Dhaurhara Substation. | 2026-01-15 11:07 | 2026-01-15 11:07
2026-01-15 | 2026-01-15 08:14 | 2026-01-15 08:15 | Grid | OTHERS | Others | Electrical | GRID Fluctuation | 2026-01-16 15:44 | 2026-01-16 15:44
2026-01-15 | 2026-01-16 06:12 | 2026-01-16 06:21 | Grid | 132 KV TRANSMISSION LINE | Transmission Line | Electrical | Grid Failed from Dhaurhara Substation. | 2026-01-16 15:47 | 2026-01-16 15:47
2026-01-16 | 2026-01-16 10:34 | 2026-01-16 10:36 | Grid | OTHERS | Others | Electrical | Grid Breaker auto tripped due to heavy jerk observed from grid side. | 2026-01-18 15:01 | 2026-01-18 15:01
2026-01-23 | 2026-01-24 01:36 | 2026-01-24 01:37 | Grid | OTHERS | Others | Electrical | Grid Breaker auto tripped due to heavy jerk observed from grid side. | 2026-01-27 15:00 | 2026-01-27 15:00
2026-01-29 | 2026-01-27 06:31 | 2026-01-30 03:19 | 35 TPH Boiler & 4MW Turbine | OTHERS | Others | Other | 4.00 MW STG Set and 35 TPH boiler taken shutdown for scheduled Maintenance work of Distillery Plant. | 2026-01-31 11:43 | 2026-01-31 11:43
2026-01-29 | 2026-01-29 10:40 | 2026-01-30 01:37 | 3MW Turbine (New) | MILL - GENERAL CLEANING | Others | Other | 3MW New STG set taken shutdown for Scheduled Mill cleaning. | 2026-01-31 11:46 | 2026-01-31 11:46
2026-01-29 | 2026-01-29 10:47 | 2026-01-30 01:27 | 3MW Turbine (Old) | MILL - GENERAL CLEANING | Others | Other | 3 MW Old STG set stopped for Scheduled Mill cleaning. | 2026-01-31 11:48 | 2026-01-31 11:48
2026-02-02 | 2026-02-02 02:37 | 2026-02-02 21:49 | 35 TPH Boiler | OTHERS | Furnace Tubes, Boiler Bank, super Heater & Eco | Mechanical | 4.00MW STG Set Breaker manually Opened due to Boiler Economiser Tube leakage. | 2026-02-03 19:58 | 2026-02-03 19:58
2026-02-05 | 2026-02-05 16:25 | 2026-02-05 16:26 | Grid | OTHERS | Others | Electrical | Grid Breaker auto tripped due to heavy jerk observed from grid side. | 2026-02-06 09:53 | 2026-02-06 09:53
2026-02-10 | 2026-02-06 23:54 | 2026-02-10 21:21 | 35 TPH Boiler | OTHERS | Ash Handling System -3 (Economiser) | Mechanical | 4.00MW STG Set Breaker manually Opened due to Boiler Economiser Tube leakage. | 2026-02-11 09:44 | 2026-02-11 09:44
2026-03-05 | 2026-03-05 02:05 | 2026-03-05 15:28 | 3MW Turbine (Old) | OTHERS | Others | Other | 3 MW Old TG stopped due to Mill Stopped for No Cane Condition. | 2026-03-06 10:42 | 2026-03-06 10:42
2026-03-05 | 2026-03-05 00:50 | 2026-03-05 16:05 | 3MW Turbine (New) | OTHERS | Others | Other | 3MW New STG stopped due to Mill Stopped for No Cane Condition. | 2026-03-06 10:45 | 2026-03-06 10:45
2026-03-13 | 2026-03-13 07:26 | 2026-03-13 09:35 | 35 TPH Boiler | FUEL HANDLING SYSTEM | New Belt Conveyor-4 (NBC-4) | Mechanical | 4.00MW STG Set Breaker manually Opened due to Bagasse Jamm in NBC-4. | 2026-03-14 09:37 | 2026-03-14 09:37
2026-03-20 | 2026-03-20 17:04 | 2026-03-20 17:05 | Grid | OTHERS | Others | Other | Grid breaker auto tripped due to heavy jerk observed from Grid side and Bad weather conditions. | 2026-03-21 10:25 | 2026-03-21 10:25
2026-03-20 | 2026-03-21 06:42 | 2026-03-21 09:06 | 35 TPH Boiler & 4MW Turbine | FUEL HANDLING SYSTEM | Dist Belt Conveyor-5 (DBC-5) | Mechanical | 4MW STG set stopped due to bagasse jamm at DBC-5 chute. | 2026-03-21 10:27 | 2026-03-21 10:27
2026-03-22 | 2026-03-22 17:04 | 2026-03-22 17:05 | Grid | OTHERS | Others | Other | Grid breaker auto tripped due to heavy jerk observed from Grid side. | 2026-03-23 10:09 | 2026-03-23 10:09
2026-03-24 | 2026-03-25 01:15 | 2026-03-25 01:17 | Grid | 132 KV TRANSMISSION LINE | Transmission Line | Electrical | Grid breaker auto tripped due to heavy jerk observed from Grid side. | 2026-03-25 10:51 | 2026-03-25 10:51
2026-04-01 | 2026-04-01 19:27 | 2026-04-01 19:28 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | Grid Breaker auto tripped due to heavy jerk observed from grid side. | 2026-04-08 16:01 | 2026-04-08 16:01
2026-04-01 | 2026-04-01 19:35 | 2026-04-01 20:30 | 3MW Turbine (Old) | TURBINE & GENERATOR | Others | Instrumentation | 3MW Old STG Breaker Tripped due to actuator issue. | 2026-04-08 16:04 | 2026-04-08 16:04
2026-04-01 | 2026-04-01 19:56 | 2026-04-01 20:15 | 3MW Turbine (New) | TURBINE & GENERATOR | Others | Instrumentation | 3MW New STG Breaker Tripped due to actuator issue. | 2026-04-08 16:06 | 2026-04-08 16:06
2026-04-01 | 2026-04-02 03:18 | 2026-04-02 18:10 | 3MW Turbine (Old) | TURBINE & GENERATOR | HP Actuator | Instrumentation | 3MW Old STG Breaker Tripped due to actuator issue. | 2026-04-08 16:09 | 2026-04-08 16:09
2026-04-01 | 2026-04-02 03:20 | 2026-04-02 04:47 | 3MW Turbine (New) | TURBINE & GENERATOR | HP Actuator | Instrumentation | 3MW New STG Breaker Tripped due to actuator issue. | 2026-04-08 16:10 | 2026-04-08 16:10
2026-04-03 | 2026-04-03 09:42 | 2026-04-03 09:43 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | Grid breaker auto tripped due to heavy jerk observed from Grid side. | 2026-04-08 16:12 | 2026-04-08 16:12
2026-04-06 | 2026-04-06 08:08 | 2026-04-06 08:09 | Grid | 132 KV TRANSMISSION LINE | Others | Electrical | Grid breaker auto tripped due to heavy jerk observed from Grid side. | 2026-05-09 12:30 | 2026-05-09 12:30