## Sheet Map
sheet name | id | EQUIPMENT TAG NAME/APPLICATION
TURBINE :: ZIL/SUG/01 | 9d00e5872e68 | ZIL/SUG/01
TURBINE :: ZIL/SUG/02 | a8964cb61c08 | ZIL/SUG/02
TURBINE :: ZIL/SUG/03 | 2439fbd82dd9 | ZIL/SUG/03
Mill-16 :: ZIL/SUG./001 (FCV_101) | 0bf4f35b1931 | ZIL/SUG./001 (FCV_101)
Mill-16 :: ZIL/SUG./002 (FCV_101) | c5bf7bc1c10d | ZIL/SUG./002 (FCV_101)
Mill-16 :: ZIL/SUG./003 (LCV_101) | 947ee1a0f346 | ZIL/SUG./003 (LCV_101)
Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | e029ba2b49f1 | ZIL/SUG./004 (XV_RJ1_SOV1)
Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | b171df0157e0 | ZIL/SUG./005 (XV_RJ1_SOV1)
Mill-16 :: ZIL/SUG./010 (LI_101 ) | 27b6f162412b | ZIL/SUG./010 (LI_101 )
Mill-16 :: ZIL/SUG./011 (LI_102 ) | 2927091f1041 | ZIL/SUG./011 (LI_102 )
Mill-16 :: ZIL/SUG./012 ( LI_103 ) | b7fc6d12f62b | ZIL/SUG./012 ( LI_103 )
Mill-16 :: ZIL/SUG./013 (LI_104 ) | e8816bcbb3ed | ZIL/SUG./013 (LI_104 )
Mill-16 :: ZIL/SUG./014 (LI_105 ) | 41800e67671c | ZIL/SUG./014 (LI_105 )
Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | 7a33c1c48f41 | ZIL/SUG./015 (VIB101,VIB102,VIB106)
Transmitter :: ZIL/SUG./01/TX.-01 | d16b06a34dbb | ZIL/SUG./01/TX.-01
Transmitter :: ZIL/SUG./02/TX.-2 | 325da979b950 | ZIL/SUG./02/TX.-2
Transmitter :: ZIL/SUG./03/TX.-03 | 5e92fe30c410 | ZIL/SUG./03/TX.-03
Transmitter :: ZIL/SUG./04/TX.-04 | 1492ad800d11 | ZIL/SUG./04/TX.-04
Transmitter :: ZIL/SUG./05/TX.-05 | f79fd145caa8 | ZIL/SUG./05/TX.-05
Transmitter :: ZIL/SUG./06/TX.-06 | ae232e634443 | ZIL/SUG./06/TX.-06
Transmitter :: ZIL/SUG./07/TX.-07 | 73362d5a8684 | ZIL/SUG./07/TX.-07
Transmitter :: ZIL/SUG./08/TX.-08 | 6eb025f934c5 | ZIL/SUG./08/TX.-08
DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | 98d45d854a4c | ZIL/SUG./010 (03.TCV.180.B01)
DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | c219e585b204 | ZIL/SUG./011 (05.TCV.120.B01)
DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | 728aab9228cb | ZIL/SUG./012 (03.TCV.190.B01)
DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | 0e16f540bdb9 | ZIL/SUG./013 ( 05TCV.130.B01)
RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | dba6174703a9 | ZIL/SUG./014 (03.TCV.100.B01)
RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | 5f800da90b4a | ZIL/SUG./015 ( 03.TCV.100.B01)
RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | 526ac52027dc | ZIL/SUG./018 ( 05LCV.060B01)
RJH-21-27 :: ZIL/SUG./019 | 1412c805983c | ZIL/SUG./019
RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | 4d4569238db2 | ZIL/SUG./001 ( 16.BCV.050.B01)
B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | e3a4cd203885 | ZIL/SUG./021 (14.TCV.080.B01)
B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | f01365191f1a | ZIL/SUG./022 (14.TCV.100.B01)
B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | d396dac8074f | ZIL/SUG./023 (14.TCV.090.B01)
B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | 63f546416713 | ZIL/SUG./024 (14.TCV.070.B01)
B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | bc6efc435637 | ZIL/SUG./(10.TCV.040.B01)
B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | 6fdc5841fc51 | ZIL/SUG./B.COMP-CT-01
B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | 3625f4d4442a | ZIL/SUG./B.COMP-CT-02
B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | 12829ae4f18f | ZIL/SUG./B.COMP-CT-03
B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | afad394ca1cb | ZIL/SUG./B.COMP-CT-04
B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | 597294c3185a | ZIL/SUG./B.COMP-CT-07
B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | 907a80f96b95 | ZIL/SUG./B.COMP-CT-08
B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | 99f0de160490 | ZIL/SUG./B.COMP-CT-09
B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | a65fa8877e60 | ZIL/SUG./B.COMP-CT-10
B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | b5bbabc2f896 | ZIL/SUG./B.COMP-CT-11
B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | 8e3e8411ce0e | ZIL/SUG./C.COMP-CT-01
B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | a45a075bfead | ZIL/SUG./C.COMP-CT-02
B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | 00e3316dc6ca | ZIL/SUG./C.COMP-CT-03
B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | 97da6dceec8e | ZIL/SUG./C.COMP-CT-04
B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | b5ab141c8d2d | ZIL/SUG./C.COMP-CT-05
B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | 26bcd605138c | ZIL/SUG./C.COMP-CT-06
B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | 9a5aa2c1b3db | ZIL/SUG./C.COMP-CT-07
B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | 67fb92945881 | ZIL/SUG./C.COMP-CT-08
B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | 905ecbe97331 | ZIL/SUG./C.COMP-CT-09
B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | e2401b8b1e50 | ZIL/SUG./C.COMP-CT-10
B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | 748006fed2de | ZIL/SUG./C.COMP-CT-11
RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | eab4335e0100 | ZIL/SUG./075 (45XU009)
RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | 662074755756 | ZIL/SUG./076(13.TCV.005)
RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | b23732fe727e | ZIL/SUG./077 (15.FCV.027)
RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | 954e4d4e8c73 | ZIL/SUG./078 (45.XV.009)
RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | 0418af8673f5 | ZIL/SUG./079(14.BCV.210.B01)
RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | bd3879df9894 | ZIL/SUG./080 (22.TCV.205.B01)
RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | af99b8d37f38 | ZIL/SUG./080A
RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | 95694f79439e | ZIL/SUG./080B
RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | bb167ab80e83 | ZIL/SUG./026 (11.BCV.010.B01)
RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | 252f350bd646 | ZIL/SUG./027 (11.BCV.020.B01)
RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | d55667635172 | ZIL/SUG./028 (11.BCV.030.B01)
RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | 979d9199700e | ZIL/SUG./029 (17.BCV.020.B01)
RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ce0886fd193a | ZIL/SUG./030 (11.BCV.050.B01)
RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | 8847db57d6c4 | ZIL/SUG./031 (14.TCV.210.B01)
RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | 6bd63805c851 | ZIL/SUG./032 /BCV_TCV_601
RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | c4a15ad7ef55 | ZIL/SUG./033/BCV_PCV_601
RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | a6ccee96c381 | ZIL/SUG./034 (12.LCV.070.B01)
RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | 2a97d275d4c2 | ZIL/SUG./035 (12.LCV.080.B01)
RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | a86f0652b773 | ZIL/SUG./036 (12.LCV.090.B01)
RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | a6fcdab27935 | ZIL/SUG./037 (16.MO.30)
RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | be91ac565e45 | ZIL/SUG./038 (16.MO.40)
RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | dcf4ecd6d4e3 | ZIL/SUG./038 (16.MO.30)
RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | 972075a393f6 | ZIL/SUG./039 (15.LCV.030.B01)
RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | 5c691766a74b | ZIL/SUG./040 ( 16.LCV.040.B01)
RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | 0991d898c1fe | ZIL/SUG./041 (16.LCV.050.B01)
RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | 5ce37176f8c1 | ZIL/SUG./042 (03.FCV.120.B01)
RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | c390ef7b0c6c | ZIL/SUG./044 (07.BCV.070.B01)
RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | cbeaae6311d0 | ZIL/SUG./045 (07.LCV.080.B01)
RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | 8080e0713182 | ZIL/SUG./046 (07.BCV.080.B01)
RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | fc898c1d8e7e | ZIL/SUG./046 (07.LCV.070B01)
RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | 62393dae1725 | ZIL/SUG./047 (07.LCV.050.B01)
RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | 7d8200d43fdb | ZIL/SUG./048 (FCV-204)
RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | 224cb1e8b151 | ZIL/SUG./049 (07LCV.040.B01)
RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | 360a63aa1908 | ZIL/SUG./050 (07LCV.050.B01)
RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | 49e1cd515e1c | ZIL/SUG./051 (07LCV.020B01)
RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | aaf0cecbc41e | ZIL/SUG./052 (07LCV.060B01)
RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | 619fc7f42e81 | ZIL/SUG./053 (07LCV.030B01)
RAW QUAD 47 :: ZIL/SUG./054/SAFETY | afdf7d239cec | ZIL/SUG./054/SAFETY
FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | e420b9453293 | ZIL/SUG/01/DS_MASS_FLW_DUMMY
FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | 720a91e7c2e5 | ZIL/SUG/01/_03_FI_040_B01
FLOW METER :: ZIL/SUG/01/FT_SJMG | 957ad8dc5034 | ZIL/SUG/01/FT_SJMG
FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | be2378ecb451 | ZIL/SUG./01/_03_FI_040_B02
FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | cd4285a04f9d | ZIL/SUG./01/FT_IMWF_101
FLOW METER :: ZIL/SUG./01/FT_RWF_102 | b3385a37c807 | ZIL/SUG./01/FT_RWF_102
FLOW METER :: ZIL/SUG./01/UGR-FM-1 | 1dade74e949f | ZIL/SUG./01/UGR-FM-1
FLOW METER :: ZIL/SUG./CPU-WFM | e2d0d566e3c3 | ZIL/SUG./CPU-WFM
FLOW METER :: ZIL/SUG./001/COLD-WATER | 18035210f01c | ZIL/SUG./001/COLD-WATER
FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | 6246406e90fc | ZIL/SUG./01/_05_FT_100_B01
FLOW METER :: ZIL/SUG./01/03.FT140.B01. | 30fd196df9a0 | ZIL/SUG./01/03.FT140.B01.
FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | bd1904436933 | ZIL/SUG./01/_03_FT_120_B01
FLOW METER :: ZIL/SUG./01/DE-SWEETING | a1fc27d3d05a | ZIL/SUG./01/DE-SWEETING
FLOW METER :: ZIL/SUG./01/05.FT060.B01. | bd2155ca5019 | ZIL/SUG./01/05.FT060.B01.
FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | 35a210b6557b | ZIL/SUG./01/_05_FT_040_B01
FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | 5023db2c9a2a | ZIL/SUG/01/_07_FT_100_B01
FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | 0991cf792b3d | ZIL/SUG./01/_15_FT_013_B01
FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | d9fb31fb1206 | ZIL/SUG./C.CONTI/FT_25
FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | 8af6187bbb9e | ZIL/SUG./C.CONTI/FT_26
FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | bc3c1501a99c | ZIL/SUG./B.CONTI/FT_23
FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | 8fa2fb7ddc7c | ZIL/SUG./B.CONTI/FT_24
FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | 1ed56a8556e2 | ZIL/SUG./B.CONTI/FT_Grain
FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | 7499bc8d58d4 | ZIL/SUG./C.CONTI/FT_Grain
FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | b59871438033 | ZIL/SUG./01/05.FT.130.B01
FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | bb677b5e85f7 | ZIL/SUG./01/OVER-HEAD-FM
FLOW METER :: ZIL/SUG./01/UGR-FM-2 | 43cdc8679bf2 | ZIL/SUG./01/UGR-FM-2
FLOW METER :: ZIL/SUG./01/ADMIN-FM | 895b3ba52928 | ZIL/SUG./01/ADMIN-FM
FLOW METER :: ZIL/SUG./01/STP-FM | fd337d3480ae | ZIL/SUG./01/STP-FM
FLOW METER :: ZIL/SUG./01/T-YARD-FM | f7ba61246ec7 | ZIL/SUG./01/T-YARD-FM
FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | 769599b2370f | ZIL/SUG./01/DIS.-TW-FM-1
WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | 6386c46456f5 | ZIL/SUG./001/L-DWM-1
WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | 0f487f52027c | ZIL/SUG./001/M-DWM-2
WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | e586dcabb084 | ZIL/SUG./001/S-DWM-3
WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | f016b81a848a | ZIL/SUG./001/25KG-SWM-5
WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | 17005bd31542 | ZIL/SUG./001/PH-DWM-04
CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | df263fd8dd87 | ZIL/SUG./001/B-CFM-01
CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | f2a80d59cb5b | ZIL/SUG./001/B-CFM-02
CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | 4dfb948743da | ZIL/SUG./001/B-CFM-03
CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | 84bfaa76d74a | ZIL/SUG./001/B-CFM-04
CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | d19aae6716bd | ZIL/SUG./001/C-CFM-01
CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | cb36bcb64470 | ZIL/SUG./001/C-CFM-02
CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | 27d85fa2b593 | ZIL/SUG./001/C-CFM-03
CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | 4db646afc3ed | ZIL/SUG./001/RAW-CFM-01
CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | 32e46fdd6380 | ZIL/SUG./001/REF-CFM- 01
AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | c188745054f4 | ZIL/SUG./001/AC-1
AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | cd41d6b59f65 | ZIL/SUG./001/AC-2
AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | fb2f08d5c731 | ZIL/SUG./001/AC-3
AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | 8fb00e31b753 | ZIL/SUG./001/AC-4
AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | 710c680f5b8e | ZIL/SUG./001/AC dryer-1
AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | a50eb0d41272 | ZIL/SUG./001/AC dryer-2
Pan-1-23 :: ZIL/SUG./001/APFC-01 | c827e7da1a31 | ZIL/SUG./001/APFC-01
Pan-1-23 :: ZIL/SUG./001/APFC-02 | 05187a35ba10 | ZIL/SUG./001/APFC-02
Pan-1-23 :: ZIL/SUG./001/APFC-03 | 278ad771b6bc | ZIL/SUG./001/APFC-03
Pan-1-23 :: ZIL/SUG./001/APFC-04 | ce0a187f8376 | ZIL/SUG./001/APFC-04
Pan-1-23 :: ZIL/SUG./001/APFC-05 | 782baa8ab1ae | ZIL/SUG./001/APFC-05
Pan-1-23 :: ZIL/SUG./001/APFC-06 | c628710cdf3a | ZIL/SUG./001/APFC-06
Pan-1-23 :: ZIL/SUG./001/APFC-07 | 543d7e2c8e59 | ZIL/SUG./001/APFC-07
Pan-1-23 :: ZIL/SUG./001 /APFC-08 | de63f992d023 | ZIL/SUG./001 /APFC-08
Pan-1-23 :: ZIL/SUG./001 /APFC-09 | 058911f68dfa | ZIL/SUG./001 /APFC-09
Pan-1-23 :: ZIL/SUG./001 /APFC-10 | 559e712e58dc | ZIL/SUG./001 /APFC-10
Pan-1-23 :: ZIL/SUG./001 /APFC-11 | 626316f2c996 | ZIL/SUG./001 /APFC-11
Pan-1-23 :: ZIL/SUG./001 /APFC-12 | d35d3744d1a1 | ZIL/SUG./001 /APFC-12
Pan-1-23 :: ZIL/SUG./001/APFC-13A | 1e66a0a9e65e | ZIL/SUG./001/APFC-13A
Pan-1-23 :: ZIL/SUG./001/APFC-13B | e7e34ef15d20 | ZIL/SUG./001/APFC-13B
Pan-1-23 :: ZIL/SUG./001/APFC-13C | 3aa694fe15f5 | ZIL/SUG./001/APFC-13C
Pan-1-23 :: ZIL/SUG./001/APFC-13D | fa2230fcc4ee | ZIL/SUG./001/APFC-13D
Pan-1-23 :: ZIL/SUG./001/VB-01 | fe351a48a563 | ZIL/SUG./001/VB-01
Pan-1-23 :: ZIL/SUG./001/VB-02 | 61943b9b1ba8 | ZIL/SUG./001/VB-02
Pan-1-23 :: ZIL/SUG./001/VB-03 | cd4bb3efe536 | ZIL/SUG./001/VB-03
Pan-1-23 :: ZIL/SUG./001/VB-08 | f968f06fea01 | ZIL/SUG./001/VB-08
Pan-1-23 :: ZIL/SUG./001/VB-10 | a2b8465e1110 | ZIL/SUG./001/VB-10
Pan-1-23 :: ZIL/SUG./001/VB-11 | cdfe835c318c | ZIL/SUG./001/VB-11
Pan-1-23 :: ZIL/SUG./001/VB-12 | d2001f5aa802 | ZIL/SUG./001/VB-12
VRL 24-53 :: ZIL/SUG./001 /PSV201 | 887ae1f6ae33 | ZIL/SUG./001 /PSV201
VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | f4c4ed140b10 | ZIL/SUG./001/ TCV-201(i)
VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | 427ebac0a020 | ZIL/SUG./001/ TCV-201(ii)
VRL 24-53 :: ZIL/SUG./001/TCV-203 | c6d1668e078d | ZIL/SUG./001/TCV-203
VRL 24-53 :: ZIL/SUG./001/TCV-202E | 900cdbffa416 | ZIL/SUG./001/TCV-202E
VRL 24-53 :: ZIL/SUG./001 /TCV203D | e8d420266467 | ZIL/SUG./001 /TCV203D
VRL 24-53 :: ZIL/SUG./001/TCV-203A | b235c3640469 | ZIL/SUG./001/TCV-203A
VRL 24-53 :: ZIL/SUG./001 /TCV-203B | 78233573e360 | ZIL/SUG./001 /TCV-203B
VRL 24-53 :: ZIL/SUG./001/TCV203-C | dd5f44a6aeea | ZIL/SUG./001/TCV203-C
VRL 24-53 :: ZIL/SUG./001/TCV204 | 7b31872bcb82 | ZIL/SUG./001/TCV204
VRL 24-53 :: ZIL/SUG./001/TCV-205 | 59fbb9226a80 | ZIL/SUG./001/TCV-205
VRL 24-53 :: ZIL/SUG./001/TCV-206 | 67d4939ac651 | ZIL/SUG./001/TCV-206
VRL 24-53 :: ZIL/SUG./001/TCV-207 | 246f47a0663c | ZIL/SUG./001/TCV-207
VRL 24-53 :: ZIL/SUG./001/TCV-208 | 694c45876510 | ZIL/SUG./001/TCV-208
VRL 24-53 :: ZIL/SUG./001/TCV-209 | 50013bc177da | ZIL/SUG./001/TCV-209
VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | 6706b19850b5 | ZIL/SUG./001/TCV-OVERHEAD
VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | c308418c135d | ZIL/SUG./001/B_MOLASSES_CV
VRL 24-53 :: ZIL/SUG./001 FCV-205 | 6f5787014b99 | ZIL/SUG./001 FCV-205
VRL 24-53 :: ZIL/SUG./001 05FCVB01 | a033258467d5 | ZIL/SUG./001 05FCVB01
VRL 24-53 :: ZIL/SUG./001/FCV-203 | 76d8be18192e | ZIL/SUG./001/FCV-203
VRL 24-53 :: ZIL/SUG./001 /TCV-400 | 9ec178bfc889 | ZIL/SUG./001 /TCV-400
VRL 24-53 :: ZIL/SUG./001/MOL-CV | 7748877dd6ba | ZIL/SUG./001/MOL-CV
VRL 24-53 :: ZIL/SUG./001 TCV-702 | 26bf36a6aff8 | ZIL/SUG./001 TCV-702
VRL 24-53 :: ZIL/SUG./001/ FCV_204 | 9975fc2df93f | ZIL/SUG./001/ FCV_204
VRL 24-53 :: ZIL/SUG./001/VC-CV | 2e8b9febffd0 | ZIL/SUG./001/VC-CV
VRL 24-53 :: ZIL/SUG./001 FCV-203 | 7e56f4827698 | ZIL/SUG./001 FCV-203
VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | 51467edc85fe | ZIL/SUG./001/ SY_B_MOLASSES
VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | f85198df25c9 | ZIL/SUG./001/E-BOILER-CV
VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | 7a4dbee41d12 | ZIL/SUG./001/SYRUP-LCV
Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | d9e12e66a845 | ZIL/SUG./001/SYRUP-CV1
Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | 9c36e42133ae | ZIL/SUG./001/SYRUP-CV2
Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | f67abe0068a9 | ZIL/SUG./001/B-HEAVY-CV1
Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | 204045dddced | ZIL/SUG./001/B-HEAVY-CV2
Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | d76d3e71fd2e | ZIL/SUG./001/C-HEAVY-CV1
Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | 7089d2944e2d | ZIL/SUG./001/C-HEAVY-CV2
Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | b562ab37e218 | ZIL/SUG./001/C-HEAVY-CV3
Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | 13658c4b2ce8 | ZIL/SUG./001/DECANTER-1/CV1
Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | 1131a0579f8e | ZIL/SUG./Decanter-1/CV-2
Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | e004a93ec595 | ZIL/SUG./DECANTER-2/CV-2
Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | 452cb739b3ba | ZIL/SUG./DECANTER-CV3
Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | 106efa60c6a7 | ZIL/SUG./001/C.CFM-01
Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | 4cf80560f098 | ZIL/SUG./002/C.CFM-02
Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | e3012d82779e | ZIL/SUG./003/C.CFM-03
Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | 206559743ac0 | ZIL/SUG./004/C1.CFM-04
Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | a070470bf94e | ZIL/SUG./005/C1.CFM-05
Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | 40579c9b934c | ZIL/SUG./006/C.CFM-06
Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | 1482438a94b5 | ZIL/SUG./007/IJP-1
Transient Heater 66-73 :: ZIL/SUG./008 | 4601d338f802 | ZIL/SUG./008
Transient Heater 66-73 :: ZIL/SUG./001 /TCV | c4c2eefab033 | ZIL/SUG./001 /TCV
Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | da94085bd25e | ZIL/SUG./SULPHER/PANEL
Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | c2b506d4463f | ZIL/SUG./FILM/PANEL
Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | e731b480d0d2 | ZIL/SUG./001/DS-CFM- 01
DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | af899fc65ee8 | ZIL/SUG./01/FT_201A
DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ffbe763f258c | ZIL/SUG./01/FT_204
DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | 85491c06d1fb | ZIL/SUG./01/FT_205
DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | c88545950e1c | ZIL/SUG./01/FT_601
DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | 25522698de7b | ZIL/SUG./01/FT-206
DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | 09140bce6549 | ZIL/SUG./01/FT-207
DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | 1d899fefa475 | ZIL/SUG./Vacuum-FM-2
DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | e13c55910104 | ZIL/SUG./01/COND.-FM
DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | d301d63c057c | ZIL/SUG./01/B-HEAVY-FM
DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | 010c97204f9c | ZIL/SUG./01/ETP-SPRAY-O/L
DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 614469c06d4b | ZIL/SUG./01/OVER-HEAD/SPRAY-FM
DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | 078132aed9f9 | ZIL/SUG./01/ETP-O/L-REF-CTFM
DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | 35e024b60280 | ZIL/SUG./01/ETP-I/L-FM
DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | 63bac132e48d | ZIL/SUG./01/ETP-O/L-FM
DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | b6ba0b086fba | ZIL/SUG./01/ETP-B-VER-FM
DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ca56812f6c79 | ZIL/SUG./01/ETP-HYDRO-FM
DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | f8d36da8154c | ZIL/SUG./01/CT-FM
DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | 31fc811e7d98 | ZIL/SUG./01/SURUP-MASS
DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | 7f8f018f4d99 | ZIL/SUG./01/B.CONT.PAN-FM-1
DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | 039a284eb2db | ZIL/SUG./01/B.CONT.PAN-FM-2
DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | 90f6c0ce2d60 | ZIL/SUG./01/B.CONT.PAN-FM-3
DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | c40b1cbeacec | ZIL/SUG./01/75.FT.020.01
DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | eeef619dc388 | ZIL/SUG./01/75.FT.035.01.
DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | 1692889d20f9 | ZIL/SUG./01/Centric-01-FM
DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | 16c61e481883 | ZIL/SUG./01//Centric-02-FM
DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | 8f72e7e40ccc | ZIL/SUG./Decanter-HWFM
SEDL14 :: ZIL/SUG./001/ACCUM | 611ec01c83dd | ZIL/SUG./001/ACCUM
SEDL14 :: ZIL/SUG./001/EVP- A SET | 4edea75d6371 | ZIL/SUG./001/EVP- A SET
SEDL14 :: ZIL/SUG./001/ EVP- B SET | 70b4794bb0de | ZIL/SUG./001/ EVP- B SET
SEDL14 :: ZIL/SUG./001/DS EVP- C SET | dd636e16205b | ZIL/SUG./001/DS EVP- C SET
SEDL14 :: ZIL/SUG./001/Pan-1 | 6ffb952cc49e | ZIL/SUG./001/Pan-1
SEDL14 :: ZIL/SUG./001/Pan-2 | f527c311e5cd | ZIL/SUG./001/Pan-2
SEDL14 :: ZIL/SUG./001/Pan-4 | ba09f15b928b | ZIL/SUG./001/Pan-4
SEDL14 :: ZIL/SUG./001/Pan-6 | 5eb44c927ceb | ZIL/SUG./001/Pan-6
SEDL14 :: ZIL/SUG./001/Pan-7 | bc495932d540 | ZIL/SUG./001/Pan-7
SEDL14 :: ZIL/SUG./001/Pan-8 | edb78c39280b | ZIL/SUG./001/Pan-8
SEDL14 :: ZIL/SUG./001/Pan-9 | b58d9fe6d056 | ZIL/SUG./001/Pan-9
SEDL14 :: ZIL/SUG./001/Pan-10 | f2537d4a3330 | ZIL/SUG./001/Pan-10
SEDL14 :: ZIL/SUG./001/Pan-11 | 14cdf83b5c38 | ZIL/SUG./001/Pan-11
SEDL14 :: ZIL/SUG./001/Pan-12 | b559d63183c6 | ZIL/SUG./001/Pan-12
SEDL14 :: ZIL/SUG./001/Pan-13 | b378778c6ab8 | ZIL/SUG./001/Pan-13
Hi-Tech :: ZIL/SUG./001/M1-SWM | 3bd74d627abf | ZIL/SUG./001/M1-SWM
Hi-Tech :: ZIL/SUG./01/M2-SWM | ab356bfdc2ff | ZIL/SUG./01/M2-SWM
Hi-Tech :: ZIL/SUG./01/S-SWM | 26a43b7dfa80 | ZIL/SUG./01/S-SWM
Hi-Tech :: ZIL/SUG./01/L-SWM | 6fafe505f018 | ZIL/SUG./01/L-SWM
D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | 7a3eb383c90c | ZIL/SUG./001 ( 40FCV101)
D.B.F 14 :: ZIL/SUG./001 (40XV102) | 05ec9f5bc726 | ZIL/SUG./001 (40XV102)
D.B.F 14 :: ZIL/SUG./001 (40XV103) | 11dcd9c3da64 | ZIL/SUG./001 (40XV103)
D.B.F 14 :: ZIL/SUG./001 (40XV105) | c90105591ef7 | ZIL/SUG./001 (40XV105)
D.B.F 14 :: ZIL/SUG./001 (40XV106) | c5c251e5e479 | ZIL/SUG./001 (40XV106)
D.B.F 14 :: ZIL/SUG./001 (40XV107) | b5a7a06c42c2 | ZIL/SUG./001 (40XV107)
D.B.F 14 :: ZIL/SUG./001 (40XV108) | 1a298040c9ea | ZIL/SUG./001 (40XV108)
D.B.F 14 :: ZIL/SUG./001 (40XV202) | f17e9f0ef77c | ZIL/SUG./001 (40XV202)
D.B.F 14 :: ZIL/SUG./001 (40XV203) | 11fd144e2a54 | ZIL/SUG./001 (40XV203)
D.B.F 14 :: ZIL/SUG./001 (40XV205) | ae927933014e | ZIL/SUG./001 (40XV205)
D.B.F 14 :: ZIL/SUG./001 (40XV206) | c5431b24d860 | ZIL/SUG./001 (40XV206)
D.B.F 14 :: ZIL/SUG./001 (40XV207) | 4ef27273fcae | ZIL/SUG./001 (40XV207)
D.B.F 14 :: ZIL/SUG./001 (40XV208) | 6f0df9d5dac2 | ZIL/SUG./001 (40XV208)
D.B.F 14 :: ZIL/SUG./001 (40FCV003) | a10c85b7482a | ZIL/SUG./001 (40FCV003)
I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | 1cb9b5ce967c | ZIL/SUG./001 (52 FCV 101)
I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | d1651f38d251 | ZIL/SUG./001 (52 XV 102)
I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | cd76793a1867 | ZIL/SUG./001 (52 XV 103)
I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | fbbf27511e0e | ZIL/SUG./001 (52 XV 104)
I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | 88e0c7415c60 | ZIL/SUG./001 (52 XV 105)
I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | 63127c6882ad | ZIL/SUG./001 (52 XV 106)
I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | e3800d2d6ba3 | ZIL/SUG./001 (52 XV 108)
I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | 2da5835fef9b | ZIL/SUG./001 (52 XV 110 )
I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | e4c4c04b2bb1 | ZIL/SUG./001 (52 XV 111)
I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | b8849694327a | ZIL/SUG./001 (52 XV 118)
I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | 0799a65b9568 | ZIL/SUG./001 (52 XV 119)
I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | a74a679cab3b | ZIL/SUG./001 (52 XV 120)
I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | b9bdd4fb67d5 | ZIL/SUG./001 (52 XV 121)
I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | 45b3dfbc9cc9 | ZIL/SUG./001 (52 FCV 201)
I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | bb218e11bff5 | ZIL/SUG./001 (52 XV 202)
I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | 7f0a70fb60da | ZIL/SUG./001 (52 XV 203)
I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | 478724a411da | ZIL/SUG./001 (52 XV 204)
I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | 66fa4c0c4412 | ZIL/SUG./001 (52 XV 205)
I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | dcad64bcb0fb | ZIL/SUG./001 (52 XV 206)
I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | 4b60fc4973e0 | ZIL/SUG./001 (52 XV 208)
I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | f623dac7b3dc | ZIL/SUG./001 (52 XV 210)
I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | 59a2640f4f85 | ZIL/SUG./001 (52 XV 211)
I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | a83bf72fffa4 | ZIL/SUG./001 (52 XV 218)
I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | 551193369d6a | ZIL/SUG./001 (52 XV 219 )
I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | e9619a09fee7 | ZIL/SUG./001 (52 XV 220)
I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | 6c84ae83dee0 | ZIL/SUG./001 (52 XV 221)
I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | 8d31714f6be8 | ZIL/SUG./001 (52 FCV 301)
I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | b47c5e17e65e | ZIL/SUG./001 (52 XV 302)
I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | cdd12698eba1 | ZIL/SUG./001 (52 XV 303)
I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | 0455409d1e96 | ZIL/SUG./001 (52 XV 304)
I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | d253aeb78ee7 | ZIL/SUG./001 (52 XV 305)
I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | 87037ca13222 | ZIL/SUG./001 (52 XV 306)
I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | d08a5b1c82b9 | ZIL/SUG./001 (52 XV 308)
I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | a12747901927 | ZIL/SUG./001 (52 XV 310)
I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | dec00ba465cb | ZIL/SUG./001 (52 XV 311)
I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | 6dc309fdc4d0 | ZIL/SUG./001 (52 XV 318)
I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | 4ef7a370c829 | ZIL/SUG./001 (52 XV 319)
I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | 0c4d5ee8dec8 | ZIL/SUG./001 (52 XV 320)
I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | 371b7cdefdcf | ZIL/SUG./001 (52 XV 321)
I.E.R 49 :: ZIL/SUG./001 (52 XV005) | 5327e9dcefbd | ZIL/SUG./001 (52 XV005)
I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | 727e6f6de9ff | ZIL/SUG./001 (52 XV 006)
I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | 21241bcb069b | ZIL/SUG./001 (52 XV 007 )
I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | 5c7f61e1426a | ZIL/SUG./001 (52 XV 003)
I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | bb33dc7b7b85 | ZIL/SUG./001 (52 XV 002 )
I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | d6dd30c6388f | ZIL/SUG./001 (25 TCV 029 )
I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | bafef7605571 | ZIL/SUG./001 (52 XV 036)
I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | f5f0a13a5636 | ZIL/SUG./001 (52 XV 032)
I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | 766dcca928c1 | ZIL/SUG./001 (52 XV 031)
I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ab4f190cbd95 | ZIL/SUG./001/FEED-CV-1
DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | 5993c160b9a2 | ZIL/SUG./001 (20 TCV 015)
DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | eb4a0efd5fd7 | ZIL/SUG./001 (20FCV005)
DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | c70872fd1a22 | ZIL/SUG./001 (20TCV010BO1)
DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | 631763471d13 | ZIL/SUG./001 (20TCV020B01)
Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | abc839905c17 | ZIL/SUG./001 (52 TCV 004)
Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | b848afc7905c | ZIL/SUG./001 (52 FCV 009)
Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | d01294aa990d | ZIL/SUG./001 (52 XV 010)
Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | c4d124f8c5d8 | ZIL/SUG./001 (52 FCV 011)
Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | cc7083d97c8d | ZIL/SUG./001 (52 XV 012)
Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | 8ee862ebe50b | ZIL/SUG./001 (52 XV 025)
Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ad61c6278c96 | ZIL/SUG./001 (52 XV 026)
Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | a073779ae039 | ZIL/SUG./001 (52 FCV 013)
Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | d71a9363dc58 | ZIL/SUG./001 (52 XV 014)
Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | 42f1e215b0a9 | ZIL/SUG./001 (52 XV 016)
Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ae6966e9a386 | ZIL/SUG./001 (15 XV 017)
Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | bb9c0e634560 | ZIL/SUG./001 (52 XV 037)
Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | 638ce12c909b | ZIL/SUG./001 (15 TCV 014)
Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | a28a7e94a1d3 | ZIL/SUG./001 (21TCV040B01)
Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | 757bff158fc7 | ZIL/SUG./001 (21LCV070B01)
Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | e4e5220db386 | ZIL/SUG./001/BCV_TCV_801
Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | 557e0f2b71c9 | ZIL/SUG./001/BCV_PCV_802
Ground floor 19 :: ZIL/SUG./001 (FCV-101) | 53f83b28fde1 | ZIL/SUG./001 (FCV-101)
Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | 084b3e862ac1 | ZIL/SUG./001 (11 BCV 020B01)
Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | da9ea21a639a | ZIL/SUG./001 (022 XV 022G04)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | 42dac004a4f4 | ZIL/SUG./001 (22XV 022 G01 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | fc6514957839 | ZIL/SUG./001 (22XV 022 G02 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | 605f102ad327 | ZIL/SUG./001 (22XV 022 G03 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | 4cd770d2a9d6 | ZIL/SUG./001 (22XV023B03)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | b2d532e54e78 | ZIL/SUG./001 (22XV023B02)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | 5e14184cfee1 | ZIL/SUG./001 (22XV023B04)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | b770b860ce1f | ZIL/SUG./001 (22XV023B05)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | b375c53e076a | ZIL/SUG./001 (22XV020B04)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | 9a103cf9b1fd | ZIL/SUG./001 (22XV024G05)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | 994551843400 | ZIL/SUG./001 (22XV024G01 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | 1263aad094e0 | ZIL/SUG./001 (22XV024G02)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | 40d69f8d0541 | ZIL/SUG./001 (22XV024G03)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | 619697b82989 | ZIL/SUG./001 (22XV024G04 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | e08aa888ab59 | ZIL/SUG./001 (22XV025G04 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | e04e2652c429 | ZIL/SUG./001 (22XV025G03 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | 123458af3aa3 | ZIL/SUG./001 (22XV025G02)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | 69933f8b594b | ZIL/SUG./001 (22XV035B01)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | e881dbb65d0f | ZIL/SUG./001 (22XV035B02)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | 685c5d0f61ef | ZIL/SUG./001 (22XV035B03)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | 6578d8e773ed | ZIL/SUG./001 (22XV035B04 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | b365c2364848 | ZIL/SUG./001 (22XV040B04)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | 419f270f6fe3 | ZIL/SUG./001 (22XV040B03)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | a4faa312e150 | ZIL/SUG./001 (22XV040B02 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | 043e96a04bfc | ZIL/SUG./001 (22XV040B01)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | aea32b2789c2 | ZIL/SUG./001 (22XV055B01)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | 897673af0370 | ZIL/SUG./001 (22XV055B02)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | 87f16ec4bdc4 | ZIL/SUG./001 (22XV055B03)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | 9f30719e3bf8 | ZIL/SUG./001 (22XV055B04 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | fc29bf7ede53 | ZIL/SUG./001 (22XV060B01)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | c1dd23655faa | ZIL/SUG./001 (22XV060B02)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | 4b9cc98c90b7 | ZIL/SUG./001 (22XV060B03)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ddcebcd5f601 | ZIL/SUG./001 (22XV060B04 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | be8a090ce1a4 | ZIL/SUG./001 (22XV065B01)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | 44f4e38d8346 | ZIL/SUG./001 (22XV065B02)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | b0105263b96f | ZIL/SUG./001 (22XV065B03)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | 5565bb63c995 | ZIL/SUG./001 (22XV065B04 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | b1fbf73ae090 | ZIL/SUG./001 (22XV070B01)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | 8da9f9df239a | ZIL/SUG./001 (22XV070B02)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | 6c66b1aad269 | ZIL/SUG./001 (22XV070B03)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | e7a8515694d5 | ZIL/SUG./001 (22XV070B04 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | a38efd3909f6 | ZIL/SUG./001 (22XV045B01 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | e9e63e1171f1 | ZIL/SUG./001 (22XV045B02 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | 4f49fa96e155 | ZIL/SUG./001 (22XV045B03)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | de442ebe8ae1 | ZIL/SUG./001 (22XV045B04)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | 9d56fabe49bb | ZIL/SUG./001 (22XV045B05 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | 5dad742f24de | ZIL/SUG./001 (22XV050B01)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | 8da93aa17979 | ZIL/SUG./001 (22XV050B02 )
Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | dfae3c9e283a | ZIL/SUG./001 (22XV050B03)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | f9f11926a2e9 | ZIL/SUG./001 (22XV050B04)
Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | edfa40e24fb4 | ZIL/SUG./001 (22XV050B05 )
Ref. Condensor 57 :: ZIL/SUG./001/CV1 | fa7bc5cf2fa1 | ZIL/SUG./001/CV1
Ref. Condensor 57 :: ZIL/SUG./001/CV2 | e02aff0e8587 | ZIL/SUG./001/CV2
Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ec3241fc59ff | ZIL/SUG./001 (18 LCV 20 BO1)
Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | 040f80bbc08a | ZIL/SUG./001 (18 LCV 20 BO2)
Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | 66297fc4d293 | ZIL/SUG./001 (18 LCV 20 BO3)
Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | 94b8925ee290 | ZIL/SUG./01/16_FT_130_B01
Ref Flow Meter h :: ZIL/SUG./01/15FT027 | e7f1f3e6a995 | ZIL/SUG./01/15FT027
Ref Flow Meter h :: ZIL/SUG./01/20FT005 | 2072c1fbc922 | ZIL/SUG./01/20FT005
Ref Flow Meter h :: ZIL/SUG./01/40FT003 | 0155572917de | ZIL/SUG./01/40FT003
Ref Flow Meter h :: ZIL/SUG./01/40FT101 | 1fd6a2e688fc | ZIL/SUG./01/40FT101
Ref Flow Meter h :: ZIL/SUG./01/40FT201 | cb893e239628 | ZIL/SUG./01/40FT201
Ref Flow Meter h :: ZIL/SUG./01/52FT009 | 2c380a6b658e | ZIL/SUG./01/52FT009
Ref Flow Meter h :: ZIL/SUG./01/52FT011 | a950c822dcf4 | ZIL/SUG./01/52FT011
Ref Flow Meter h :: ZIL/SUG./01/52FT013 | 5835d3ce44c2 | ZIL/SUG./01/52FT013
Ref Flow Meter h :: ZIL/SUG./01/52FT101 | 1c3773dcdaec | ZIL/SUG./01/52FT101
Ref Flow Meter h :: ZIL/SUG./01/52FT201 | a1a8aa3809ce | ZIL/SUG./01/52FT201
Ref Flow Meter h :: ZIL/SUG./52FT301 | 79215e3dac44 | ZIL/SUG./52FT301
Ref Flow Meter h :: ZIL/SUG./01/FT-101 | 2971b643188c | ZIL/SUG./01/FT-101
Ref Flow Meter h :: ZIL/SUG./01/FT-102 | 9b58b5d21863 | ZIL/SUG./01/FT-102
Ref Flow Meter h :: ZIL/SUG./01/FT-202 | 5fe3890252f6 | ZIL/SUG./01/FT-202
Ref Flow Meter h :: ZIL/SUG./01/FT-301 | 2bb5d3c2977c | ZIL/SUG./01/FT-301
Ref Flow Meter h :: ZIL/SUG./01/FT-302 | 22e44c5a04db | ZIL/SUG./01/FT-302
Ref Flow Meter h :: ZIL/SUG./01/FT-303 | 253224e49b3f | ZIL/SUG./01/FT-303
Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | d2cecfab4a9d | ZIL/SUG./01/IER-4-FEED
conntroller - :: ZIL/GSM/C-1/01 | a32dcd230a83 | ZIL/GSM/C-1/01
conntroller - :: ZIL/GSM/C-2/02 | eadbc93a4fe8 | ZIL/GSM/C-2/02
conntroller - :: ZIL/GSM/C-3/03 | c66da537a3f4 | ZIL/GSM/C-3/03
conntroller - :: ZIL/GSM/C-4/04 | d2b830397ff3 | ZIL/GSM/C-4/04
conntroller - :: ZIL/GSM/C-1/PANEL-1 | ce05f2903868 | ZIL/GSM/C-1/PANEL-1
conntroller - :: ZIL/GSM/C-1/PANEL-2 | 21720f1a39ef | ZIL/GSM/C-1/PANEL-2
conntroller - :: ZIL/GSM/C-1/PANEL-3 | 734e1015a686 | ZIL/GSM/C-1/PANEL-3
conntroller - :: ZIL/GSM/C-1/PANEL-4 | e226e3801516 | ZIL/GSM/C-1/PANEL-4
conntroller - :: ZIL/GSM/C-1/PANEL-5 | f7af7c819c63 | ZIL/GSM/C-1/PANEL-5
conntroller - :: ZIL/GSM/C-1/PANEL-6 | 2e78e356479d | ZIL/GSM/C-1/PANEL-6
conntroller - :: ZIL/GSM/C-1/PANEL-7 | 1a91ce41fc0e | ZIL/GSM/C-1/PANEL-7
conntroller - :: ZIL/GSM/C-2/PANEL-1 | df07c42cffe6 | ZIL/GSM/C-2/PANEL-1
conntroller - :: ZIL/GSM/C-2/PANEL-2 | 8af012e10964 | ZIL/GSM/C-2/PANEL-2
conntroller - :: ZIL/GSM/C-2/PANEL-3 | 66eb3a3cc50d | ZIL/GSM/C-2/PANEL-3
conntroller - :: ZIL/GSM/C-2/PANEL-4 | 8f7328846fe0 | ZIL/GSM/C-2/PANEL-4
conntroller - :: ZIL/GSM/C-2/PANEL-5 | a6f4aab960b2 | ZIL/GSM/C-2/PANEL-5
conntroller - :: ZIL/GSM/C-2/PANEL-6 | 1b902e56fe02 | ZIL/GSM/C-2/PANEL-6
conntroller - :: ZIL/GSM/C-2/PANEL-7 | ad6cda468b78 | ZIL/GSM/C-2/PANEL-7
conntroller - :: ZIL/GSM/C-3/PANEL-1 | 6da378442da1 | ZIL/GSM/C-3/PANEL-1
conntroller - :: ZIL/GSM/C-3/PANEL-2 | a747f65eadc3 | ZIL/GSM/C-3/PANEL-2
conntroller - :: ZIL/GSM/C-3/PANEL-3 | b7258927d4e1 | ZIL/GSM/C-3/PANEL-3
conntroller - :: ZIL/GSM/C-4/PANEL-1 | 4d6ef1105f70 | ZIL/GSM/C-4/PANEL-1
conntroller - :: ZIL/GSM/C-4/PANEL-2 | d66d1b71b9f4 | ZIL/GSM/C-4/PANEL-2
conntroller - :: ZIL/GSM/C-4/PANEL-3 | 63e563bfb640 | ZIL/GSM/C-4/PANEL-3
conntroller - :: ZIL/GSM/C-4/PANEL-4 | d6689fb09412 | ZIL/GSM/C-4/PANEL-4
conntroller - :: ZIL/GSM/C-4/PANEL-5 | 65fe634cebfb | ZIL/GSM/C-4/PANEL-5
conntroller - :: ZIL/GSM/BRS | 1f7a39c51ee3 | ZIL/GSM/BRS
conntroller - :: ZIL/GSM/SEDL | 9c6075df4678 | ZIL/GSM/SEDL
conntroller - :: ZIL/GSM/MCS/PANEL | 45f06d18b66d | ZIL/GSM/MCS/PANEL
conntroller - :: ZIL/GSM/B&C Conti. | 8eb79ccf6d67 | ZIL/GSM/B&C Conti.
conntroller - :: ZIL/SUG/PLC-1 | ebc2e4d34893 | ZIL/SUG/PLC-1
conntroller - :: ZIL/SUG/PLC-2 | 9c35534a604f | ZIL/SUG/PLC-2
Work stations :: ZIL/GSM/Server-1 | d08de2e083c9 | ZIL/GSM/Server-1
Work stations :: ZIL/GSM/Server-2 | 270cd60ab099 | ZIL/GSM/Server-2
Work stations :: ZIL/GSM/Server-3 | d599279ca67b | ZIL/GSM/Server-3
Work stations :: ZIL/GSM/ENGG.ES-1 | 2de1d33c5501 | ZIL/GSM/ENGG.ES-1
Work stations :: ZIL/GSM/OS-1 | 05e40c302e77 | ZIL/GSM/OS-1
Work stations :: ZIL/GSM/OS-2 | 7b248c5b7f01 | ZIL/GSM/OS-2
Work stations :: ZIL/GSM/OS-3 | b16171a22e95 | ZIL/GSM/OS-3
Work stations :: ZIL/GSM/OS-4 | 84bd3c7347c4 | ZIL/GSM/OS-4
Work stations :: ZIL/GSM/OS-5 | c8fbaa610800 | ZIL/GSM/OS-5
Work stations :: ZIL/GSM/OS-6 | 86c66511a674 | ZIL/GSM/OS-6
Work stations :: ZIL/GSM/OS-7 | 3d21a2eb194e | ZIL/GSM/OS-7
Work stations :: ZIL/GSM/OS-8 | b1930c60688e | ZIL/GSM/OS-8
Work stations :: ZIL/GSM/SPARE | d12cd381cec6 | ZIL/GSM/SPARE
Work stations :: ZIL/GSM/OS-B&C | 237799de980f | ZIL/GSM/OS-B&C
Work stations :: ZIL/GSM/CLIENT-1 | d874f39f176a | ZIL/GSM/CLIENT-1
Work stations :: ZIL/GSM/CLIENT-2 | 3293ed79696b | ZIL/GSM/CLIENT-2
Work stations :: ZIL/GSM/OS-SEDL | ad1b56012e2b | ZIL/GSM/OS-SEDL
Fire control panel :: ZIL/GSM/FA-01 | 8938859f7f9d | ZIL/GSM/FA-01
Fire control panel :: ZIL/GSM/FA-02 | 76748315eff8 | ZIL/GSM/FA-02
Fire control panel :: ZIL/GSM/FA-03 | cc7fd480dc3e | ZIL/GSM/FA-03
B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | 70ee7410612a | ZIL/SUG./B.COMP-CT-05
FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | 3370e96b2811 | ZIL/SUG./01/16.FT.075.B01
VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | 969d52681150 | ZIL/SUG./001/SY_B_MOL_CV2
DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | 09d54898090a | ZIL/SUG./01/Vacuum-FM-01
DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | 910c1c18dcc0 | ZIL/SUG./01/DIST.-TWFM-2
DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | 7b6e4014649d | ZIL/SUG./01/ETP-DECANTER-FM
D.B.F 14 :: ZIL/SUG./001 (40FCV201) | e71a9add8164 | ZIL/SUG./001 (40FCV201)

## EQUIPMENT LIFE HISTORY CARD
sheet id | sheet name | EQUIPMENT TAG NAME/APPLICATION | NAME OF EQUIPMENT | LOCATION | DATE OF COMMISSIONING
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE | SUGAR PLANT-3 MW OLD POWER TURBINE | 1996-06-06
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE | SUGAR PLANT-3 MW NEW POWER TURBINE | 1996-06-06
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Mill turbine-01 | SUGAR PLANT-Mill turbine-01 | 1996-06-06
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve | SUGAR UNIT - Mill Imbibition Control Valve 01 | 2015
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve | SUGAR UNIT - Mill Imbibition Control Valve 02 | 2015
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve | SUGAR UNIT - Mill Imbibition Tank Control Valve | 2015
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve | SUGAR UNIT - Rotary screen Valve 01(A) | 2015
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve | SUGAR UNIT - Rotary screen Valve 01(B) | 2015
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | Leval sensor | SUGAR UNIT - Zero mill Chute Level sensor | 2015
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | Leval sensor | SUGAR UNIT - 1st Mill Chute Level sensor | 2015
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | Leval sensor | SUGAR UNIT - 2nd Mill Chute Level sensor | 2015
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | Leval sensor | SUGAR UNIT - 3rd Mill Chute Level sensor | 2015
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | Leval sensor | SUGAR UNIT - 4th Mill Chute Level sensor | 2015
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | Shreder -1 | SUGAR UNIT - Shreder LHS Side | 2015
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | Pressure,Level,Temperature Tx. | SUGAR UNIT - Condensate Flush Tank | 2015
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | Temperature Tx. | SUGAR UNIT - Vapour Line juice Heater(VLJH) & Condensate Heater | 2015
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | Temperature Tx. | SUGAR UNIT - Deficated Juice heater (DJ) | 2015
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | Level Transmitter | SUGAR UNIT - R/F Quad Level Transmitter | 2015
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | pH Transmitter | SUGAR UNIT - R/F Quad Deficator pH | 2015
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | pH Transmitter | SUGAR UNIT - R/F MCS melt pH | 2015
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | Vibration Transmitter | SUGAR UNIT - 3 MW New Power Turbine | 2025
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter | SUGAR UNIT - 3 MW Old Power Turbine | 2025
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve | SUGAR UNIT - DCH Tower Refinery 01 | 2015
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve | SUGAR UNIT - DCH Tower Refinery 02 | 2015
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve | SUGAR UNIT - DCH Tower Refinery 03 | 2015
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve | SUGAR UNIT - DCH Tower Refinery 04 | 2015
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve | SUGAR UNIT - Raw & Refinery (Quad ) R J Heater 1 | 2015
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve | SUGAR UNIT - Raw & Refinery (Quad ) R J Heater 2 | 2015
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve | SUGAR UNIT - Raw SRT Pump O/L line valve | 2015
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve | SUGAR UNIT - 3 ATA Intermixsing Valve | 2015
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve | SUGAR UNIT - Melt Concetrator O/L Control Valve | 2015
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve | SUGAR UNIT - Raw DCH A HEAVY 01 | 2015
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve | SUGAR UNIT - Raw DCH C- LIGHT 02 | 2015
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve | SUGAR UNIT - Raw DCH BH -03 | 2015
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve | SUGAR UNIT - Raw DCH R3 MOLASSES 04 | 2015
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve | SUGAR UNIT - SCS Control Valve | 2015
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve | SUGAR UNIT - B Conti.Compartment No 01 | 2015
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve | SUGAR UNIT - B Conti.Compartment No 02 | 2015
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve | SUGAR UNIT - B Conti.Compartment No 03 | 2015
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve | SUGAR UNIT - B Conti.Compartment No 04 | 2015
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve | SUGAR UNIT - B Conti.Compartment No 07 | 2015
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve | SUGAR UNIT - B Conti.Compartment No 08 | 2015
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve | SUGAR UNIT - B Conti.Compartment No 09 | 2015
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve | SUGAR UNIT - B Conti.Compartment No 10 | 2015
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve | SUGAR UNIT - B Conti.Compartment No 11(Only Electrode) | 2015
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve | SUGAR UNIT - C Conti.Compartment No 1 | 2015
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve | SUGAR UNIT - C Conti.Compartment No 2 | 2015
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve | SUGAR UNIT - C Conti.Compartment No 3 | 2015
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve | SUGAR UNIT - C Conti.Compartment No 4 | 2015
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve | SUGAR UNIT - C Conti.Compartment No 5 | 2015
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve | SUGAR UNIT - C Conti.Compartment No 6 | 2015
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve | SUGAR UNIT - C Conti.Compartment No 7 | 2015
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve | SUGAR UNIT - C Conti.Compartment No 8 | 2015
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve | SUGAR UNIT - C Conti.Compartment No 09 | 2015
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve | SUGAR UNIT - C Conti.Compartment No 10 | 2015
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve | SUGAR UNIT - C Conti.Compartment No 11 (Only Electrode) | 2015
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve | SUGAR UNIT - Raw Meltar Leval Control Valve | 2015
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve | SUGAR UNIT - Raw Meltar Steam Control Valve | 2015
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve | SUGAR UNIT - Raw Meltar Water Control Valve | 2015
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve | SUGAR UNIT - Raw Meltar Bricks Sampler | 2015
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve | SUGAR UNIT - Raw B.H. Leval Control Valve | 2015
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve | SUGAR UNIT - Hot water line Valve Near Vartical Crystlizer | 2015
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve | SUGAR UNIT - Cold Water storage tank from CPU Line | 2015
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve | SUGAR UNIT - Cold water storage tank from tube-well | 2015
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve | SUGAR UNIT - RAW PAN No 01 Auto feed Valve | 2015
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve | SUGAR UNIT - RAW PAN No 02 Auto feed Valve | 2015
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve | SUGAR UNIT - RAW PAN No 03 Auto feed Valve | 2015
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve | SUGAR UNIT - RAW PAN No 04 Auto feed Valve | 2015
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve | SUGAR UNIT - RAW PAN No 05 Auto feed Valve | 2015
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve | SUGAR UNIT - Raw House BC Meltar Control Valve | 2015
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve | SUGAR UNIT - Raw House Steam Valve Exhust steam to PHE I/L temp. control valve | 2015
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve | SUGAR UNIT -Raw House Steam Valve Exhust steam to PHE I/L Pressure control valve | 2015
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve | SUGAR UNIT -Raw Crystlizer Power Cylinder- 01 | 2015
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve | SUGAR UNIT -Raw Crystlizer Power Cylinder- 02 | 2015
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve | SUGAR UNIT -Raw Crystlizer Power Cylinder- 03 | 2015
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve | SUGAR UNIT - Concentrator MOV Near C Cont. 01 | 2015
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve | SUGAR UNIT - Concentrator MOV Near C Cont. 02 | 2015
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve | SUGAR UNIT - Concentrator MOV Near Raw Safety valve Cont. 03 | 2015
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve | SUGAR UNIT - Raw House Meltconcetrtor 1sT Body I/L | 2015
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve | SUGAR UNIT - Raw House Meltconcentrtor 2nd Body I/L | 2015
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve | SUGAR UNIT - Raw House Meltconcetrtor 3rd Body I/L | 2015
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve | SUGAR UNIT - Raw Quad Lime Control Valve | 2015
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve | SUGAR UNIT - Raw Quad 800 A Body Syrup I/L | 2015
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve | SUGAR UNIT - Raw Quad 800 B Body O/L Control Valve | 2015
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve | SUGAR UNIT - Raw Quad 800 B Body Syrup I/L | 2015
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve | SUGAR UNIT - Raw Quad 800 A Body Syrup I/L | 2015
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve | SUGAR UNIT - Raw Quad 1000 Body Syrup I/L | 2015
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve | SUGAR UNIT -Raw Quad 836 Body I/L Valve | 2015
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve | SUGAR UNIT -Raw Quad 2500 A Body I/L Valve | 2015
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve | SUGAR UNIT -Raw Quad 2500 B Body I/L Valve | 2015
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve | SUGAR UNIT -Raw Quad 3800 Body I/L Valve | 2015
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve | SUGAR UNIT -Raw Quad FFE 1250 Body I/L Valve | 2015
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve | SUGAR UNIT - S K 2500 Body I/L Valve | 2015
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve | SUGAR UNIT - Raw Quad Safety Valve | 2015
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter | SUGAR UNIT -DS House | 2016
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter | SUGAR UNIT - Refinery House | 2016
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter | SUGAR UNIT - DS | 2016
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery | SUGAR UNIT - Refinery | 2016
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water | SUGAR UNIT - Imbibition water flow near mill no-03 | 2016
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter | SUGAR UNIT - Rotary Hot Water | 2016
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter | SUGAR UNIT - Near 70 TPH UGR FLOW METER | 2016
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter | SUGAR UNIT - CPU line To cold storage tank Flow meter | 2016
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter | SUGAR UNIT - Near 3 MW Flow Meter | 2016
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter | SUGAR UNIT - Mud O/L Flow Meter | 2016
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter | SUGAR UNIT -Raw Quad Deficated Juice Flow meter | 2016
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter | SUGAR UNIT - Raw quad Lime flow meter | 2016
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter | SUGAR UNIT - Raw Quad D-Sweeting Hot water | 2016
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter | SUGAR UNIT -Raw Quad Hot water Clear Juice-SRT | 2016
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter | SUGAR UNIT - Raw Quad Magnafloc Dosing | 2016
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter | SUGAR UNIT - Raw Quad Syrup Extraction | 2016
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter | SUGAR UNIT -Raw Quad Scum Transfer Pump | 2016
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter | SUGAR UNIT - Raw Pan C Conti. Pan Feed line | 2016
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter | SUGAR UNIT - C Conti. Pan Condenset line | 2016
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter | SUGAR UNIT - B Conti. Pan Feed line | 2016
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter | SUGAR UNIT - B Conti. Pan Condenset line | 2016
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter | SUGAR UNIT -B Conti. Pan Grain flow meter | 2016
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter | SUGAR UNIT - C Conti. Pan Grain Flow Meter | 2016
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter | SUGAR UNIT - Raw Quad DCH Syrup I/L Line | 2016
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter | SUGAR UNIT - Raw Quad Over Head Tank | 2016
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter | SUGAR UNIT - Near Boiler UGR | 2016
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter | SUGAR UNIT - Admin Bulding Flow meter | 2016
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter | SUGAR UNIT - STP Plant Flow meter | 2016
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter | SUGAR UNIT - Truck Yard flow meter | 2016
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter | SUGAR UNIT - Disterlly tubewell Flow Meter | 2016
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine | SUGAR UNIT - L-Duplex weighing Machine (Refinery house) | 2016
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine | SUGAR UNIT - M-Duplex weighing Machine (Refinery house) | 2016
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine | SUGAR UNIT - S-Duplex Weighing Machine (Refinery house) | 2016
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine | SUGAR UNIT - 25 KG Simplex Weighing Machine (Refinery house) | 2016
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine | SUGAR UNIT - Pharma Duplex Weighing Machine (Refinery house) | 2016
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | B Centrifugal Machine | SUGAR UNIT - B Centrifugal Machine-1 (Raw house) | 2016
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | B Centrifugal Machine | SUGAR UNIT - B Centrifugal Machine-2 (Raw house) | 2016
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | B Centrifugal Machine | SUGAR UNIT - B Centrifugal Machine-3 (Raw house) | 2016
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | B Centrifugal Machine | SUGAR UNIT - B Centrifugal Machine-4 (Raw house) | 2016
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | C Centrifugal Machine | SUGAR UNIT - C Centrifugal Machine-1 (Raw house) | 2016
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | C Centrifugal Machine | SUGAR UNIT - C Centrifugal Machine-2 (Raw house) | 2016
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | C Centrifugal Machine | SUGAR UNIT - C Centrifugal Machine-3 (Raw house) | 2016
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | Raw Centrifugal Machine Drive | SUGAR UNIT - Raw Centrifugal Machine-1 (Raw house) | 2016
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | Refinery Centrifugal Machine Drive | SUGAR UNIT - Refinery Centrifugal Machine-1 (Refinery) | 2016
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | Air Compressure | SUGAR UNIT - Air Compressure -01 | 2016
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | Air Compressure | SUGAR UNIT - Air Compressure -02 | 2016
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | Air Compressure | SUGAR UNIT - Air Compressure -03 | 2016
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | Air Compressure | SUGAR UNIT - Air Compressure -04 | 2016
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | Air Compressure | SUGAR UNIT - Air Compressur Dryer -1 | 2016
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | Air Compressure | SUGAR UNIT - Air Compressur Dryer -2 | 2016
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve | SUGAR UNIT - DS PAN No 01 Auto feed Valve | 2000
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve | SUGAR UNIT - DS PAN No 02 Auto feed Valve | 2000
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve | SUGAR UNIT - DS PAN No 03 Auto feed Valve | 2000
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve | SUGAR UNIT - DS PAN No 04 Auto feed Valve | 2000
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve | SUGAR UNIT - DS PAN No 05 Auto feed Valve | 2000
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve | SUGAR UNIT - DS PAN No 06 Auto feed Valve | 2000
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve | SUGAR UNIT - DS PAN No 07 Auto feed Valve | 2000
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve | SUGAR UNIT - DS PAN No 08 Auto feed Valve | 2000
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve | SUGAR UNIT - DS PAN No 09 Auto feed Valve | 2000
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve | SUGAR UNIT - DS PAN No 10 Auto feed Valve | 2000
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve | SUGAR UNIT - DS PAN No 11 Auto feed Valve | 2000
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve | SUGAR UNIT - DS PAN No 12 Auto feed Valve | 2000
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve | SUGAR UNIT - B Continuous Pan No .13 Auto feed Valve No1
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve | SUGAR UNIT - B Continuous Pan No .13 Auto feed Valve No2 | 2000
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve | SUGAR UNIT - B Continuous Pan No .13 Auto feed Valve No 3 | 2000
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve | SUGAR UNIT - B Continuous Pan No .13 Auto feed Valve No 4 | 2000
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve | SUGAR UNIT - PAN No.01 Vacuum breaker | 2025
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve | SUGAR UNIT - PAN No.02 Vacuum breaker | 2025
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve | SUGAR UNIT - PAN No.03 Vacuum breaker | 2025
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve | SUGAR UNIT - PAN No.08 Vacuum breaker | 2025
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve | SUGAR UNIT - PAN No .10 Vacuum breaker | 2025
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve | SUGAR UNIT - Pan No .11 Vacuum breaker | 2025
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve | SUGAR UNIT - Pan No .12 Vacuum breaker | 2025
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve | SUGAR UNIT- DS Exhaust Pressure Control valve
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve | SUGAR UNIT - DS D-Supper Heating control valve 01 | 2000
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve | SUGAR UNIT - DS D-Supper Heating control valve 02 | 2000
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve | SUGAR UNIT - DS 2nd Vapour DCH Control Valve | 2016
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve | SUGAR UNIT - DS 2nd Vapour B/C Pan | 2016
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve | SUGAR UNIT - DS 2 nd Vapour A Pan | 2016
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve | SUGAR UNIT - DS 3rd A QUAD | 2016
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve | SUGAR UNIT - DS 3rd B QUAD | 2016
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve | SUGAR UNIT - DS 3rd C QUAD | 2016
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve | SUGAR UNIT - DS 4th A QUAD | 2016
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve | SUGAR UNIT - DS 4th B Quad | 2016
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve | SUGAR UNIT DS 4th C Quad | 2016
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve | SUGAR UNIT - DS 5th A QUAD | 2016
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve | SUGAR UNIT - DS 5th B QUAD | 2016
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve | SUGAR UNIT - DS 5th C QUAD | 2016
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve | SUGAR UNIT - DS Over Head Crystllizer Water temp control | 2000
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve | SUGAR UNIT - B Molasses tank level Control valve | 2000
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve | SUGAR UNIT - DS 1250 Falling Film Juice line Valve
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve | SUGAR UNIT - 2500 Falling Film Juice line Valve
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve | SUGAR UNIT - DS 2500 Vapaur cell juice line | 2000
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve | SUGAR UNIT - DS Sulphited juice heater 2nd heating
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve | SUGAR UNIT - DS MOL FLOW | 2000
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve | SUGAR UNIT - DS S.H.W.W.
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve | SUGAR UNIT DS-2500 Falling Film vapour line
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve | SUGAR UNIT - DS 2500 Vapour Cell Vapour Line
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve | SUGAR UNIT-DS A Havy molasses condinser
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve | SUGAR UNIT - DS Syrup to SCS | 2022
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve | SUGAR UNIT - DS E Boiler water Level Control. | 2008
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve | SUGAR UNIT - DS Syrup level control | 2019
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve | SUGAR UNIT - DS Syrup weingh Scale Inlet | 2022
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve | SUGAR UNIT - DS Syrup weingh Scale Outlet | 2022
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve | SUGAR UNIT - DS B havey weighing scale inlet | 2021
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve | SUGAR UNIT - DS B havey weighing scale outlet | 2021
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve | SUGAR UNIT - DS 10 TON weingh Scale Valve-1 | 2022
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve | SUGAR UNIT - DS 10 TON weingh Scale Valve-2 | 2022
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve | SUGAR UNIT - DS 10 TON weingh Scale Valve-3 | 2021
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve | SUGAR UNIT - Decanter-1 Mud I/L Valve | 2025
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve | SUGAR UNIT - Decanter-1 Hot water I/L Valve | 2025
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve | SUGAR UNIT - Decanter-02 Hot water I/L Valve | 2025
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve | SUGAR UNIT - Hot water I/L Valve | 2025
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve | SUGAR UNIT - C Continuous Machine Transient Heater Contol Valve 1 | 2009
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve | SUGAR UNIT - C Continuous Machine Transient Heater Contol Valve 2 | 2009
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve | SUGAR UNIT - C Continuous Machine Transient Heater Contol Valve 3 | 2009
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve | SUGAR UNIT - C Continuous Machine Transient Heater Contol Valve 4 | 2009
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve | SUGAR UNIT - C Continuous Machine Transient Heater Contol Valve 5 | 2009
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve | SUGAR UNIT - C Continuous Machine Transient Heater Contol Valve 6 | 2025
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | Control valve | SUGAR UNIT - Injection Header Pressure Cantrol Valve | 2009
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | Control valve | SUGAR UNIT - DS Spray Systam Overhead Tank level control | 2009
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | Control valve | SUGAR UNIT - Overhead crystallizer water temp. Control | 2009
da94085bd25e | Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | ZIL/SUG./SULPHER/PANEL | Temperature Indicator | SUGAR UNIT - Batch Type Sulpher Furnece | 2010
c2b506d4463f | Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | ZIL/SUG./FILM/PANEL | Temperature Indicator | SUGAR UNIT - Film Type Sulpher fernace | 2008
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | DS Centrifugal Machine Drive | SUGAR UNIT - Refinery Centrifugal Machine-1 (DS) | 2000
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter | SUGAR UNIT - Clear Juice Flow | 2016
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter | SUGAR UNIT - IIA 2500FFE IL Juice Flow | 2016
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter | SUGAR UNIT - IIB 1250FFE IL Juice Flow | 2016
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter | SUGAR UNIT - A & B Cond Flow | 2016
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter | SUGAR UNIT - Mol Flow | 2016
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter | SUGAR UNIT - Filterate Flow | 2016
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter | SUGAR UNIT - Water flow vacuum filter 14/36[2] | 2016
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter | SUGAR UNIT -Water flow meter near Pan no 04 | 2016
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter | SUGAR UNIT - Flow meter B havy DS | 2016
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter | SUGAR UNIT - Flow Meter DS Spray O/L ETP | 2016
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter | SUGAR UNIT - Flow Meter Spray System Overheade tank | 2016
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter | SUGAR UNIT - Flow Meter Ref. Cooling Tower O/L ETP | 2016
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter | SUGAR UNIT - Flow Meter ETP (1) Inlet | 2016
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter | SUGAR UNIT - Flow Meter ETP(2) Outlet | 2025
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter | SUGAR UNIT - Flow Meter ETP(3) to B Vertical | 2016
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter | SUGAR UNIT - Flow Meter ETP Hydrojet | 2024
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter | SUGAR UNIT - Flow Meter Overhead Tank to Cooling Tower | 2016
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter | SUGAR UNIT - Mass Flow Meter DS Syrup Line | 2022
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter | SUGAR UNIT - B Continuous Pan Water line | 2024
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter | SUGAR UNIT -B Continuous Pan Condonset line | 2024
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter | SUGAR UNIT - B Continuous Pan Grain line | 2024
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter | SUGAR UNIT - Decanter 01- I/L Flow Meter | 2025
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter | SUGAR UNIT - Decanter 02- I/L Flow Meter | 2025
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter | SUGAR UNIT - Decanter- 01 O/L flow meter (Centric-01) | 2025
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter | SUGAR UNIT - Decanter- 02 O/L flow meter (Centric-02) | 2025
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter | SUGAR UNIT - Decanter- 01 O/L Hot Water | 2025
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser | SUGAR UNIT -Accuamlator Pump 1 & 2 | 2006
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser | SUGAR UNIT -DS EVP- A SET Condenser | 2006
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser | SUGAR UNIT -DS EVP- B SET Condenser | 2006
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser | SUGAR UNIT -DS EVP- C SET Condenser | 2006
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser | SUGAR UNIT -DS Pan No 1 Condenser | 2006
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser | SUGAR UNIT -DS Pan No 2 Condenser | 2006
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser | SUGAR UNIT -DS Pan No 4 Condenser | 2006
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser | SUGAR UNIT -DS Pan No 6 Condenser | 2006
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser | SUGAR UNIT -DS Pan No 7 Condenser | 2006
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser | SUGAR UNIT -DS Pan No 8 Condenser | 2006
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser | SUGAR UNIT -DS Pan No 9 Condenser | 2006
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser | SUGAR UNIT -DS Pan No 10 Condenser | 2006
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser | SUGAR UNIT -DS Pan No 11 condenser | 2006
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser | SUGAR UNIT -DS Pan No 12 Condenser | 2006
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser | SUGAR UNIT -DS Pan No 13 Condenser | 2006
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine | SUGAR UNIT - M-1 Simplex Weighing Machine (DS house) | 2016
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine | SUGAR UNIT - M-2 Simplex Weighing Machine (DS house) | 2016
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine | SUGAR UNIT -S Simplex Weighing Machine (DS house) | 2016
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine | SUGAR UNIT - L Simplex Weighing Machine (DS house) | 2016
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve | SUGAR UNIT - :DBF 1 Flow control valve ( MCS Refinery) | 2015
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- | SUGAR UNIT - :DBF 1 Feed valve ( MCS Refinery) | 2015
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve | SUGAR UNIT - :DBF 1 Vent valve ( MCS Refinery) | 2015
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve | SUGAR UNIT - :DBF 1 Drain Down valve ( MCS Refinery) | 2015
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve | SUGAR UNIT - :DBF 1 Filtrate melt outlet valve ( MCS Refinery) | 2015
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve | SUGAR UNIT - :DBF 1 Air sperge valve ( MCS Refinery) | 2015
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve | SUGAR UNIT - :DBF 1 Back Wash valve ( MCS Refinery) | 2015
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve | SUGAR UNIT - :DBF 2 Feed valve ( MCS Refinery) | 2015
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve | SUGAR UNIT - :DBF 2 Vent valve ( MCS Refinery) | 2015
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve | SUGAR UNIT - :DBF 2 Drain Down valve ( MCS Refinery) | 2015
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve | SUGAR UNIT - :DBF 2 Filtrate melt outlet valve ( MCS Refinery) | 2015
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve | SUGAR UNIT - :DBF 2 Air sparge ( MCS Refinery) | 2015
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve | SUGAR UNIT - :DBF 2 Back wash valve ( MCS Refinery) | 2015
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve | SUGAR UNIT - :DBF Back wash valve ( MCS Refinery) | 2015
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve | SUGAR UNIT - I.E.R Column No 1 Melt Inltet Flow Control Valve (Refinery) | 2015
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve | SUGAR UNIT - I.E.R Column No 1 Melt Inltet Control Valve (Refinery) | 2015
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve | SUGAR UNIT - I.E.R Column No 1 Recovered/Back wash water Control Valve | 2015
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve | SUGAR UNIT - I.E.R Column No 1 Sweetring drain liquier Valve (Refinery) | 2015
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve | SUGAR UNIT -I.E.R Column No 1 Sweet Water drain Control Valve | 2015
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve | SUGAR UNIT - I.E.R Column No 1 Effluent /Brine Discharge Control Valve (Refinery) | 2015
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve | SUGAR UNIT - I.E.R Column No 1 Air Inlet Control Valve (Refinery) | 2015
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve | SUGAR UNIT - I.E.R Column No 1 Back wash outlet Control Valve (Refinery) | 2015
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve | SUGAR UNIT - I.E.R Column No 1 Air Vent Control Valve (Refinery) (To Effluent) | 2015
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve | SUGAR UNIT-I.E.R Column No 1 Chemical & Hot water Inltet Control Valve (Refinery) | 2015
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve | SUGAR UNIT - I.E.R Column No 1 Declourised liquor Control Valve (Refinery) | 2015
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve | SUGAR UNIT -I.E.R Column No 1 Sweetring on drain liquor Control Valve(Refinery) | 2015
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve | SUGAR UNIT - I.E.R Column No 1 Sweetring on Effluent drain Control Valve | 2015
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve | SUGAR UNIT - I.E.R Column No 2 Melt Inltet Flow Control Valve (Refinery) | 2015
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve | SUGAR UNIT - I.E.R Column No 2 Melt Inltet Control Valve (Refinery) | 2015
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve | SUGAR UNIT - I.E.R Column No 2 Recovered/Back wash water Control Valve | 2015
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve | SUGAR UNIT - I.E.R Column No 2 Sweetring drain liquier Valve (Refinery) | 2015
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve | SUGAR UNIT -I.E.R Column No 2 Sweet Water drain Control Valve | 2015
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve | SUGAR UNIT - I.E.R Column No 2 Effluent /Brine Discharge Control Valve (Refinery) | 2015
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve | SUGAR UNIT - I.E.R Column No 2 Air Inlet Control Valve (Refinery) | 2015
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve | SUGAR UNIT - I.E.R Column No 2 Back wash outlet Control Valve (Refinery) | 2015
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve | SUGAR UNIT - I.E.R Column No 2 Air Vent Control Valve (Refinery) (To Effluent) | 2015
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve | SUGAR UNIT-I.E.R Column No 2 Chemical & Hot water Inltet Control Valve (Refinery) | 2015
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve | SUGAR UNIT - I.E.R Column No 2 Declourised liquor Control Valve (Refinery) | 2015
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve | SUGAR UNIT -I.E.R Column No 2 Sweetring on drain liquor Control Valve(Refinery) | 2015
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve | SUGAR UNIT - I.E.R Column No 3 Sweetring on Effluent drain Control Valve | 2015
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve | SUGAR UNIT - I.E.R Column No 3 Melt Inltet Flow Control Valve (Refinery) | 2015
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve | SUGAR UNIT - I.E.R Column No 3 Melt Inltet Control Valve (Refinery) | 2015
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve | SUGAR UNIT - I.E.R Column No 3 Recovered/Back wash water Control Valve | 2015
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve | SUGAR UNIT - I.E.R Column No 3 Sweetring drain liquier Valve (Refinery) | 2015
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve | SUGAR UNIT -I.E.R Column No 3 Sweet Water drain Control Valve | 2015
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve | SUGAR UNIT - I.E.R Column No 3 Effluent /Brine Discharge Control Valve (Refinery) | 2015
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve | SUGAR UNIT - I.E.R Column No 3 Air Inlet Control Valve (Refinery) | 2015
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve | SUGAR UNIT - I.E.R Column No 3 Back wash outlet Control Valve (Refinery) | 2015
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve | SUGAR UNIT - I.E.R Column No 3 Air Vent Control Valve (Refinery) (To Effluent) | 2015
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve | SUGAR UNIT-I.E.R Column No 3 Chemical & Hot water Inltet Control Valve (Refinery) | 2015
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve | SUGAR UNIT - I.E.R Column No 3 Declourised liquor Control Valve (Refinery) | 2015
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve | SUGAR UNIT -I.E.R Column No 3 Sweetring on drain liquor Control Valve(Refinery) | 2015
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve | SUGAR UNIT - I.E.R Column No 3 Sweetring on Effluent drain Control Valve | 2015
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve | SUGAR UNIT - I.E.R Column Sweetring off Common Syphon Melt Drain Control Valve | 2015
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve | SUGAR UNIT -I.E.R Column Common Brine Discharge Syphon Control Valve | 2015
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve | SUGAR UNIT -I.E.R Column Sweetring off Common Syphon Sweet water drain Control Valve | 2015
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve | SUGAR UNIT -I.E.R Column outlet common line recirculation to IER feed tank Control Valve | 2015
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve | SUGAR UNIT -I.E.R Column common outlet line to decoloursied tank Control Valve | 2015
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve | SUGAR UNIT -Brine PTHE Steam control valve (Refinery) | 2015
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve | SUGAR UNIT -Brine sand filter inlet control valve (Refinery) | 2015
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve | SUGAR UNIT -Brine sand filter by pass control valve (Refinery) | 2015
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve | SUGAR UNIT -Brine sand filter outlet control valve (Refinery) | 2015
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve | SUGAR UNIT - I.E.R Column No 4 Melt Inltet Flow Control Valve (Refinery) | 2026
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve | SUGAR UNIT - MCS DCH MELT Temp Control Valve (Refinery) | 2015
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve | SUGAR UNIT -MCS DCH MELT Flow Control Valve (Refinery) | 2015
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve | SUGAR UNIT -DCH Molasses R1 Temp Control Valve (Refinery) | 2015
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve | SUGAR UNIT -DCH Molasses R2 Temp Control Valve (Refinery) | 2015
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve | SUGAR UNIT - Hot Water tank temp. control valve (Refinery) | 2015
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve | SUGAR UNIT - Hot Water Pump flow control valve (Refinery) | 2015
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve | SUGAR UNIT - Hot water pump delivery line control valve (Refinery) | 2015
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve | SUGAR UNIT - Recovered water pump delivery line flow contol valve (Refinery) | 2015
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve | SUGAR UNIT - Recovered water pump delivery line contol valve (Refinery) | 2015
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve | SUGAR UNIT - Column brine / water discharge line to valve to BRS (Refinery) | 2015
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve | SUGAR UNIT - Column brine / water discharge line to valve to recovered water tank (Refinery) | 2015
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve | SUGAR UNIT - Saturated brine pump delivery line flow control valve (Refinery) | 2015
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve | SUGAR UNIT - Saturated brine pump delivery line control valve (Refinery) | 2015
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve | SUGAR UNIT - Hot water /recovered water common header valve to column back wash | 2015
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve | SUGAR UNIT - Sweet water tank hot water level control valve | 2015
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve | SUGAR UNIT- Hot water /recovered water common header valve to sand filter PTHE. (Refinery) | 2015
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve | SUGAR UNIT - Sweet water tank steam control valve (Refinery) | 2015
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve | SUGAR UNIT -FBD Heater air flow control valve (Refinery) | 2015
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve | SUGAR UNIT - Primary Sugar dust Tank water level Control valve (Refinery) | 2015
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve | SUGAR UNIT -Refinery Exhaust steam to PHE I/L Temp. control valve(SHWW) | 2015
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve | SUGAR UNIT - Refinery Exhaust steam to PHE I/L Pressure control valve(SHWW) | 2015
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve | SUGAR UNIT - B.R.S Brine Control valve (Refinery) | 2015
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve | SUGAR UNIT - Refinary PAN No 2 Auto feed Valve | 2015
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve | SUGAR UNIT -Cooling condenser Main Valve Raw. Pan.no.1 | 2015
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve | SUGAR UNIT -Cooling condenser Jet valve Raw. Pan.no.1 | 2015
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve | SUGAR UNIT -Cooling condenser Spray 1 valve Raw. Pan.no.1 | 2015
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve | SUGAR UNIT -Cooling condenser Spray 2 valve Raw Pan.no.1 | 2015
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve | SUGAR UNIT -Cooling condenser Jet valve RAW. Pan.no.2 (Refinery) | 2015
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve | SUGAR UNIT -Cooling condenser Spray valve RAW. Pan.no.2 (Refinery) | 2015
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve | SUGAR UNIT -Cooling condenser Spray valve RAW. Pan.no.2 (Refinery) | 2015
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve | SUGAR UNIT -Cooling condenser Spray valve RAW. Pan.no.2 (Refinery) | 2015
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve | SUGAR UNIT -Cooling condenser Jet valve RAW. Pan.no.3 (Refinery) | 2015
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve | SUGAR UNIT -Cooling condenser Main valve RAW. Pan.no.4 (Refinery) | 2015
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve | SUGAR UNIT -Cooling condenser Spray valve RAW. Pan.no.4 (Refinery) | 2015
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve | SUGAR UNIT -Cooling condenser Spray valve RAW. Pan.no.4 (Refinery) | 2015
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve | SUGAR UNIT -Cooling condenser spray valve RAW. Pan.no.4 (Refinery) | 2015
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve | SUGAR UNIT -Cooling condenser Jet valve RAW. Pan.no.4 (Refinery) | 2015
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve | SUGAR UNIT -Cooling condenser Main valve RAW. Pan.no.5 (Refinery) | 2015
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve | SUGAR UNIT -Cooling condenser Jet valve RAW. Pan.no.5 (Refinery) | 2015
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve | SUGAR UNIT -Cooling condenser Spray valve RAW. Pan.no.5 (Refinery) | 2015
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve | SUGAR UNIT -Cooling condenser Main valve B Continuous Pan (Refinery) | 2015
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve | SUGAR UNIT -Cooling condenser Spray valve B Continuous Pan (Refinery) | 2015
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve | SUGAR UNIT -Cooling condenser Spray valve B Continuous Pan (Refinery) | 2015
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve | SUGAR UNIT -Cooling condenser Jet valve B Continuous Pan (Refinery) | 2015
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve | SUGAR UNIT -Cooling condenser jet valve C Continuous Pan (Refinery) | 2015
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve | SUGAR UNIT -Cooling condenser Spray valve C Continuous Pan (Refinery) | 2015
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve | SUGAR UNIT -Cooling condenser Spray valve C Continuous Pan (Refinery) | 2015
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve | SUGAR UNIT -Cooling condenser main valve C Continuous Pan (Refinery) | 2015
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve | SUGAR UNIT -Cooling condenser Main Valve Refinery Pan No.1 (Refinery) | 2015
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Refinery Pan No.1 (Refinery) | 2015
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Refinery Pan No.1 (Refinery) | 2015
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve | SUGAR UNIT -Cooling condenser Jet valve Refinery Pan No.1 (Refinery) | 2015
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve | SUGAR UNIT -Cooling condenser Main Valve Refinery Pan No.2 (Refinery) | 2015
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Refinery Pan No.2 (Refinery) | 2015
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Refinery Pan No.2 (Refinery) | 2015
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve | SUGAR UNIT -Cooling condenser Jet valve Refinery Pan No.2 (Refinery) | 2015
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve | SUGAR UNIT -Cooling condenser Main Valve Refinery Pan No.3 (Refinery) | 2015
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Refinery Pan No.3 (Refinery) | 2015
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Refinery Pan No.3 (Refinery) | 2015
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve | SUGAR UNIT -Cooling condenser Jet valve Refinery Pan No.3 (Refinery) | 2015
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve | SUGAR UNIT -Cooling condenser Main Valve Melt Concentrator (Refinery) | 2015
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Melt Concentrator (Refinery) | 2015
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Melt Concentrator (Refinery) | 2015
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve | SUGAR UNIT -Cooling condenser Jet valve Melt Concentrator (Refinery) | 2015
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve | SUGAR UNIT -Cooling condenser Main Valve Evaporator A set (Refinery) | 2015
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Evaporator A set (Refinery) | 2015
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Evaporator A set (Refinery) | 2015
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Evaporator A set (Refinery) | 2015
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve | SUGAR UNIT -Cooling condenser Jet valve Evaporator A set (Refinery) | 2015
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve | SUGAR UNIT -Cooling condenser Main Valve Evaporator B set (Refinery) | 2015
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Evaporator B set (Refinery) | 2015
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Evaporator B set (Refinery) | 2015
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve | SUGAR UNIT -Cooling condenser Spray valve Evaporator B set (Refinery) | 2015
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve | SUGAR UNIT -Cooling condenser Jet valve Evaporator B set (Refinery) | 2015
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve | SUGAR UNIT -Cooling condenser Jet valve R3 PAN | 2025
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve | SUGAR UNIT -Cooling condenser spray valve R3 PAN | 2025
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve | SUGAR UNIT - Crystlizer No 1. Power Cylender (Refinery) | 2015
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve | SUGAR UNIT - Crystlizer No 2. Power Cylender (Refinery) | 2015
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve | SUGAR UNIT - Crystlizer No 3. Power Cylender (Refinery) | 2015
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter | SUGAR UNIT -Refinery Ground Floor Decolorised Liqour Tank Outlet | 2016
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter | SUGAR UNIT - Refinery Ground Floor Sweet Water | 2016
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter | SUGAR UNIT - DCH Untreated Melt Feed | 2016
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter | SUGAR UNIT - MCS refinery DBF Backwash | 2016
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter | SUGAR UNIT -Refinery MCS DBF 1 Liqour Feed I/L | 2016
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter | SUGAR UNIT - Refinery MCS DBF 2 Liqour Feed I/L | 2016
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER | SUGAR UNIT - REFINERY GROUND FLOOR HOT WATER | 2016
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER | SUGAR UNIT -REFINERY GROUND FLOOR RECOVERED WATER | 2016
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER | SUGAR UNIT - REFINERY GROUND FLOOR SATURATED BRINE OUTLET | 2016
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER | SUGAR UNIT - MCS IER COLUMN 1 FEED | 2016
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER | SUGAR UNIT -MCS IER COLUMN 2 FEED | 2016
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER | SUGAR UNIT -MCS IER COLUMN 3 FEED | 2016
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter | SUGAR UNIT - Refinery BRS 1st Stage Feed In | 2016
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter | SUGAR UNIT - Refinery BRS 1st Stage Feed Out | 2016
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter | SUGAR UNIT - Refinery BRS 1st Stage Reject Tank | 2016
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter | SUGAR UNIT - Refinery BRS 2nd Stage Permit Tank | 2016
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter | SUGAR UNIT - Refinery BRS 2nd Stage Reject Tank | 2016
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter | SUGAR UNIT - Refinery BRS 2nd Stage Recycle | 2016
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER | SUGAR UNIT -MCS IER COLUMN 4 FEED | 2025
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C1 CPU PANEL RAW HOUSE | 2016
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C2 CPU PANEL RAW HOUSE | 2016
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C3 CPU PANEL MILL HOUSE | 2016
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C4 CPU PANEL REFINERY HOUSE | 2016
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C1 I/O PANEL-1(F) RAW HOUSE | 2016
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C1 I/O PANEL-2(F) RAW HOUSE | 2016
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C1 I/O PANEL-3(F) RAW HOUSE | 2016
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C1 I/O PANEL-4(F) RAW HOUSE | 2016
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C1 I/O PANEL-5(F) RAW HOUSE | 2016
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C1 I/O PANEL-6(F) RAW HOUSE | 2016
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C1 I/O PANEL-7(F) RAW HOUSE | 2016
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C2 I/O PANEL-1(F) RAW HOUSE | 2016
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C2 I/O PANEL-2(F) RAW HOUSE | 2016
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C2 I/O PANEL-3(F) RAW HOUSE | 2016
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C2 I/O PANEL-4(F) RAW HOUSE | 2016
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C2 I/O PANEL-5(F) RAW HOUSE | 2016
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C2 I/O PANEL-6(F) RAW HOUSE | 2016
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C2 I/O PANEL-7(F) RAW HOUSE | 2016
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C3 I/O PANEL-1(F) MILL HOUSE | 2016
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C3 I/O PANEL-2(F) MILL HOUSE | 2016
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C3 I/O PANEL-3(F) MILL HOUSE | 2016
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C4 I/O PANEL-1(F) REFINERY HOUSE | 2016
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C4 I/O PANEL-2(F) REFINERY HOUSE | 2016
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C4 I/O PANEL-3(F) REFINERY HOUSE | 2016
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C4 I/O PANEL-4(F) REFINERY HOUSE | 2016
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT | DCS FOR SUGAR PLANT EXPANSION C4 I/O PANEL-5(F) REFINERY HOUSE | 2016
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL | REFINERY HOUSE BRS PANEL | 2016
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL | SPRAY ENGINEERING DS QUAD | 2004
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | ALLEN BRADLLY CONTROLLER | Melt CLARIFICATION SYSTEM(MCS) | 2016
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER | B&C CONTINUOUS PAN | 2016
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel | Decanter-1 | 2016
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel | Decanter-2 PLC Panel | 2016
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 | SERVER FOR SUGAR PLANT RAW HOUSE RAKE ROOM | 2016, up-garadetion year 2024-25
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 | SERVER FOR SUGAR PLANT RAW HOUSE RAKE ROOM | 2016, up-garadetion year 2024-25
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER | SERVER FOR SUGAR PLANT RAW HOUSE RAKE ROOM | 2024
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION | ENGINEERING WORKSTATION FOR SUGAR PLANT RAW HOUSE | 2016, up-garadetion year 2024-25
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 | OPERATOR WORKSTATION FOR SUGAR PLANT RAW HOUSE CONTROL ROOM | 2016, up-garadetion year 2024-25
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 | OPERATOR WORKSTATION FOR SUGAR PLANT RAW HOUSE CONTROL ROOM | 2016, up-garadetion year 2024-25
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 | OPERATOR WORKSTATION FOR SUGAR PLANT VRL CONTROL ROOM | 2016, up-garadetion year 2024-25
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 | OPERATOR WORKSTATION FOR SUGAR PLANT REFINERY QUAD CONTROL ROOM | 2016, up-garadetion year 2024-25
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 | OPERATOR WORKSTATION FOR SUGAR PLANT RAW PAN CONTROL ROOM | 2016, up-garadetion year 2024-25
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 | OPERATOR WORKSTATION FOR SUGAR PLANT MILL HOUSE CONTROL ROOM | 2016, up-garadetion year 2024-25
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 | OPERATOR WORKSTATION FOR SUGAR PLANT MILL HOUSE CONTROL ROOM | 2016, up-garadetion year 2024-25
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 | OPERATOR WORKSTATION FOR SUGAR PLANT REFINERY HOUSE CONTROL ROOM | 2016, up-garadetion year 2024-25
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OS-SPARE | RAW CONTROL ROOM | 2024
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM | B&C CONTINUOUS PAN CONTROL ROOM | 2016
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM | MCS CONTROL ROOM ENGINEERING CUM OPERATOR SYSTEM | 2016
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM | MCS CONTROL ROOM OPERATOR SYSTEM | 2016
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM | SEDL CONTROL ROOM | 2016
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL | MILL HOUSE CONTROL ROOM FIRE ALARAM SYSTEM | 2016
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL | RAW HOUSE CONTROL ROOM | 2016
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL | PROJECT OFFICE MCC CONTROL ROOM | 2016
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve | SUGAR UNIT - B Conti.Compartment No 05 | 2015
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter | SUGAR UNIT - Raw Quad Meltconcentrator O/L | 2016
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve | SUGAR UNIT -DS Syrup to weighing scale
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter | SUGAR UNIT - Water flow vacuum filter | 2016
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter | SUGAR UNIT - Distillery Tubewell Water line
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter | SUGAR UNIT - ETP Dicanter Flow meter | 2025
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve | SUGAR UNIT - :DBF 2 Flow control valve ( MCS Refinery) | 2015

## EQUIPMENT SPECIFICATION
sheet id | sheet name | EQUIPMENT TAG NAME/APPLICATION | NAME OF EQUIPMENT | section | sub_section | Parameter label | Parameter value
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE |  |  | Make | Triveni Engineering Works Naini Allahabad
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE |  |  | Type | FR14M
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE |  |  | Power | 3000 K.W.
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE |  |  | S.L No | 140M077
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE |  |  | Rotor /Gear Speed | 2300/1500 Revs/Min.
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE |  |  | Steam temp. | 415ᵒc
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE |  |  | Trip Speed | 9158/9574 Revs/Min.
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE |  |  | Exhaust temp. | 150ᵒc
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE |  |  | Steam Pressure | 42 kg/cm2
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE |  |  | Exhaust Pressure | 1.2 kg/cm2
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE |  |  | Governor | Woodward
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | POWER TURBINE |  |  | Part no./Serial no. | 8516-050 /203758212400RPM CW
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE |  |  | Make | Triveni Engineering Works Naini Allahabad
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE |  |  | Type | FR14M
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE |  |  | Power | 3000 K.W.
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE |  |  | S.L No | 1000M75
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE |  |  | Rotor /Gear Speed | 2300/1500 Revs/Min.
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE |  |  | Steam temp. | 415ᵒc
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE |  |  | Trip Speed | 9158/9574 Revs/Min.
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE |  |  | Exhaust temp. | 150ᵒc
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE |  |  | Steam Pressure | 42 kg/cm2
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE |  |  | Exhaust Pressure | 1.2 kg/cm2
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE |  |  | Governor | Woodward
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | POWER TURBINE |  |  | Part no./Serial no. | 8516-050 /203758212400RPM CW
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Mill turbine-01 |  |  | Make | Triveni Engineering Works Naini Allahabad
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Mill turbine-01 |  |  | Type | 525 MM Turbine
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Mill turbine-01 |  |  | Power | 1250 BHP KW/HP
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Mill turbine-01 |  |  | S.L No- | 525142
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Mill turbine-01 |  |  | Rotor /Gear Speed | 6400/800 Revs/Min.
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Mill turbine-01 |  |  | Steam temp. | 415ᵒc
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Mill turbine-01 |  |  | Trip Speed | 8800/9200 Revs/Min.
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Mill turbine-01 |  |  | Exhaust temp. | 150ᵒc
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Mill turbine-01 |  |  | Steam Pressure | 45 kg/cm2
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Mill turbine-01 |  |  | Exhaust Pressure | 1.2 Kg/cm2
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Make | Pneucon
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Sr.No. | 14111400766
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Type | Diaphram
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Model | A216WCB
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Year of Manufacture | 2014
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Tubing | Pu-Tube
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Size | 150 MM
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Cv | Hand wheel
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Characteristic | Equal
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Positioner | Pneucon
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Seat Replacement type | PTFE
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Model | PVP
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Seat Leakage Class | VI
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Air to fail | Valve Close
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Sr.No. | N1F8067473080
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Travel | 38 MM
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Supply Pressure | 2.5 KSC
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | AFR | Savo
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | P Shut | 2 KSC
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Control valve |  |  | Imbibition Water Pressure Tx. | Yokogawa/EJA530E-JBS40N-012EL
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Make | Instrument & System
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Sr.No. | 69200
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Type | Diaphram
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Model | Perposnet
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Year of Manufacture | 2014
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Tubing | Pu-Tube
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Size | 150 MM
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Cv | Hand wheel
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Characteristic | Equal
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Positioner | Pneucon
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Seat Replacement type | PTFE
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Model | PVP
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Seat Leakage Class | VI
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Air to fail | Valve Close
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Sr.No. | N1F8067473080
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Travel | 38 MM
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Supply Pressure | 2.5 KSC
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | AFR | Savo
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | P Shut | 2 KSC
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Make | Pneucon
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Sr.No. | 1302-31406
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Type | Diaphram
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Model | 230/PDS140S
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Year of Manufacture | 2014
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Tubing | Pu-Tube
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Size | 200 MM
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Cv | 1225
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Hand wheel | YES
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Characteristic | Throttling
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Positioner | Pneucon
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Seat Replacement type | PTFE
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Type of Valve | ButterFly Valve(Contoured)
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Model | PVP-1
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Seat Leakage Class | VI
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Air to fail | Valve Open
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Travel | 90ᵒ
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Supply Pressure | 2.5 KSC
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | AFR | Savo
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | P Shut | .5 KSC
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Imbibition Water Tank Level | YOKOGAWA/EJA210E-JMS5J-912EN-WA1JA15
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Temperature Tx. | Headmounted
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Control valve |  |  | Temp. Gauge | General
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Make | Pneucon
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Sr.No. | Type
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Model | Actuator-RD 06
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Year of Manufacture | 2014
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Tubing | SS-304
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Size | 50 MM
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Cv | 68
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Hand wheel | YES
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Characteristic | Throttling
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Positioner/SOV | NOLWSP
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Seat Replacement type | PTFE
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Type of Valve | On-Off
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Model | RD1101
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Seat Leakage Class | VI
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Air to fail | Valve Close
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Travel | 90ᵒ
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Supply Pressure | 4 KSC
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | AFR | Janetics
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | P Shut | 1 KSC
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | Control valve |  |  | Model | FRC 1361 (1/4")
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Make | Pneucon
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Sr.No. | 241212350
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Type | Rotary single acting
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Model | Actuator-RD 06
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Year of Manufacture | 2025
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Tubing | SS-304
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Size | 50 MM
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Cv | 68
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Hand wheel | YES
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Characteristic | Throttling
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Positioner/SOV | NOLWSP
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Seat Replacement type | PTFE
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Type of Valve | On-Off
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Seat Leakage Class | VI
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Air to fail | Valve Close
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Travel | 90ᵒ
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Supply Pressure | 4 KSC
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | AFR | Janetics
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | P Shut | 1 KSC
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Control valve |  |  | Model | FRC 1361 (1/4")
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | Leval sensor |  |  | Make | SIEVPL (S.I Energy)
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | Leval sensor |  |  | Tag.No.LI-101 | Type -Capacitive sensor
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | Leval sensor |  |  | Model | No- EVDCL-06
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | Leval sensor |  |  | Year of Manufacture | 2023
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | Leval sensor |  |  | Zero mill lube oil Pressure transmitter | Yokogawa/EJA530E-JAS40N-012EL
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | Leval sensor |  |  | Zero Mill roller bearing Temperature Tx. | TEMPSUN MAKE L SHAPE RTD
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | Leval sensor |  |  | Make | SIEVPL (S.I Energy)
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | Leval sensor |  |  | Tag.No.LI-102 | Type -Capacitive sensor
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | Leval sensor |  |  | Model | No- EVDCL-06
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | Leval sensor |  |  | Year of Manufacture | 2023
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | Leval sensor |  |  | 1st Mill Chest Pressure transmitter | Yokogawa/EJA530E-JAS40N-012EL
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | Leval sensor |  |  | 1st Mill roller bearing Temperature Tx. | TEMPSUN MAKE L SHAPE RTD
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | Leval sensor |  |  | Live Steam Pressure Tx. | ABB/264H5QSBA1B1
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | Leval sensor |  |  | Techometer Generator | Beacon
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | Leval sensor |  |  | Digital techo meter | Beacon
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | Leval sensor |  |  | Make | SIEVPL (S.I Energy)
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | Leval sensor |  |  | Tag.No.LI-103 | Type -Capacitive sensor
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | Leval sensor |  |  | Model | No- EVDCL-06
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | Leval sensor |  |  | Year of Manufacture | 2025
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | Leval sensor |  |  | 2nd Mill ChestPressure transmitter | Yokogawa/EJA530E-JAS40N-012EL
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | Leval sensor |  |  | 2nd Mill roller bearing Temperature Tx. | TEMPSUN MAKE L SHAPE RTD
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | Leval sensor |  |  | Techometer Generator | Beacon
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | Leval sensor |  |  | Digital techo meter | Beacon
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | Leval sensor |  |  | Make | SIEVPL (S.I Energy)
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | Leval sensor |  |  | Tag.No.LI-104 | Type -Capacitive sensor
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | Leval sensor |  |  | Model | No- EVDCL-06
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | Leval sensor |  |  | Year of Manufacture | 2025
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | Leval sensor |  |  | 3rd Mill Chest Pressure transmitter | Yokogawa/EJA530E-JAS40N-012EL
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | Leval sensor |  |  | 3rd Mill roller bearing Temperature Tx. | TEMPSUN MAKE L SHAPE RTD
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | Leval sensor |  |  | Techometer Generator | Beacon
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | Leval sensor |  |  | Digital techo meter | Beacon
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | Leval sensor |  |  | Make | SIEVPL (S.I Energy)
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | Leval sensor |  |  | Tag.No.LI-105 | Type -Capacitive sensor
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | Leval sensor |  |  | Model | No- EVDCL-06
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | Leval sensor |  |  | Year of Manufacture | 2023
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | Leval sensor |  |  | 4th Mill roller bearing Temperature Tx. | TEMPSUN MAKE L SHAPE RTD
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | Leval sensor |  |  | Steam turbine Exaust Pressure in common Header PT | Yokogawa/EJA530E-JAS40N-012EL
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | Shreder -1 |  |  | Make | Hansford
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | Shreder -1 |  |  | Sr.No. | Type - Vibration sensor
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | Shreder -1 |  |  | Model | HS420-F-025-50-01420
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | Shreder -1 |  |  | Year of Manufacture | 2023
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | Shreder -1 |  |  | Pressure transmitter | Yokogawa/EJA530E-JAS40N-012EL
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | Pressure,Level,Temperature Tx. |  |  | Condensate Flush Tank 1st Chem. PT | Yokogawa/EJA530E-JAS40N-012EL
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | Pressure,Level,Temperature Tx. |  |  | 1st Vopor Cond. from Evp to 1st Cham.I/L Temp. Tx. | Yokogawa/YTA 110 - EA2DB
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | Pressure,Level,Temperature Tx. |  |  | flash tank Cond. Trans. Pumps Suction Header Temp. Tx. | Yokogawa/YTA 110 - EA2DB
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | Pressure,Level,Temperature Tx. |  |  | Condensate Flush Tank 2nd Chem. PT | Yokogawa/EJA530E-JAS40N-012EL
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | Pressure,Level,Temperature Tx. |  |  | Cond.flash tank to 2nd Cham. Inlet Temp. Tx. | Yokogawa/YTA 110 - EA2DB
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | Pressure,Level,Temperature Tx. |  |  | Condensate Flash Tank LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | Pressure,Level,Temperature Tx. |  |  | Condensate Flush Tank 3rd Chem. PT | Yokogawa/EJA530E-JAS40N-012EL
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | Pressure,Level,Temperature Tx. |  |  | Cond. flash tank to 3rd Cham. I/L Temp. Tx. | Yokogawa/YTA 110 - EA2DB
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | Temperature Tx. |  |  | SJP Disch. to VLJH-A Htr. IL Juice Temp | Yokogawa/YTA 110 - EA2DB
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | Temperature Tx. |  |  | VLJH-B Heater OL Juice Temp1 O/L Juice Temp Tx. | Yokogawa/YTA 110 - EA2DB
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | Temperature Tx. |  |  | Condensate Heater-1 O/L Juice Temp Tx. | Yokogawa/YTA 110 - EA2DB
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | Temperature Tx. |  |  | Condensate Heater-2 O/L Juice Temp Tx. | Yokogawa/YTA 110 - EA2DB
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | Temperature Tx. |  |  | Condensate Heater-3 O/L Juice Temp Tx. | Yokogawa/YTA 110 - EA2DB
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | Temperature Tx. |  |  | DJ-1 Heater Juice IL Temp | Yokogawa/YTA 110 - EA2DB
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | Temperature Tx. |  |  | DJ-1 Heater Juice Outlet Temp | Yokogawa/YTA 110 - EA2DB
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | Temperature Tx. |  |  | DJ-2 Heater Juice Outlet Temp | Yokogawa/YTA 110 - EA2DB
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | Temperature Tx. |  |  | DJ-3 Heater Juice Outlet Temp | Yokogawa/YTA 110 - EA2DB
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | Level Transmitter |  |  | High Brix Sweet Water Tank Level Tx | Rosemount/2051L2AAOAD21AAM5D4Q4
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | Level Transmitter |  |  | Lime Sucrate Dosing Tank LT | Rosemount/2051L2AAOAD21AAM5D4Q4
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | Level Transmitter |  |  | Mid Brix Sweet Water Tank Level Tx | Rosemount/2051L2AAOAD21AAM5D4Q4
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | Level Transmitter |  |  | Floc. Dosing Tank LT | Rosemount/2051L2AAOAD21AAM5D4Q4
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | Level Transmitter |  |  | Low Brix Sweet Water Tank Level Tx | Rosemount/2051L2AAOAD21AAM5D4Q4
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | Level Transmitter |  |  | Condensate Tank PP LT | ABB/266DDHFSSA2A7-L9R1
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | pH Transmitter |  |  | Make | FORBES MARSHALL
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | pH Transmitter |  |  | Ph Electrode Make | HAMILTON
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | pH Transmitter |  |  | Ph Electrode Model | HT242428-1111
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | pH Transmitter |  |  | Model | PRO PH 8966
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | pH Transmitter |  |  | Measuring range | 0-14 pH
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | pH Transmitter |  |  | Pressure Range | 0 to 16 bar
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | pH Transmitter |  |  | Electrode Sensor Cable | VP6-10 METER
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | pH Transmitter |  |  | Part no. | HT 355111
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | pH Transmitter |  |  | Make | FORBES MARSHALL
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | pH Transmitter |  |  | Ph Electrode Make | HAMILTON
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | pH Transmitter |  |  | Ph Electrode Model | HT242428-1111
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | pH Transmitter |  |  | Model | PRO PH 8966
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | pH Transmitter |  |  | Measuring range | 0-14 pH
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | pH Transmitter |  |  | Pressure Range | 0 to 16 bar
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | pH Transmitter |  |  | Liquor Heat Exchanger to Reaction tank Temp. Trans. | Yokogawa/YTA 110 - EA2DB
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | pH Transmitter |  |  | Electrode Sensor Cable | VP6-10 METER
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | pH Transmitter |  |  | Part no. | HT 355111
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | Vibration Transmitter |  |  | 3MW New Alt Pdsl ber NDE ver vib Tx. | Hansford/HS420-F-025-50-01420
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | Vibration Transmitter |  |  | 3MW New Alt Pdsl ber DE Axial vib Tx. | Hansford/HS420-F-025-50-01420
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | Vibration Transmitter |  |  | RPM Indicator | Masibus/5296
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | Vibration Transmitter |  |  | 3MW New Alt Pdsl ber NDE Hz vib Tx. | Hansford/HS420-F-025-50-01420
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | Vibration Transmitter |  |  | 3MW New Tur gearbox ver vib Tx. | Hansford/HS420-F-025-50-01420
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | Vibration Transmitter |  |  | Temp/Pr. Gauge | General
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | Vibration Transmitter |  |  | 3MW New Alt Pdsl ber DE ver vib Tx. | Hansford/HS420-F-025-50-01420
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | Vibration Transmitter |  |  | 3MW New Tur Pdsl ver vib Tx. | Hansford/HS420-F-025-50-01420
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter |  |  | 3MW old Alt Pdsl ber NDE ver vib Tx. | Hansford/HS420-F-025-50-01420
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter |  |  | 3MW old Alt Pdsl ber DE Axial vib Tx. | Hansford/HS420-F-025-50-01420
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter |  |  | Digital techometer | Beacon
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter |  |  | 3MW old Alt Pdsl ber NDE Hz vib Tx. | Hansford/HS420-F-025-50-01420
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter |  |  | 3MW old Tur gearbox ver vib Tx. | Hansford/HS420-F-025-50-01420
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter |  |  | Steam temp Indicator | Masibus/LC5296
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter |  |  | 3MW old Alt Pdsl ber DE ver vib Tx. | Hansford/HS420-F-025-50-01420
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter |  |  | 3MW old Tur Pdsl ver vib Tx. | Hansford/HS420-F-025-50-01420
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter |  |  | Exhaust Temp Indicator | Nishka
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter |  |  | Pr./Temp. Gauge | Genaral
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter |  |  | Temperature Scanner | Masibus
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | Vibration Transmitter |  |  | Steam flow Totaliser | Nishka
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Make | Pneucon
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Sr.No. | 1511 41498
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Type | Rotary single acting
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Model | 232 SA 200 +M
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Year of Manufacture | 2014
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Tubing | SS-304
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Size | 350 MM
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Cv | 3250
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Hand wheel | YES
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Characteristic | Throttling
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Positioner | Siemens
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Seat Replacement type | PTFE
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Type of Valve | Butterfly valve
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Model | Sipart PS2
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Seat Leakage Class | VI
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Air to fail | Valve Open
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Sr.No. | NIF9087475737
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Travel | 90ᵒ
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Supply Pressure | 4 KSC
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | AFR | Janetics
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | P Shut | 1 KSC
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | DJ-2 Heater Juice O/L Temp Tx. | Yokogawa/YTA 110 - EA2DB
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | Control valve |  |  | Level Switch | Automat
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Make | Pneucon
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Sr.No. | 1511 41503
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Type | Rotary single acting
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Model | 232 SA 200 +M
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Year of Manufacture | 2014
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Tubing | SS-304
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Size | 300 MM
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Cv | 2750
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Hand wheel | YES
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Characteristic | Throttling
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Positioner | Siemens
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Seat Replacement type | PTFE
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Type of Valve | Butterfly valve
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Model | Sipart PS2
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Seat Leakage Class | VI
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Air to fail | Valve Open
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Sr.No. | NIF9097475752
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Travel | 90ᵒ
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Supply Pressure | 4 KSC
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | AFR | Janetics
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | P Shut | 1 KSC
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | Clear Juice from CJP to CJ-1 Htr. Temp Tx. | Yokogawa/YTA 110 - EA2DB
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | CJ-1 Heater(Existing) Juice Outlet Temp. Tx. | Yokogawa/YTA 110 - EA2DB
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | Control valve |  |  | 2nd Vapours from EVP to CJ-1 Htr. Temp Tx. | Yokogawa/YTA 110 - EA2DB
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Make | Pneucon
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Sr.No. | 1511 41499
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Type | Rotary single acting
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Model | 232 SA 150 +M
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Year of Manufacture | 2014
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Tubing | SS-304
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Size | 200 MM
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Cv | 1225
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Hand wheel | YES
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Characteristic | Throttling
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Positioner | Siemens
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Seat Replacement type | PTFE
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Type of Valve | Butterfly valve
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Model | Sipart PS2
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Seat Leakage Class | VI
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Air to fail | Valve Open
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Sr.No. | NIF9087475704
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Travel | 90ᵒ
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Supply Pressure | 4 KSC
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | AFR | Janetics
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | P Shut | 1 KSC
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | DJ-3 Heater Juice Outlet Temp Tx. | Yokogawa/YTA 110 - EA2DB
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | Control valve |  |  | Level Switch | automat
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Make | Pneucon
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Sr.No. | 1511 41504
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Type | Rotary single acting
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Model | 232 SA 150 +M
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Year of Manufacture | 2014
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Tubing | SS-304
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Size | 200 MM
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Cv | 1225
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Hand wheel | YES
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Characteristic | Throttling
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Positioner | Siemens
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Seat Replacement type | PTFE
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Type of Valve | Butterfly valve
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Model | Sipart PS2
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Seat Leakage Class | VI
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Air to fail | Valve Open
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Sr.No. | NIF8037470881
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Travel | 90ᵒ
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Supply Pressure | 4 KSC
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | AFR | Janetics
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | P Shut | 1 KSC
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | CJ-2 Htr. Juice Outlet Temp Tx. | Yokogawa/YTA 110 - EA2DB
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | Control valve |  |  | 1st Vapours from EVP to CJ-2 Htr. Temp Tx. | Yokogawa/YTA 110 - EA2DB
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Make | Pneucon
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Sr.No. | 1511 41496
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Type | Rotary single acting
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Model | 232 SA 200 +M
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Year of Manufacture | 2014
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Tubing | SS-304
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Size | 400 MM
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Cv | 4500
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Hand wheel | YES
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Characteristic | Throttling
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Positioner | YTC
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Seat Replacement type | EPDM
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Type of Valve | Butterfly valve
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Model | EP1000
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Seat Leakage Class | VI
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Air to fail | Valve Open
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Sr.No. | RD201406
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Travel | 90ᵒ
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Supply Pressure | 4 KSC
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | AFR | Janetics
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | P Shut | 1 KSC
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | RJ-1 Heater(Existing) Cal. Pre. Tx. | Yokogawa/EJA530E-JAS40N-012EL
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Control valve |  |  | Gauge | General
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Make | Pneucon
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Sr.No. | 1511 41497
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Type | Rotary single acting
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Model | 232 SA 200 +M
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Year of Manufacture | 2014
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Tubing | SS-304
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Size | 400 MM
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Cv | 4500
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Hand wheel | YES
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Characteristic | Throttling
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Positioner | YTC
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Seat Replacement type | EPDM
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Type of Valve | Butterfly valve
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Model | EP1000
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Seat Leakage Class | VI
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Air to fail | Valve Open
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Sr.No. | RD201406
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Travel | 90ᵒ
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Supply Pressure | 4 KSC
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | AFR | Janetics
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | P Shut | 1 KSC
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | RJ-1 Heater(Existing) Cal. Pre. Tx. | Yokogawa/EJA530E-JAS40N-012EL
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | Control valve |  |  | Gauge | General
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Make | Pneucon
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Sr.No. | 1511 41502
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Type | Rotary single acting
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Model | 232/SA100+M
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Year of Manufacture | 2014
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Tubing | SS-304
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Size | 100 MM
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Cv | 275
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Hand wheel | YES
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Characteristic | Throttling
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Positioner | ******
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Seat Replacement type | PTFE
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Type of Valve | Butterfly valve
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Model | ******
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Seat Leakage Class | VI
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Air to fail | Open
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Sr.No. | ******
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Travel | 90ᵒ
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | Control valve |  |  | P Shut | 5 KSC
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Make | DELWEL FLOW
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Sr.No. | DVA150088-01
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Type | Rotary single acting
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Model | 260-10
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Year of Manufacture | 2014
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Tubing | SS-304
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Size | DN5050 /20"
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Cv | *****
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Hand wheel | YES
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Characteristic | Throttling
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Positioner | ABB
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Seat Replacement type | PTFE
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Type of Valve | Butterfly valve
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Model | TZIDC 110
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Seat Leakage Class | VI
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Air to fail | Open
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Sr.No. | 822868
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Travel | 90ᵒ
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Supply Pressure | 2.5 KSC
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | AFR | Janetics
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | P Shut | 5 KSC
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | Model | FRC 1361 (1/4")
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | Control valve |  |  | 3 Ata Steam Pressure(Ventury) Tx. | Abb/266HSHQSBA7-L9B6R1
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Make | Pneucon
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Sr.No. | 1512 41530
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Type | Rotary single acting
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Model | 232/SA-125M
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Year of Manufacture | 2014
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Tubing | SS-304
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Size | 150 MM
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Cv | 650
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Hand wheel | YES
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Characteristic | Throttling
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Positioner | Siemens
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Seat Replacement type | EPDM
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Type of Valve | Butterfly valve
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Model | Sipart PS2
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Seat Leakage Class | VI
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Air to fail | Valve Open
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Sr.No. | N1F8037470847
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Travel | 90ᵒ
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Supply Pressure | 4 KSC
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | AFR | Janetics
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | P Shut | 1 KSC
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Make | Pneucon
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Sr.No. | 1511 41521
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Type | Rotary single acting
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Model | 232 SA 100 +M
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Year of Manufacture | 2014
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Tubing | SS-304
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Size | 100 MM
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Cv | 275
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Hand wheel | YES
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Characteristic | Throttling
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Positioner | Siemens
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Seat Replacement type | PTFE
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Type of Valve | Butterfly valve
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Model | Sipart PS2
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Seat Leakage Class | VI
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Air to fail | Valve Close
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Sr.No. | NIF9087475737
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Travel | 90ᵒ
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Supply Pressure | 4 KSC
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | AFR | Janetics
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | P Shut | 1 KSC
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | R3 Mol.from R3 Pump-1 To R3 Mol Cond. IL Temp. Tx | Yokogawa/YTA 110 - EA2DB
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | R3 Mol Cond. O/L Temp. Tx | Yokogawa/YTA 110 - EA2DB
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | R3 MOL Cond. Level Switch | AUTOMAT/2500-A-250-C-3-6-.5-6-W
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | Control valve |  |  | R3 Molasses tank LT | SIEMENS/7ML52212BA11
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Make | Pneucon
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Sr.No. | 1511 41523
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Type | Rotary single acting
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Model | 232 SA 085 +M
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Year of Manufacture | 2014
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Tubing | SS-304
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Size | 80 MM
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Cv | 170
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Hand wheel | YES
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Characteristic | Throttling
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Positioner | YTC
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Seat Replacement type | PTFE
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Type of Valve | Butterfly valve
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Model | ARP-E901
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Seat Leakage Class | VI
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Air to fail | Valve Close
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Sr.No. | 6334
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Travel | 90ᵒ
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Supply Pressure | 4 KSC
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | AFR | Janetics
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | P Shut | 1 KSC
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | A-Heavy Mol.from A-Heavy Pump-1 To A-Heavy Mol Cond. IL Temp. Tx | Yokogawa/YTA 110 - EA2DB
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | A-Heavy Mol Cond. O/L Temp. Tx | Yokogawa/YTA 110 - EA2DB
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | A-Heavy MOL Cond. Level Switch | AUTOMAT/2500-A-250-C-3-6-.5-6-W
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | A-Heavy Mol Tank-1 LT | SIEMENS/7ML52212BA11
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | A-Heavy Mol Tank-2 LT | SIEMENS/7ML52212BA11
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | Control valve |  |  | A-light/melt Mol Tank LT | SIEMENS/7ML52212BA11
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Make | Pneucon
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Sr.No. | 1511 41522
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Type | Rotary single acting
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Model | 232 SA 100 +M
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Year of Manufacture | 2014
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Tubing | SS-304
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Size | 100 MM
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Cv | 275
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Hand wheel | YES
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Characteristic | Throttling
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Positioner | Siemens
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Seat Replacement type | PTFE
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Type of Valve | Butterfly valve
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Model | Sipart PS2
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Seat Leakage Class | VI
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Air to fail | Valve Close
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Sr.No. | NIF6017458236
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Travel | 90ᵒ
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Supply Pressure | 4 KSC
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | AFR | Janetics
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | P Shut | 1 KSC
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | B-Heavy Mol.from B-Heavy Pump-1 To A-Heavy Mol Cond. IL Temp. Tx | Yokogawa/YTA 110 - EA2DB
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | B-Heavy Mol Cond. O/L Temp. Tx | Yokogawa/YTA 110 - EA2DB
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | B-Heavy MOL Cond. Level Switch | TRUMEN TECHNOLOGY LTD./IP-68
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | Control valve |  |  | B-Heavy Mol. Tank level Tx. | SIEMENS/7ML52212BA11
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Make | Pneucon
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Sr.No. | 1511 41520
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Type | Rotary single acting
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Model | 232 SA 085 +M
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Year of Manufacture | 2014
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Tubing | SS-304
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Size | 80 MM
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Cv | 170
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Hand wheel | YES
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Characteristic | Throttling
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Positioner | Siemens
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Seat Replacement type | PTFE
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Type of Valve | Butterfly valve
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Model | Sipart PS2
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Seat Leakage Class | VI
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Air to fail | Valve Close
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Sr.No. | NIF7217467445
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Travel | 90ᵒ
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Supply Pressure | 4 KSC
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | AFR | Janetics
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | P Shut | 1 KSC
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | C Light Mol.from C Light Mol Pump-1 To C Light Mol Mol Cond. IL Temp. Tx | Yokogawa/YTA 110 - EA2DB
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | C Light Mol Cond. O/L Temp. Tx | Yokogawa/YTA 110 - EA2DB
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | C Light Mol Cond. Level Switch | TRUMEN TECHNOLOGY LTD./IP-68
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | C Light Molasses Tank | SIEMENS/7ML52212BA11
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Syrup stoarge Tank 1 LT | SIEMENS/7ML52212BA11
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Syrup stoarge Tank 2 LT | SIEMENS/7ML52212BA11
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Syrup stoarge Tank 3 LT | SIEMENS/7ML52212BA11
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | Control valve |  |  | Syrup stoarge Tank 4 LT | SIEMENS/7ML52212BA11
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Make | Crane
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Sr.No | 8825
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Type | Rotary single acting
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Model | B14A035
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Year of Manufacture | 2014
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Tubing | SS-304
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Size | 150 MM
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Cv | 650
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Hand wheel | YES
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Characteristic | Throttling
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Positioner | YTC
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Seat Replacement type | EPDM
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Type of Valve | Butterfly valve
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Model | YT-1000
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Seat Leakage Class | VI
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Air to fail | Valve Open
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Travel | 90ᵒ
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Supply Pressure | 4 KSC
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | AFR | Janetics
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | P Shut | 1 KSC
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Syrup Heater Pressure Trans. | Yokogawa/EJA530E-JAS40N-012EL
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | 3rd Vapours From Evp. to Syrup Heater Inlet PT | Yokogawa/EJA530E-JAS40N-012EL
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Syrup Feed Pumps Discharge to Syrup Htr IL Temp. Tx. | Yokogawa/YTA 110 - EA2DB
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | Control valve |  |  | Syrup Heater Outlet Syrup Temp. Tx. | Yokogawa/YTA 110 - EA2DB
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Make | Revo
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Sr.No. | B15D2103
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Type | Rotary single acting
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Model | RD700600500000
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Year of Manufacture | 2014
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Tubing | SS-304
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Size | 50 MM
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Cv | 68
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Hand wheel | No
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Characteristic | Throttling
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Positioner | ABB
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Seat Replacement type | EPDM
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Type of Valve | Butterfly valve
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Model | RD1101
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Seat Leakage Class | VI
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Air to fail | Valve Open
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Sr.No. | 122122
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Travel | 90ᵒ
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Supply Pressure | 4 KSC
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | AFR | Janetics
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | P Shut | 1 KSC
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Model | FRC 1361 (1/4")
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | B Continuous Pan I/L Pre. Tx. | Yokogawa/EJA530E-JAS40N-012EL
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | B Continuous Pan Calendria Pre. Tx. | Yokogawa/EJA530E-JAS40N-012EL
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | B-Continous Pan Inlet Vapour Temp. tx. | Yokogawa/YTA 110 - EA2DB
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Con.B Cont. Pan Water O/L Temp. Tx. | Yokogawa/YTA 110 - EA2DB
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | B Grain Crystalyzer(New) Level Trans. | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | B Mas. Sealing Crys.(Existing) LT | SIEMENS/7ML52212BA11
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | Control valve |  |  | Conductivity Tx. | ISCT-1073
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Make | Revo
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Sr.No. | B15H0373
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Type | Rotary single acting
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Model | RD700600500000
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Year of Manufacture | 2014
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Tubing | SS-304
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Size | 50 MM
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Cv | 68
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Hand wheel | No
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Characteristic | Throttling
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Positioner | ABB
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Seat Replacement type | EPDM
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Type of Valve | Butterfly valve
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Model | RD1101
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Seat Leakage Class | VI
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Air to fail | Valve Open
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Sr.No. | 122122
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Travel | 90ᵒ
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Supply Pressure | 4 KSC
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | AFR | Janetics
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | P Shut | 1 KSC
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Model | FRC 1361 (1/4")
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Conductivity Tx. | ISCT-1071
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | Control valve |  |  | Make | I & S
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Make | Revo
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Sr.No. | B15D2111
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Type | Rotary single acting
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Model | RD700600500000
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Year of Manufacture | 2014
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Tubing | SS-304
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Size | 50 MM
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Cv | 68
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Hand wheel | No
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Characteristic | Throttling
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Positioner | ABB
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Seat Replacement type | EPDM
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Type of Valve | Butterfly valve
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Model | RD1101
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Seat Leakage Class | VI
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Air to fail | Valve Open
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Sr.No. | 122122
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Travel | 90ᵒ
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Supply Pressure | 4 KSC
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | AFR | Janetics
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | P Shut | 1 KSC
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Model | FRC 1361 (1/4")
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Conductivity Tx. | ISCT-1077
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | Control valve |  |  | Make | I & S
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Make | Revo
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Sr.No. | B15D2100
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Type | Rotary single acting
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Model | RD700600500000
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Year of Manufacture | 2014
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Tubing | SS-304
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Size | 50 MM
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Cv | 68
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Hand wheel | No
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Characteristic | Throttling
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Positioner | ABB
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Seat Replacement type | EPDM
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Type of Valve | Butterfly valve
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Model | RD1101
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Seat Leakage Class | VI
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Air to fail | Valve Open
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Sr.No. | 122122
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Travel | 90ᵒ
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Supply Pressure | 4 KSC
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | AFR | Janetics
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | P Shut | 1 KSC
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Model | FRC 1361 (1/4")
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Conductivity Tx. | ISCT-1070
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | Control valve |  |  | Make | I & S
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Make | Revo
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Sr.No. | B15D2099
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Type | Rotary single acting
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Model | RD700600500000
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Year of Manufacture | 2014
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Tubing | SS-304
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Size | 50 MM
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Cv | 68
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Hand wheel | No
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Characteristic | Throttling
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Positioner | ABB
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Seat Replacement type | EPDM
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Type of Valve | Butterfly valve
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Model | RD1101
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Seat Leakage Class | VI
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Air to fail | Valve Open
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Sr.No. | 122122
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Travel | 90ᵒ
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Supply Pressure | 4 KSC
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | AFR | Janetics
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | P Shut | 1 KSC
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Model | FRC 1361 (1/4")
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Conductivity Tx. | ISCT-1076
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | Control valve |  |  | Make | I & S
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Make | Revo
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Sr.No. | B15D2102
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Type | Rotary single acting
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Model | RD700600500000
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Year of Manufacture | 2014
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Tubing | SS-304
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Size | 50 MM
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Cv | 68
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Hand wheel | No
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Characteristic | Throttling
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Positioner | ABB
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Seat Replacement type | EPDM
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Type of Valve | Butterfly valve
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Model | RD1101
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Seat Leakage Class | VI
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Air to fail | Valve Open
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Sr.No. | 122122
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Travel | 90ᵒ
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Supply Pressure | 4 KSC
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | AFR | Janetics
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | P Shut | 1 KSC
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Model | FRC 1361 (1/4")
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Conductivity Tx. | ISCT-10XX
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | Control valve |  |  | Make | I & S
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Make | Revo
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Sr.No. | B15D2093
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Type | Rotary single acting
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Model | RD700600500000
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Year of Manufacture | 2014
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Tubing | SS-304
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Size | 50 MM
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Cv | 68
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Hand wheel | No
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Characteristic | Throttling
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Positioner | ABB
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Seat Replacement type | EPDM
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Type of Valve | Butterfly valve
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Model | RD1101
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Seat Leakage Class | VI
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Air to fail | Valve Open
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Sr.No. | 122122
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Travel | 90ᵒ
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Supply Pressure | 4 KSC
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | AFR | Janetics
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | P Shut | 1 KSC
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Model | FRC 1361 (1/4")
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Conductivity Tx. | ISCT-1080
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | Control valve |  |  | Make | I & S
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Make | Revo
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Sr.No. | B15D2092
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Type | Rotary single acting
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Model | RD700600500000
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Year of Manufacture | 2014
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Tubing | SS-304
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Size | 50 MM
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Cv | 68
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Hand wheel | No
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Characteristic | Throttling
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Positioner | ABB
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Seat Replacement type | EPDM
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Type of Valve | Butterfly valve
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Model | RD1101
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Seat Leakage Class | VI
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Air to fail | Valve Open
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Sr.No. | 122122
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Travel | 90ᵒ
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Supply Pressure | 4 KSC
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | AFR | Janetics
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | P Shut | 1 KSC
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Model | FRC 1361 (1/4")
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Conductivity Tx. | ISCT-1075
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | Control valve |  |  | Make | I & S
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Make | Revo
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Sr.No. | B15D2105
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Type | Rotary single acting
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Model | XXXXXXXX
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Year of Manufacture | 2014
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Tubing | SS-304
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Size | 50 MM
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Cv | 68
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Hand wheel | No
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Characteristic | Throttling
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Positioner | ABB
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Seat Replacement type | EPDM
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Type of Valve | Butterfly valve
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Model | RD1101
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Seat Leakage Class | VI
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Air to fail | Valve Open
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Sr.No. | 122122
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Travel | 90ᵒ
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Supply Pressure | 4 KSC
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | AFR | Janetics
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | P Shut | 1 KSC
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Model | FRC 1361 (1/4")
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Conductivity Tx. | ISCT-1078
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | Control valve |  |  | Make | I & S
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Make | Revo
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Sr.No. | B15D2105
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Type | Rotary single acting
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Model | RD700600500000
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Year of Manufacture | 2014
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Tubing | SS-304
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Size | 50 MM
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Cv | 68
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Hand wheel | No
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Characteristic | Throttling
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Positioner | ABB
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Seat Replacement type | EPDM
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Type of Valve | Butterfly valve
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Model | RD1101
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Seat Leakage Class | VI
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Air to fail | Valve Open
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Sr.No. | 122122
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Travel | 90ᵒ
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Supply Pressure | 4 KSC
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | AFR | Janetics
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | P Shut | 1 KSC
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Model | FRC 1361 (1/4")
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | C Continuous Pan I/L Pre. Tx. | Yokogawa/EJA530E-JAS40N-012EL
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | C Continuous Pan Calendria Pre. Tx. | Yokogawa/EJA530E-JAS40N-012EL
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | C-Continous Pan Inlet Vapour Temp. tx. | Yokogawa/YTA 110 - EA2DB
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | Cond.C Cont. Pan Water O/L Temp. Tx. | Yokogawa/YTA 110 - EA2DB
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | C Grain Crystalyzer(New) Level Trans. | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | Control valve |  |  | C Mas. Sealing Crys.(Existing) LT | SIEMENS/7ML52212BA11
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Make | Revo
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Sr.No. | B15D2109
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Type | Rotary single acting
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Model | RD700600500000
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Year of Manufacture | 2014
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Tubing | SS-304
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Size | 50 MM
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Cv | 68
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Hand wheel | No
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Characteristic | Throttling
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Positioner | ABB
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Seat Replacement type | EPDM
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Type of Valve | Butterfly valve
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Model | RD1101
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Seat Leakage Class | VI
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Air to fail | Valve Open
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Sr.No. | 122122
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Travel | 90ᵒ
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Supply Pressure | 4 KSC
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | AFR | Janetics
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | P Shut | 1 KSC
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | Control valve |  |  | Model | FRC 1361 (1/4")
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Make | Revo
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Sr.No. | B15D2098
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Type | Rotary single acting
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Model | RD700600500000
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Year of Manufacture | 2014
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Tubing | SS-304
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Size | 50 MM
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Cv | 68
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Hand wheel | No
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Characteristic | Throttling
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Positioner | ABB
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Seat Replacement type | EPDM
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Type of Valve | Butterfly valve
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Model | RD1101
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Seat Leakage Class | VI
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Air to fail | Valve Open
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Sr.No. | 122122
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Travel | 90ᵒ
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Supply Pressure | 4 KSC
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | AFR | Janetics
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | P Shut | 1 KSC
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | Control valve |  |  | Model | FRC 1361 (1/4")
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Make | Revo
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Sr.No. | B15D2107
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Type | Rotary single acting
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Model | RD700600500000
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Year of Manufacture | 2014
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Tubing | SS-304
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Size | 50 MM
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Cv | 68
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Hand wheel | No
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Characteristic | Throttling
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Positioner | ABB
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Seat Replacement type | EPDM
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Type of Valve | Butterfly valve
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Model | RD1101
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Seat Leakage Class | VI
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Air to fail | Valve Open
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Sr.No. | 122122
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Travel | 90ᵒ
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Supply Pressure | 4 KSC
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | AFR | Janetics
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | P Shut | 1 KSC
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | Control valve |  |  | Model | FRC 1361 (1/4")
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Make | Revo
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Sr.No. | B15D2297
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Type | Rotary single acting
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Model | RD700600500000
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Year of Manufacture | 2014
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Tubing | SS-304
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Size | 50 MM
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Cv | 68
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Hand wheel | No
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Characteristic | Throttling
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Positioner | ABB
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Seat Replacement type | EPDM
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Type of Valve | Butterfly valve
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Model | RD1101
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Seat Leakage Class | VI
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Air to fail | Valve Open
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Sr.No. | 122122
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Travel | 90ᵒ
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Supply Pressure | 4 KSC
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | AFR | Janetics
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | P Shut | 1 KSC
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | Control valve |  |  | Model | FRC 1361 (1/4")
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Make | Revo
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Sr.No. | B15D2095
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Type | Rotary single acting
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Model | RD700600500000
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Year of Manufacture | 2014
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Tubing | SS-304
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Size | 50 MM
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Cv | 68
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Hand wheel | No
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Characteristic | Throttling
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Positioner | ABB
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Seat Replacement type | EPDM
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Type of Valve | Butterfly valve
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Model | RD1101
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Seat Leakage Class | VI
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Air to fail | Valve Open
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Sr.No. | 122122
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Travel | 90ᵒ
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Supply Pressure | 4 KSC
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | AFR | Janetics
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | P Shut | 1 KSC
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | Control valve |  |  | Model | FRC 1361 (1/4")
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Make | Revo
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Sr.No. | B15D2094
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Type | Rotary single acting
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Model | RD700600500000
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Year of Manufacture | 2014
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Tubing | SS-304
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Size | 50 MM
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Cv | 68
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Hand wheel | No
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Characteristic | Throttling
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Positioner | ABB
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Seat Replacement type | EPDM
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Type of Valve | Butterfly valve
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Model | RD1101
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Seat Leakage Class | VI
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Air to fail | Valve Open
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Sr.No. | 122122
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Travel | 90ᵒ
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Supply Pressure | 4 KSC
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | AFR | Janetics
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | P Shut | 1 KSC
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Control valve |  |  | Model | FRC 1361 (1/4")
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Make | Revo
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Sr.No. | B15D2036
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Type | Rotary single acting
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Model | RD700600500000
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Year of Manufacture | 2014
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Tubing | SS-304
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Size | 50 MM
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Cv | 68
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Hand wheel | No
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Characteristic | Throttling
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Positioner | ABB
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Seat Replacement type | EPDM
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Type of Valve | Butterfly valve
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Model | RD1101
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Seat Leakage Class | VI
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Air to fail | Valve Open
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Sr.No. | 122122
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Travel | 90ᵒ
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Supply Pressure | 4 KSC
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | AFR | Janetics
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | P Shut | 1 KSC
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | Control valve |  |  | Model | FRC 1361 (1/4")
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Make | Revo
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Sr.No. | B15D2104
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Type | Rotary single acting
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Model | RD700600500000
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Year of Manufacture | 2014
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Tubing | SS-304
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Size | 50 MM
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Cv | 68
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Hand wheel | No
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Characteristic | Throttling
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Positioner | ABB
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Seat Replacement type | EPDM
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Type of Valve | Butterfly valve
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Model | RD1101
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Seat Leakage Class | VI
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Air to fail | Valve Open
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Sr.No. | 122122
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Travel | 90ᵒ
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Supply Pressure | 4 KSC
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | AFR | Janetics
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | P Shut | 1 KSC
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | Control valve |  |  | Model | FRC 1361 (1/4")
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Make | Revo
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Sr.No. | B15D2108
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Type | Rotary single acting
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Model | RD700600500000
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Year of Manufacture | 2014
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Tubing | SS-304
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Size | 50 MM
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Cv | 68
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Hand wheel | No
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Characteristic | Throttling
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Positioner | ABB
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Seat Replacement type | EPDM
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Type of Valve | Butterfly valve
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Model | RD1101
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Seat Leakage Class | VI
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Air to fail | Valve Open
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Sr.No. | 122122
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Travel | 90ᵒ
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Supply Pressure | 4 KSC
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | AFR | Janetics
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | P Shut | 1 KSC
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | Control valve |  |  | Model | FRC 1361 (1/4")
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Make | Revo
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Sr.No. | XXXXXXX
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Type | Rotary single acting
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Model | XXXXX
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Year of Manufacture | 2014
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Tubing | SS-304
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Size | 50 MM
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Cv | 68
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Hand wheel | No
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Characteristic | Throttling
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Positioner | ABB
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Seat Replacement type | EPDM
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Type of Valve | Butterfly valve
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Model | RD1101
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Seat Leakage Class | VI
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Air to fail | Valve Open
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Sr.No. | 122122
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Travel | 90ᵒ
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Supply Pressure | 4 KSC
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | AFR | Janetics
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | P Shut | 1 KSC
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | Control valve |  |  | Model | FRC 1361 (1/4")
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Make | Pneucon
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Sr.No. | 160241905
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Type | Rotary single acting
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Model | 232 SA 100 +M
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Year of Manufacture | 2014
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Tubing | SS-304
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Size | 100 MM
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Cv | 90
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Hand wheel | YES
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Characteristic | Throttling
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Positioner | YTC
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Seat Replacement type | PTFE
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Type of Valve | Butterfly valve
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Model | RD1101
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Seat Leakage Class | VI
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Air to fail | Valve Close
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Sr.No. | 122122
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Travel | 90ᵒ
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Supply Pressure | 4 KSC
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | AFR | Janetics
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | P Shut | 1 KSC
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Model | FRC 1361 (1/4")
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Raw Sugar Brix Tx. | Samar/BR-14160
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | Control valve |  |  | Raw Meltar Leval Tx. | Yokogawa/EJA210E-JMS5J-912EN-WA13A1S
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Make | Pneucon
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Sr.No. | 160241904
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Type | Rotary single acting
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Model | 232 SA 085M
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Year of Manufacture | 2014
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Tubing | SS-304
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Size | 80 MM
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Cv | 170
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Hand wheel | YES
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Characteristic | Throttling
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Positioner | Siemens
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Seat Replacement type | PTFE
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Type of Valve | Butterfly valve
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Model | Sipart PS2
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Seat Leakage Class | VI
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Air to fail | Valve Close
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Sr.No. | N1F8067473072
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Travel | 90ᵒ
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Supply Pressure | 4 KSC
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | AFR | Janetics
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | P Shut | 1 KSC
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Model | FRC 1361 (1/4")
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | Control valve |  |  | Meltar Temp. Tx. | Yokogawa/YTA 110 - EA2DB
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Make | Pneucon
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Sr.No. | 160241906
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Type | Rotary single acting
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Model | 232 SA 85+M
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Year of Manufacture | 2014
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Tubing | SS-304
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Size | 80 MM
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Cv | 170
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Hand wheel | YES
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Characteristic | Throttling
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Positioner | Siemens
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Seat Replacement type | PTFE
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Type of Valve | Butterfly valve
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Model | Sipart PS2
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Seat Leakage Class | VI
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Air to fail | Valve Close
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Sr.No. | N1F0167483432
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Travel | 90ᵒ
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Supply Pressure | 4 KSC
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | AFR | Janetics
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | P Shut | 3 KSC
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | Control valve |  |  | Model | FRC 1361 (1/4")
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Make | Power-tork
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Sr.No. | 140130806
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Type | Rotary single acting
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Model | PT063F/7014
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Year of Manufacture | 2014
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Tubing | SS-304
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Size | 25 MM
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Cv | 90
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Hand wheel | NO
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Characteristic | Throttling
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Positioner | Siemens
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Seat Replacement type | PTFE
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Type of Valve | Butterfly valve
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Model | Sipart PS2
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Seat Leakage Class | VI
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Air to fail | Valve Close
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Sr.No. | N1F9097475786
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Travel | 90ᵒ
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Supply Pressure | 4 KSC
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | AFR | Janetics
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | P Shut | 1 KSC
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Model | FRC 1361 (1/4")
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Meltar Bricks Trans. | Masali/TO500-LP
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | Control valve |  |  | Indicator | Masibus/LC5296H
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Make | Pneucon
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Sr.No. | 151141525
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Type | Rotary single acting
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Model | 232/SA075+M
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Year of Manufacture | 2014
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Tubing | SS-304
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Size | 50 MM
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Cv | 68
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Hand wheel | Yes
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Characteristic | Throttling
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Positioner | ******
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Seat Replacement type | PTFE
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Type of Valve | Butterfly valve
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Model | *****
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Seat Leakage Class | VI
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Air to fail | Valve Close
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Sr.No. | ******
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Travel | 90ᵒ
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Supply Pressure | 4 KSC
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | P Shut | 1 KSC
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | Control valve |  |  | B Heavy Tank Level Trans. | ABB/266DDHFSSA2A7-L9B6
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Make | Pneucon
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Sr.No. | 151141526
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Type | Rotary single acting
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Model | 232/SA075+M
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Year of Manufacture | 2014
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Tubing | SS-304
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Size | 50 MM
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Cv | 68
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Hand wheel | Yes
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Characteristic | Throttling
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Positioner | Siemens
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Seat Replacement type | PTFE
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Type of Valve | Butterfly valve
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Model | Sipart PS2
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Seat Leakage Class | VI
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Air to fail | Valve Close
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Sr.No. | N1F0167483432
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Travel | 90ᵒ
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Supply Pressure | 4 KSC
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | AFR | Janetics
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | P Shut | 1 KSC
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | Model | FRC 136134 (1/4")
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | Control valve |  |  | MVC Hot Water tank Temp. tx. | Yokogawa/YTA 110 - EA2DB
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Make | Continental
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Sr.No. | Type
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Model | Year of commissioning
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Tubing | PU
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Size | 100 MM
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Cv | 68
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Hand wheel | Yes
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Material Disc/Body | SS-304
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Characteristic | Throttling
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | SOV | Rotex
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Seat Replacement type | PTFE
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Type of Valve | Butterfly valve
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Model | SR3012
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Seat Leakage Class | VI
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Air to fail | Valve Close
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Travel | 90ᵒ
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Supply Pressure | 4 KSC
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | AFR | Janetics
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Air pr. Min /Max | 58 psi( 4 kg/cm2)
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | P Shut | 1 KSC
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | Control valve |  |  | Model | FRC 136134 (1/4")
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Make | Continental
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Sr.No. | Type
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Model | Year of commissioning
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Tubing | PU
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Size | 100 MM
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Cv | 68
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Hand wheel | Yes
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Material Disc/Body | SS-304
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | c | Throttling
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Positioner | Rotex
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Seat Replacement type | PTFE
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Type of Valve | Butterfly valve
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Model | SR3012
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Seat Leakage Class | VI
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Air to fail | Valve Close
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Travel | 90ᵒ
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Supply Pressure | 4 KSC
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | AFR | Janetics
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Air pr. Min /Max | 58 psi( 4 kg/cm2)
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | P Shut | 1 KSC
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | Control valve |  |  | Model | FRC 136134 (1/4")
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Make | Pneucon
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Sr.No. | 151141516
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Type | Diaphram
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Model | 110/PDC 140S
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Year of Manufacture | 2014
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Tubing | SS-304
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Size | 150 MM
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Cv | 450
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Hand wheel | YES
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Characteristic | Equal
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Positioner | Siemens
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Seat Replacement type | PTFE
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Model | Sipart PS2
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Seat Leakage Class | VI
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Air to fail | Valve Close
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Sr.No. | N1F6017458229
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Travel | 57 MM
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | AFR | Savo
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | P Shut | .2 KSC
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Level Transmitter | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Body Temp. Transmitter | Yokogawa/YTA 110 - EA2DB
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Brix transmitter | Birth Hold/LB565
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Body Vacuum Transmitter | Yokogawa/EJA530E-JAS40N-012EL
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Calendria temp. Transmitter | Yokogawa/YTA 110 - EA2DB
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Auto feed Panel | GN engineering
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Calendria Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Tail pipe temp Transmitter | ABB/TTF2000Y1A1B1K1C1
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Vacuum/Pr. /temp. Gauge | General
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Vacuum Breaker | Aira
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | B Seed Crystalyzer Level Trans. | Yokogawa/EJA210E-JMS5J-912EN-WA1JA15
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | A-Footing Vacuum Crys. LT | Yokogawa/EJA210E-JMS5J-912EN-WA1JA15
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | A-Footing Vacuum Cry. PT | Yokogawa/EJA530E-JAS40N-012EL
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Inje. Water Pumps Dis. Header PT | Yokogawa/EJA530E-JAS40N-012EL
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Inj. Water Pumps Dis. Header Temp. Tx. | Yokogawa/YTA 110 - EA2DB
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | Control valve |  |  | Header Temp. Trans. | ABB/TTF2000Y1A1B1K1C1
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Make | Pneucon
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Sr.No. | 151141518
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Type | Diaphram
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Model | 110/PDC 140S
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Year of Manufacture | 2014
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Tubing | SS-304
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Size | 150 MM
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Cv | 220
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Hand wheel | YES
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Characteristic | Equal
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Positioner | Siemens
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Seat Replacement type | PTFE
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Model | Sipart PS2
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Seat Leakage Class | VI
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Air to fail | Valve Close
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Sr.No. | N1F8067473108
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Travel | 57 MM
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | AFR | Savo
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | P Shut | .2 KSC
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Level Transmitter | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Body Temp. Transmitter | Yokogawa/YTA 110 - EA2DB
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Brix transmitter | Birth Hold/LB565
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Body Vacuum Transmitter | Yokogawa/EJA530E-JAS40N-012EL
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Calendria temp. Transmitter | Yokogawa/YTA 110 - EA2DB
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Auto feed Panel | GN engineering
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Calendria Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Tail pipe temp Transmitter | Yokogawa/YTA 110 - EA2DB
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Vacuum/Pr. /temp. Gauge | General
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | Control valve |  |  | Vacuum Bracker | Aira
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Make | Pneucon
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Sr.No. | 151141517
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Type | Diaphram
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Model | 110/PDC 140S
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Year of Manufacture | 2014
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Tubing | SS-304
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Size | 150 MM
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Cv | 450
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Hand wheel | YES
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Characteristic | Equal
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Positioner | Siemens
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Seat Replacement type | PTFE
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Model | Sipart PS2
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Seat Leakage Class | VI
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Air to fail | Valve Close
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Sr.No. | N1F8037470853
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Travel | 57 MM
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | AFR | Savo
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | P Shut | .2 KSC
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Level Transmitter | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Body Temp. Transmitter | Yokogawa/YTA 110 - EA2DB
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Brix transmitter | Birth Hold/LB565
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Body Vacuum Transmitter | Yokogawa/EJA530E-JAS40N-012EL
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Calendria temp. Transmitter | Yokogawa/YTA 110 - EA2DB
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Auto feed Panel | GN engineering
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Calendria Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Tail pipe temp Transmitter | ABB/TTF2000Y1A1B1K1C1
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Vacuum/Pr. /temp. Gauge | General
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Control valve |  |  | Vacuum Breaker | Aira
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Make | Pneucon
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Sr.No. | 151141533
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Type | Diaphram
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Model | 110/PDC 140S
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Year of Manufacture | 2014
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Tubing | SS-304
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Size | 150 MM
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Cv | 220
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Hand wheel | YES
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Characteristic | Equal
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Positioner | Siemens
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Seat Replacement type | PTFE
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Model | Sipart PS2
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Seat Leakage Class | VI
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Air to fail | Valve Close
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Sr.No. | N1F7217467433
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Travel | 57 MM
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | AFR | Savo
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | P Shut | .2 KSC
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Level Transmitter | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Body Temp. Transmitter | Yokogawa/YTA 110 - EA2DB
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Brix transmitter | Birth Hold/LB565
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Body Vacuum Transmitter | Yokogawa/EJA530E-JAS40N-012EL
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Calendria temp. Transmitter | Yokogawa/YTA 110 - EA2DB
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Auto feed Panel | GN engineering
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Calendria Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Tail pipe temp Transmitter | ABB/TTF2000Y1A1B1K1C1
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Vacuum/Pr. /temp. Gauge | General
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Control valve |  |  | Vacuum Breaker | Aira
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Make | Pneucon
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Sr.No. | 151141519
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Type | Diaphram
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Model | 110/PDC 0959
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Year of Manufacture | 2014
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Tubing | SS-304
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Size | 100 MM
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Cv | 450
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Hand wheel | YES
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Characteristic | Equal
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Positioner | Siemens
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Seat Replacement type | PTFE
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Model | Sipart PS2
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Seat Leakage Class | VI
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Air to fail | Valve Close
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Sr.No. | N1F7217467446
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Travel | 57 MM
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | AFR | Savo
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | P Shut | .2 KSC
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Level Transmitter | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Body Temp. Transmitter | Yokogawa/YTA 110 - EA2DB
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Brix transmitter | Birth Hold/LB565
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Body Vacuum Transmitter | Yokogawa/EJA530E-JAS40N-012EL
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Calendria temp. Transmitter | Yokogawa/YTA 110 - EA2DB
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Auto feed Panel | GN engineering
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Calendria Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Tail pipe temp Transmitter | INOR/70APHRF001
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Vacuum/Pr. /temp. Gauge | General
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | Control valve |  |  | Vacuum Breaker | Aira
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Make | Pneucon
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Sr.No. | 151141524
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Type | Diaphram
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Model | 110/PDC 095S
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Year of Manufacture | 2014
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Tubing | SS-304
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Size | 100 MM
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Cv | 90
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Hand wheel | YES
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Characteristic | Equal
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Positioner | Pneucon
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Seat Replacement type | PTFE
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Seat Leakage Class | VI
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Air to fail | Valve Close
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Travel | 57 MM
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | AFR | Savo
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | P Shut | 2 KSC
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | B/C melter brix Tx. | SMAR/BR-14160
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | Control valve |  |  | B/C melter pump suc. Header temp. | Yokogawa/YTA 110 - EA2DB
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Make | Pneucon
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Sr.No. | 160142979
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Type | Diaphram
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Model | 110/PDC 030
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Year of Manufacture | 2014
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Tubing | SS-304
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Size | 65 MM
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Cv | 90
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Hand wheel | No
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Characteristic | Equal
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Positioner | Siemens
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Seat Replacement type | PTFE
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Model | Sipart PS2
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Seat Leakage Class | VI
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Air to fail | Valve Close
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Sr.No. | N1F8067473080
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Travel | 29 MM
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Supply Pressure | 2.5 KSC
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | AFR | Savo
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | P Shut | 4 KSC
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Ex. Steam to PHE I/L PT(A Batch) | ABB/264H5QSBA1B1
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | Control valve |  |  | Ex. Steam to PHE I/L T.T.(A Batch) | ABB/TTF2000Y1A1B1K1C1
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Make | Pneucon
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Sr.No. | 16042980
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Type | Diaphram
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Model | 110/PDC 030
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Year of Manufacture | 2014
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Tubing | SS-304
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Size | 50 MM
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Cv | 50
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Hand wheel | No
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Characteristic | Equal
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Positioner | Siemens
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Seat Replacement type | PTFE
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Model | Sipart PS2
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Seat Leakage Class | VI
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Air to fail | Valve Close
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Sr.No. | N1F8067473080
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Travel | 28 MM
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Supply Pressure | 2.5 KSC
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | AFR | Savo
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | P Shut | 10 KSC
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Hot Water Rec.to Raw batch C/F PT | ABB/266HSHQSBA7-L9B6R1
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | Control valve |  |  | Raw Machine SHWW temp tx. | ABB/TTF2000Y1A1B1K1C1
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Make | Bray/Vaas
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Sr.No. | 150-637-001-001
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Type | Cylinder
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Model | 950
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Year of Manufacture | 2014
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Tubing | SS-304
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Size | 16"/400MM
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Cv | ******
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Hand wheel | YES
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Material Disc/Body | 304/ C8V/450 F/232*C
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Characteristic | Lineer
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Positioner | Siemens
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Seat Replacement type | METAL
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Type of Valve | Knife Edge.
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Model | Sipart PS2
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Seat Leakage Class | VI
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Air to fail | Valve Close
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Sr.No. | N1F3177544493
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Travel | 400 MM
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | AFR | Savo
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | P Shut | 10 KSC
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Crystlizer Level Tx. | SIEMENS/7ML52212BA11
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Control valve |  |  | Pug Mill Level Tx. | SIEMENS/7ML52212BA11
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Make | Bray/Vaas
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Sr.No. | 150-637-001-002
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Type | Cylinder
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Model | 950
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Year of Manufacture | 2014
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Tubing | SS-304
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Size | 16"/400MM
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Cv | ******
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Hand wheel | YES
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Material Disc/Body | 304/ C8V/450 F/232*C
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Characteristic | Lineer
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Positioner | Siemens
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Seat Replacement type | METAL
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Type of Valve | Knife Edge.
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Model | Sipart PS2
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Seat Leakage Class | VI
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Air to fail | Valve Close
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Sr.No. | N1F1057494175
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Travel | 400 MM
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | AFR | Savo
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | P Shut | 10 KSC
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Crystlizer Level Tx. | SIEMENS/7ML52212BA11
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | Control valve |  |  | Pug Mill Level Tx. | SIEMENS/7ML52212BA11
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Make | Bray/Vaas
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Sr.No. | 150-637-001-003
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Type | Cylinder
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Model | 950
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Year of Manufacture | 2014
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Tubing | SS-304
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Size | 16"/400MM
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Cv | ******
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Hand wheel | YES
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Material Disc/Body | 304/ C8V/450 F/232*C
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Characteristic | Equal
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Positioner | YTC
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Seat Replacement type | METAL
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Type of Valve | Knife Edge.
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Model | APRE901
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Seat Leakage Class | VI
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Air to fail | Valve Close
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Sr.No. | 2208
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Travel | 400 MM
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | AFR | Savo
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | P Shut | 10 KSC
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Control valve |  |  | Crystlizer Level Tx. | SIEMENS/7ML52212BA11
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Make | Auma
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Sr.No. | 4173813001-01
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Type | MOV
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Model | SAR15A22
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Year of Manufacture | 2014
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Tubing | SS-304
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Size | 400MM
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | IP | 68
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Hand wheel | YES
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Material Disc/Body | Characteristic
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Equal | Positioner
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Seat Replacement type | METAL
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Type of Valve | Moto
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | Seat Leakage Class | VI
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | RPM | 22
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | T Close | 60-150
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | IP | 67
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | Control valve |  |  | T open | 60-150
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Make | Auma
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Sr.No. | 4173813001-02
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Type | MOV
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Model | SAR15A22
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Year of Manufacture | 2014
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Tubing | SS-304
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Size | 400 MM
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | IP | 68
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Hand wheel | YES
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Material Disc/Body | Characteristic
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Equal | Positioner
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Seat Replacement type | METAL
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Type of Valve | Moto
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | Seat Leakage Class | VI
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | RPM | 22
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | T Close | 60-150
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | IP | 67
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | Control valve |  |  | T open | 60-150
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Make | Auma
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Sr.No. | 4303013001-06-01
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Type | MOV
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Model | SA12E180
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Year of Manufacture | 2014
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Tubing | SS-304
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Size | 400 MM
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | IP | 68
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Hand wheel | YES
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Material Disc/Body | Characteristic
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Equal | Positioner
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Seat Replacement type | METAL
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Type of Valve | Moto
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Seat Leakage Class | VI
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | RPM | 180
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | T Close | 40-110
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | IP | 67
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | T open | 40-110
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | Control valve |  |  | Lubricant | EP 0
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Make | Pneucon
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Sr.No. | 151141527
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Type | Diaphram
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Model | 110/PDO 140S
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Year of Manufacture | 2014
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Tubing | SS-304
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Size | 150 MM
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Cv | 220
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Hand wheel | YES
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Characteristic | Equal
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Positioner | Siemens
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Seat Replacement type | PTFE
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Model | Sipart PS2
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Seat Leakage Class | VI
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Air to fail | Valve Open
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Sr.No. | N1F8037470850
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Travel | 57 MM
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | AFR | Savo
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | P Shut | 3 KSC
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Melt Con. 1st body Level Tx. | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Melt Con. 1 3rd vapoor I/L Temp Tx. | Yokogawa/YTA 110 - EA2DB
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Melt Con. 1 Vapoor O/L Temp Tx. | Yokogawa/YTA 110 - EA2DB
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Melt Con. 1 3rd Vapoor I/L Pre. Tx. | Yokogawa/EJA530E-JAS40N-012EL
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Melt Con. 1 Vapor O/L Pre. Tx. | Yokogawa/EJA530E-JAS40N-012EL
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | Control valve |  |  | Melt Con. 1 O/L Conc. Liqure Temp Tx | Yokogawa/YTA 110 - EA2DB
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Make | Pneucon
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Sr.No. | 151141528
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Type | Diaphram
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Model | 110/PDO 140S
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Year of Manufacture | 2014
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Tubing | SS-304
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Size | 150 MM
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Cv | 220
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Hand wheel | YES
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Characteristic | Equal
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Positioner | Siemens
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Seat Replacement type | PTFE
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Model | Sipart PS2
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Seat Leakage Class | VI
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Air to fail | Valve Open
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Sr.No. | N1F7217487436
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Travel | 57 MM
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | AFR | Savo
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | P Shut | 3 KSC
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Melt Con. 2nd body Level Tx. | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Melt Con. 2 vapoor I/L Temp Tx. | Yokogawa/YTA 110 - EA2DB
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Melt Con. 2 Vapoor to con. O/L Temp Tx. | Yokogawa/YTA 110 - EA2DB
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Melt Con. 2 3rd Vapoor I/L Pre. Tx. | Yokogawa/EJA530E-JAS40N-012EL
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Melt Con. 2 Vapor O/L Pre. Tx. | Yokogawa/EJA530E-JAS40N-012EL
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | Control valve |  |  | Melt Con. 2 O/L Conc. Liqure Temp Tx | Yokogawa/YTA 110 - EA2DB
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Make | Pneucon
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Sr.No. | 151141529
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Type | Diaphram
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Model | 110/PDO 140S
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Year of Manufacture | 2014
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Tubing | SS-304
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Size | 150 MM
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Cv | 220
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Hand wheel | YES
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Characteristic | Equal
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Positioner | Siemens
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Seat Replacement type | PTFE
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Model | Sipart PS2
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Seat Leakage Class | VI
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Air to fail | Valve Open
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Sr.No. | N1F8067473055
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Travel | 57 MM
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | AFR | Savo
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | P Shut | 3 KSC
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Melt Con.1/2body Level Tx. | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Melt Con. 1/2 vapoor I/L Temp Tx. | Yokogawa/YTA 110 - EA2DB
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Melt Con. 1/2 Vapoor to con. O/L Temp Tx. | Yokogawa/YTA 110 - EA2DB
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Melt Con. 1/2 3rd Vapoor I/L Pre. Tx. | Yokogawa/EJA530E-JAS40N-012EL
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Melt Con. 1/2 Vapor O/L Pre. Tx. | Yokogawa/EJA530E-JAS40N-012EL
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | Control valve |  |  | Melt Con. 1/2 O/L Conc. Liqure Temp Tx | Yokogawa/YTA 110 - EA2DB
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Make | Pneucon
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Sr.No. | 151141588
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Type | Diaphram
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Model | 110/PDC09
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Year of Manufacture | 2014
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Tubing | SS-304
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Size | 100 MM
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Cv | 220
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Hand wheel | YES
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Characteristic | Equal
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Positioner | YTC
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Seat Replacement type | PTFE
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Type of Valve | Globe valve
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Seat Leakage Class | VI
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Air to fail | Close
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Travel | 38MM
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | AFR | Janetics
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | P Shut | 4 KSC
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Model | FRC 1361 (1/4")
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Flow meter | Rosemount/8705TSA020C1W0B3
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Mol tank-1 level Tx. | SIEMENS/7ML52212BA11
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | Control valve |  |  | Mol tank-2 level Tx. | SIEMENS/7ML52212BA11
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Make | Pneucon
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Sr.No. | 151141512
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Type | Diaphram
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Model | 110/PDO 140S
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Year of Manufacture | 2014
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Tubing | SS-304
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Size | 150 MM
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Cv | 450
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Hand wheel | YES
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Characteristic | Equal
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Positioner | Siemens
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Seat Replacement type | PTFE
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Model | Sipart PS2
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Seat Leakage Class | VI
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Air to fail | Valve Open
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Sr.No. | N1F8017458235
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Travel | 57 MM
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | AFR | Savo
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | P Shut | 2 KSC
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | 800 M² Body Set A LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | 800 M² Body Set A body temp Tx | Yokogawa/YTA 110 - EA2DB
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | 800 M² Body Set A Cal. temp Tx | Yokogawa/YTA 110 - EA2DB
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | 800 M² Body Set A Vacuum Tx. | Yokogawa/EJA530E-JAS40N-012EL
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | 800 M² Body Set A Cal. Pr. Tx. | Yokogawa/EJA530E-JAS40N-012EL
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | Control valve |  |  | 800 M² Body Set A juice O/L. temp Tx | Yokogawa/YTA 110 - EA2DB
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Make | Pneucon
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Sr.No. | 151141513
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Type | Diaphram
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Model | 110/PDO 140S
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Year of Manufacture | 2014
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Tubing | SS-304
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Size | 150 MM
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Cv | 450
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Hand wheel | YES
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Characteristic | Equal
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Positioner | Siemens
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Seat Replacement type | PTFE
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Model | Sipart PS2
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Seat Leakage Class | VI
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Air to fail | Valve Open
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Sr.No. | N1F8017458238
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Travel | 57 MM
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | AFR | Savo
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | P Shut | 2 KSC
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | 800 M² Body Set B LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | 800 M² Body Set B body temp Tx | Yokogawa/YTA 110 - EA2DB
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | 800 M² Body Set B Cal. temp Tx | Yokogawa/YTA 110 - EA2DB
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | 800 M² Body Set B Vacuum Tx. | Yokogawa/EJA530E-JAS40N-012EL
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | 800 M² Body Set B Cal. Pr. Tx. | Yokogawa/EJA530E-JAS40N-012EL
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | Control valve |  |  | 800 M² Body Set B juice O/L. temp Tx | Yokogawa/YTA 110 - EA2DB
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Make | Pneucon
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Sr.No. | 151141514
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Type | Diaphram
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Model | 110/PDO 140S
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Year of Manufacture | 2014
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Tubing | SS-304
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Size | 150 MM
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Cv | 450
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Hand wheel | YES
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Characteristic | Equal
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Positioner | Siemens
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Seat Replacement type | PTFE
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Model | Sipart PS2
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Seat Leakage Class | VI
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Air to fail | Valve Open
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Sr.No. | N1F8063473094
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Travel | 57 MM
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | AFR | Savo
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | P Shut | 2 KSC
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Make | Pneucon
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Sr.No. | 151141511
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Type | Diaphram
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Model | 110/PDO 140S
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Year of Manufacture | 2014
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Tubing | SS-304
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Size | 150 MM
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Cv | 450
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Hand wheel | YES
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Characteristic | Equal
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Positioner | Siemens
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Seat Replacement type | PTFE
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Model | Sipart PS2
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Seat Leakage Class | VI
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Air to fail | Valve Open
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Sr.No. | N1F8063473094
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Travel | 57 MM
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | AFR | Savo
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | P Shut | 2 KSC
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Make | Pneucon
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Sr.No. | 151141510
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Type | Diaphram
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Model | 110/PDO 140S
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Year of Manufacture | 2014
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Tubing | SS-304
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Size | 150 MM
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Cv | 625
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Hand wheel | YES
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Characteristic | Linear
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Positioner | Siemens
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Seat Replacement type | PTFE
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Model | Sipart PS2
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Seat Leakage Class | VI
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Air to fail | Valve Open
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Sr.No. | N1F8067473041
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Travel | 57 MM
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | AFR | Savo
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | P Shut | 1 KSC
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | 1000 M² Body Set A LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | 1000 M² Body Set A body temp Tx | Yokogawa/YTA 110 - EA2DB
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | 1000 M² Body Set A Cal. temp Tx | Yokogawa/YTA 110 - EA2DB
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | 1000 M² Body Set A Vacuum Tx. | Yokogawa/EJA530E-JAS40N-012EL
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | 1000 M² Body Set A Cal. Pr. Tx. | Yokogawa/EJA530E-JAS40N-012EL
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | Control valve |  |  | 1000 M² Body Set A juice O/L. temp Tx | Yokogawa/YTA 110 - EA2DB
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Make | Pneucon
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Sr.No. | 130231404
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Type | Diaphram
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Model | 230/PDS 140S
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Year of Manufacture | 2014
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Tubing | SS-304
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Size | 250 MM
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Cv | 1200
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Hand wheel | YES
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Material Disc/Body | SS-316/A216GR-WCB
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Characteristic | Throttling
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Positioner | Siemens
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Seat Replacement type | PTFE
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Type of Valve | Butterfly
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Model | Sipart PS2
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Seat Leakage Class | VI
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Air to fail | Valve Open
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Sr.No. | N1F6017458231
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Travel | 90ᵒ
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Supply Pressure | 2.5 KSC
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | AFR | Savo
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | P Shut | .5 KSC
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | 836 M² Body Set B LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | 836 M² Body Set B body temp Tx | Yokogawa/YTA 110 - EA2DB
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | 836 M² Body Set B Cal. temp Tx | Yokogawa/YTA 110 - EA2DB
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | 836 M² Body Set B Vacuum Tx. | Yokogawa/EJA530E-JAS40N-012EL
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | 836 M² Body Set B Cal. Pr. Tx. | Yokogawa/EJA530E-JAS40N-012EL
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | Control valve |  |  | 836 M² Body Set B juice O/L. temp Tx | Yokogawa/YTA 110 - EA2DB
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Make | Pneucon
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Sr.No. | 151141508
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Type | Diaphram
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Model | 110/PDO140S
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Year of Manufacture | 2014
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Tubing | SS-304
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Size | 200 MM
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Cv | 625
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Hand wheel | YES
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Characteristic | Equal
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Positioner | Siemens
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Seat Replacement type | PTFE
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Model | Sipart PS2
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Seat Leakage Class | VI
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Air to fail | Valve Open
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Sr.No. | N1F8037470860
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Travel | 57 MM
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | AFR | Savo
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | P Shut | 1 KSC
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | 2500 Body Set A LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | 2500 Body Set A body temp Tx | Yokogawa/YTA 110 - EA2DB
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | 2500 Body Set A Cal. temp Tx | Yokogawa/YTA 110 - EA2DB
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | 2500 Body Set A Vacuum Tx. | Yokogawa/EJA530E-JAS40N-012EL
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | 2500 Body Set A Cal. Pr. Tx. | Yokogawa/EJA530E-JAS40N-012EL
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | Control valve |  |  | 2500 Body Set A juice O/L. temp Tx | Yokogawa/YTA 110 - EA2DB
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Make | Pneucon
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Sr.No. | 151141507
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Type | Diaphram
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Model | 110/PDO140S
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Year of Manufacture | 2014
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Tubing | SS-304
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Size | 200 MM
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Cv | 625
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Hand wheel | YES
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Characteristic | Equal
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Positioner | Siemens
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Seat Replacement type | PTFE
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Model | Sipart PS2
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Seat Leakage Class | VI
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Air to fail | Valve Open
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Sr.No. | N1FA067473063
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Travel | 57 MM
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | AFR | Savo
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | P Shut | 1 KSC
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | 2500 Body Set B LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | 2500 Body Set B body temp Tx | Yokogawa/YTA 110 - EA2DB
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | 2500 Body Set B Cal. temp Tx | Yokogawa/YTA 110 - EA2DB
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | 2500 Body Set B Vacuum Tx. | Yokogawa/EJA530E-JAS40N-012EL
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | 2500 Body Set B Cal. Pr. Tx. | Yokogawa/EJA530E-JAS40N-012EL
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | Control valve |  |  | 2500 Body Set B juice O/L. temp Tx | Yokogawa/YTA 110 - EA2DB
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Make | Pneucon
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Sr.No. | 151141505
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Type | Diaphram
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Model | 110/PDO 300S
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Year of Manufacture | 2014
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Tubing | SS-304
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Size | 250 MM
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Cv | 925
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Hand wheel | YES
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Characteristic | Equal
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Positioner | Siemens
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Seat Replacement type | PTFE
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Model | Sipart PS2
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Seat Leakage Class | VI
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Air to fail | Valve Open
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Sr.No. | N1J5247489281
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Travel | 90 MM
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | AFR | Savo
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | P Shut | .2 KSC
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | 3800 Body Set LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | 3800 Body Set body temp Tx | Yokogawa/YTA 110 - EA2DB
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | 3800 Body Set Cal. temp Tx | Yokogawa/YTA 110 - EA2DB
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | 3800 Body Set Vacuum Tx. | Yokogawa/EJA530E-JAS40N-012EL
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | 3800 Body Set Cal. Pr. Tx. | Yokogawa/EJA530E-JAS40N-012EL
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | Control valve |  |  | 3800 Body Set juice O/L. temp Tx | Yokogawa/YTA 110 - EA2DB
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Make | Pneucon
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Sr.No. | 151141509
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Type | Diaphram
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Model | 110/PDO 140S
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Year of Manufacture | 2014
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Tubing | SS-304
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Size | 200 MM
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Cv | 625
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Hand wheel | YES
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Characteristic | Equal
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Positioner | Siemens
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Seat Replacement type | PTFE
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Model | Sipart PS2
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Seat Leakage Class | VI
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Air to fail | Valve Open
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Sr.No. | N1F8067473038
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Travel | 57 MM
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | AFR | Savo
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | P Shut | 1 KSC
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | 1250 FFE Body Set LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | 1250 FFE Body temp Tx | Yokogawa/YTA 110 - EA2DB
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | 1250 FFE Cal. temp Tx | Yokogawa/YTA 110 - EA2DB
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | 1250 FFE Body Set Vacuum Tx. | Yokogawa/EJA530E-JAS40N-012EL
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | 1250 FFE Cal. Pr. Tx. | Yokogawa/EJA530E-JAS40N-012EL
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | Control valve |  |  | 1250 FFE juice O/L. temp Tx | Yokogawa/YTA 110 - EA2DB
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Make | Pneucon
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Sr.No. | 151141506
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Type | Diaphram
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Model | 110/PDO 140S
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Year of Manufacture | 2014
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Tubing | SS-304
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Size | 250 MM
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Cv | 625
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Hand wheel | YES
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Material Disc/Body | SS-304 / A216GR WCB
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Characteristic | Equal
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Positioner | Siemens
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Seat Replacement type | PTFE
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Model | Sipart PS2
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Seat Leakage Class | VI
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Air to fail | Valve Open
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Sr.No. | N1J7217469289
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Travel | 57 MM
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | AFR | Savo
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | P Shut | .2 KSC
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | SK2500 M²(IST/IIND) Body LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | SK2500 M²(IST/IIND) Body temp Tx | Yokogawa/YTA 110 - EA2DB
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | SK2500 M²(IST/IIND) Cal. temp Tx | Yokogawa/YTA 110 - EA2DB
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | SK2500 M²(IST/IIND) Body Vacuum Tx. | Yokogawa/EJA530E-JAS40N-012EL
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | SK2500 M²(IST/IIND) Cal. Pr. Tx. | Yokogawa/EJA530E-JAS40N-012EL
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Control valve |  |  | SK2500 M²(IST/IIND) Body juice O/L. temp Tx | Yokogawa/YTA 110 - EA2DB
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Make | Pneucon
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Sr.No. | 171050005
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Type | Diaphram
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Model | 110/DVC300S
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Year of Manufacture | 2014
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Tubing | SS-304
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Size | 300 MM
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Cv | 1350
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Hand wheel | YES
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Material Disc/Body | SS-304ST / WCC+IBR
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Characteristic | Equal
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | SOV | Rotex
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Seat Replacement type | PTFE
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Seat Leakage Class | VI
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Air to fail | Valve Close
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Travel | 90 MM
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Supply Pressure | 50 PSI
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | AFR | Savo
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | P Shut | 2 KSC
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | Control valve |  |  | Exaust Steam Pres. Tx. | Yokogawa/EJA530E-JAS40N-012EL
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Manufacturer – | MICRO MOTION
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Serial No. | 3720734
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Working Temperature | (-29 to 60˚)
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Model | 1700R11ABZEZZZZ
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Range | 400 T / Hr
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | working pressure | 285 PSI
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Nominal Dia ( MM) | 100 MM
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Calibration Range | NA
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Accuracy | 0.0015
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Material Body | SS
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Sensor Material | 316 S1
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Linearity | ±0.1%
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Liner | PTFE
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Output | 4-20 mA
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Repeatability | ±0.1%
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Display Version | E- Series
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Power Supply | 90-220 VAC
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Comunication | HART
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Display unit | 2 line LCD
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Cable length | 5 Mtr
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Protection | IP 67
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | DS Mill Juice Header Pressure Tx. | Yokogawa/EJA530E-JAS40N-012EL
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | Mass Flow Meter |  |  | Screen Juice Tank Level Tx. | Yokogawa/EJA210E-JMS5J-912EN-WA1JA15
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Manufacturer – | MICRO MOTION
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Serial No. | 3351418
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Working Temperature | (-29 to 60˚)
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Model | 400M451N2BZEZZ
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Range | 275 T/Hr
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | working pressure | 285 PSI
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Nominal Dia ( MM) | 100 MM
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Calibration Range | NA
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Accuracy | 0.0015
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Material Body | Sensor Material
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | 316 S1 | Repeatability
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Liner | PTFE
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Output | 4-20 mA
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Comunication | HART
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Display Version | Power Supply
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | 90-220 VAC | Protection
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Display unit | 2 line LCD
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Cable length | 5 Mtr
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Mill Juice Header Pressure Tx. REF. | ABB/266HSHQSBA7-L9B6R1
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | Mass Flow Meter |  |  | Raw Juice Tank Level Tx. | ABB/266DDHHSSA2A7 -L9R1
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Manufacturer – | E&H
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Serial No. | H30221C20000
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Working Temperature | (-29 to 60˚)
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Model | PROMAG-10
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Range | 250/Hr
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | working pressure | 285 PSI
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Nominal Dia ( MM) | 150 MM
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Calibration Range | NA
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Accuracy | 0.0015
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Material Body | Sensor Material
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | 316 S1 | Repeatability
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Liner | PTFE
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Output | 4-20 mA
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Comunication | HART
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Display Version | E- Series
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Power Supply | 90-220 VAC
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Protection | IP 67
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Display unit | 2 line LCD
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | Magnetic Juice Flow Meter |  |  | Cable length | Head-Mount
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Manufacturer – | Abb
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Serial No. | 50RFASME
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Working Temperature | (-29 to 60˚)
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Model | DE557
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Range | 250/Hr
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | working pressure | 285 PSI
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Nominal Dia ( MM) | 200 MM
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Calibration Range | NA
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Accuracy | 0.0015
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Material Body | Sensor Material
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | 316 S1 | Repeatability
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Liner | PTFE
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Output | 4-20 mA
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Comunication | HART
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Display Version | E- Series
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Power Supply | 90-220 VAC
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Protection | IP 67
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Display unit | 2 line LCD
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | Magnetic Juice Flow Meter Refinery |  |  | Cable length | Head-Mount
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Manufacturer – | E&H
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Serial No. | L9051120000
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Working Temperature | (-29 to 60˚)
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Model | PROMAG-10
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Range | 250/Hr
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | working pressure | 285 PSI
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Nominal Dia ( MM) | 150 MM
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Calibration Range | NA
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Accuracy | 0.0015
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Material Body | Sensor Material
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | 316 S1 | Repeatability
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Liner | PTFE
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Output | 4-20 mA
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Comunication | HART
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Display Version | E- Series
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Power Supply | 90-220 VAC
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Protection | IP 67
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Display unit | 2 line LCD
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | Magnetic Flow Meter Imbibition Water |  |  | Cable length | Head-Mount
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Manufacturer – | E&H
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Serial No. | J7006720000
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Working Temperature | (-29 to 60˚)
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Model | PROMAG-10
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Range | 180/hr
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | working pressure | 285 PSI
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Nominal Dia ( MM) | 100 MM
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Calibration Range | NA
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Accuracy | 0.0015
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Material Body | Sensor Material
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | 316 S1 | Repeatability
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Liner | PTFE
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Output | 4-20 mA
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Comunication | HART
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Display Version | E- Series
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Power Supply | 90-220 VAC
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Protection | IP 67
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Display unit | 2 line LCD
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | Magnetic Flow Meter |  |  | Cable length | Head-Mount
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Manufacturer – | Adept
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Serial No. | 1904966
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Working Temperature | (-29 to 60˚)
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Model | 6410
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Range | 180/hr
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | working pressure | 285 PSI
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Nominal Dia ( MM) | 80 MM
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Calibration Range | NA
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Accuracy | 0.0015
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Material Body | Sensor Material
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | 316 S1 | Repeatability
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Liner | PTFE
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Output | 4-20 mA
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Comunication | HART
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Display Version | E- Series
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Power Supply | 90-220 VAC
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Protection | IP 67
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Display unit | 2 line LCD
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | UGR flow meter |  |  | Cable length | Head-Mount
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Manufacturer – | KROHNE
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Serial No. | 13400096
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Working Temperature | (-29 to 60˚)
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Model | IFC -100
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Range | 250/hr
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | working pressure | 285 PSI
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Nominal Dia ( MM) | 150 MM
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Calibration Range | NA
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Accuracy | 0.0015
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Material Body | Sensor Material
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | 316 S1 | Repeatability
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Liner | PTFE
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Output | 4-20 mA
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Comunication | HART
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Display Version | E- Series
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Power Supply | 90-220 VAC
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Protection | IP 67
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Display unit | 2 line LCD
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | Flow meter |  |  | Cable length | Head-Mount
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Manufacturer – | Adept
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Serial No. | 1904974
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Working Temperature | (-29 to 60˚)
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Model | 6410
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Range | 250/hr
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | working pressure | 285 PSI
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Nominal Dia ( MM) | 100 MM
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Calibration Range | NA
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Accuracy | 0.0015
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Material Body | Sensor Material
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | 316 S1 | Repeatability
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Liner | PTFE
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Output | 4-20 mA
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Comunication | HART
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Display Version | E- Series
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Power Supply | 90-220 VAC
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Protection | IP 67
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Display unit | 2 line LCD
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | Flow Meter |  |  | Cable length | Head-Mount
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Manufacturer – | Adept
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Serial No. | 13131564
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Working Temperature | (-29 to 60˚)
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Model | 8750TSA040C1WOB3
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Range | 250/hr
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | working pressure | 285 PSI
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Nominal Dia ( MM) | 100 MM
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Calibration Range | NA
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Accuracy | 0.0015
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Material Body | Sensor Material
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | 316 S1 | Repeatability
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Liner | PTFE
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Output | 4-20 mA
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Comunication | HART
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Display Version | E- Series
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Power Supply | 90-220 VAC
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Protection | IP 67
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Display unit | 2 line LCD
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Cable length | Head-Mount
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | Flow meter |  |  | Muddy Juice Tank(New) Level Trans. | Yokogawa/EJA210E-JMS5J-912EN-WA1JA15
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Manufacturer – | Rosemount
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Serial No. | 6205893
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Working Temperature | (-29 to 60˚)
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Model | 8705TSA080C1W0B3
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Range | NA
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | working pressure | 285 PSI
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Nominal Dia ( MM) | 200 MM
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Calibration Range | NA
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Accuracy | 0.0015
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Material Body | Sensor Material
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | 316 S1 | Repeatability
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Liner | PTFE
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Output | 4-20 mA
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Comunication | HART
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Display Version | E- Series
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Power Supply | 90-220 VAC
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Protection | IP 67
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Display unit | 2 line LCD
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Cable length | Head-Mount
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Defe. Juice Pumps Dis. Pre.Trans. | Yokogawa/EJA530E-JAS40N-012EL
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | Flow Meter |  |  | Defe.Juice Receiver Tank Level Tx | Yokogawa/EJA210E-JMS5J-912EN-WA1JA15
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Manufacturer – | Rosemount
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Serial No. | 13140864
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Working Temperature | (-29 to 60˚)
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Model | 8705TSA020C1W0B3
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Range | 20 /Hr
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | working pressure | 285 PSI
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Nominal Dia ( MM) | 40 MM
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Calibration Range | NA
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Accuracy | 0.0015
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Material Body | Sensor Material
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | 316 S1 | Repeatability
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Liner | PTFE
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Output | 4-20 mA
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Comunication | HART
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Display Version | E- Series
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Power Supply | 90-220 VAC
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Protection | IP 67
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Display unit | 2 line LCD
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | Lime Flow Meter |  |  | Cable length | Head-Mount
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Manufacturer – | Rosemount
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Serial No. | 6103298
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Working Temperature | (-29 to 60˚)
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Model | 8705TSA020C1W0NAB3
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Range | NA
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | working pressure | 285 PSI
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Nominal Dia ( MM) | 50 MM
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Calibration Range | NA
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Accuracy | 0.0015
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Material Body | Sensor Material
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | 316 S1 | Repeatability
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Liner | PTFE
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Output | 4-20 mA
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Comunication | HART
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Display Version | E- Series
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Power Supply | 90-220 VAC
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Protection | IP 67
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Display unit | 2 line LCD
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | D-Scutining Hot water flow meter |  |  | Cable length | Head-Mount
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Manufacturer – | Rosemount
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Serial No. | 6205887
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Working Temperature | (-29 to 60˚)
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Model | 8705TSA030C1W0B3
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Range | NA
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | working pressure | 285 PSI
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Nominal Dia ( MM) | 80 MM
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Calibration Range | NA
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Accuracy | 0.0015
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Material Body | Sensor Material
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | 316 S1 | Repeatability
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Liner | PTFE
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Output | 4-20 mA
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Comunication | HART
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Display Version | E- Series
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Power Supply | 90-220 VAC
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Protection | IP 67
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Display unit | 2 line LCD
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | Hot water Clear Juice flow meter |  |  | Cable length | Head-Mount
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Manufacturer – | ABB
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Serial No. | 3K672014310803
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Working Temperature | (-29 to 60˚)
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Model | FEP311020A1S1A1B1A1A0A1A1C1AYH1JNT3M5
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Range | NA
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | working pressure | 285 PSI
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Nominal Dia ( MM) | 25 MM
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Calibration Range | NA
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Accuracy | 0.0015
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Material Body | Sensor Material
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | 316 S1 | Repeatability
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Liner | PTFE
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Output | 4-20 mA
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Comunication | HART
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Display Version | E- Series
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Power Supply | 90-220 VAC
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Protection | IP 67
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Display unit | 2 line LCD
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | Cable length | Head-Mount
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | Magnafloc Dosing flow meter |  |  | FLOC. Holding Tank Level Trans. | Yokogawa/EJA210E-JMS5J-912EN-WA1JA15
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Manufacturer – | Rosemount
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Serial No. | 14757671
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Working Temperature | (-29 to 60˚)
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Model | 8705TSA040C1WOB3
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Range | NA
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | working pressure | 285 PSI
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Nominal Dia ( MM) | 100 MM
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Calibration Range | NA
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Accuracy | 0.0015
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Material Body | Sensor Material
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | 316 S1 | Repeatability
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Liner | PTFE
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Output | 4-20 mA
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Comunication | HART
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Display Version | E- Series
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Power Supply | 90-220 VAC
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Protection | IP 67
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Display unit | 2 line LCD
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Cable length | Head-Mount
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | Flow meter |  |  | Syrup reciver tank LT | yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Manufacturer – | Rosemount
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Serial No. | 6103292
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Working Temperature | (-29 to 60˚)
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Model | 8705TSA040C1W0B3
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Range | NA
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | working pressure | 285 PSI
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Nominal Dia ( MM) | 100 MM
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Calibration Range | NA
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Accuracy | 0.0015
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Material Body | Sensor Material
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | 316 S1 | Repeatability
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Liner | PTFE
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Output | 4-20 mA
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Comunication | HART
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Display Version | E- Series
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Power Supply | 90-220 VAC
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Protection | IP 67
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Display unit | 2 line LCD
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Cable length | Head-Mount
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | Flow Meter |  |  | Scum Receiving Tank Level Trans. | Rosemount/2051L2AADAD21AAM5D4Q4
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Manufacturer – | Rosemount
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Serial No. | 6201023
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Working Temperature | (-29 to 60˚)
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Model | 8750WBER1A1FTSA040CA1M4
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Range | NA
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | working pressure | 285 PSI
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Nominal Dia ( MM) | 100 MM
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Calibration Range | NA
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Accuracy | 0.0015
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Material Body | Sensor Material
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | 316 S1 | Repeatability
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Liner | PTFE
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Output | 4-20 mA
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Comunication | HART
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Display Version | E- Series
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Power Supply | 90-220 VAC
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Protection | IP 67
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Display unit | 2 line LCD
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | Flow meter |  |  | Cable length | Head-Mount
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Manufacturer – | Rosemount
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Serial No. | 6201025
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Working Temperature | (-29 to 60˚)
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Model | 8750WBER1A1FTSA030CA1M4
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Range | NA
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | working pressure | 285 PSI
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Nominal Dia ( MM) | 80 MM
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Calibration Range | NA
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Accuracy | 0.0015
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Material Body | Sensor Material
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | 316 S1 | Repeatability
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Liner | PTFE
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Output | 4-20 mA
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Comunication | HART
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Display Version | Power Supply
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | 90-220 VAC | Protection
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | Flow meter |  |  | Display unit | Cable length
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Manufacturer – | Rose mount
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Serial No. | 6201022
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Working Temperature | (-29 to 60˚)
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Model | 8750WBER1A1FTSA040CA1M4
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Range | NA
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | working pressure | 285 PSI
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Nominal Dia ( MM) | 100 MM
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Calibration Range | NA
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Accuracy | 0.0015
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Material Body | Sensor Material
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | 316 S1 | Repeatability
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Liner | PTFE
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Output | 4-20 mA
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Comunication | HART
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Display Version | E- Series
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Power Supply | 90-220 VAC
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Protection | IP 67
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Display unit | 2 line LCD
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | Flow meter |  |  | Cable length | 10 MTR
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Manufacturer – | Rose mount
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Serial No. | 6201024
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Working Temperature | (-29 to 60˚)
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Model | 8750WBER1A1FTSA030CA1M4
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Range | NA
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | working pressure | 285 PSI
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Nominal Dia ( MM) | 80 MM
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Calibration Range | NA
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Accuracy | 0.0015
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Material Body | Sensor Material
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | 316 S1 | Repeatability
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Liner | PTFE
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Output | 4-20 mA
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Comunication | HART
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Display Version | Power Supply
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | 90-220 VAC | Protection
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | Flow meter |  |  | Display unit | Cable length
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Manufacturer – | E&H
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Serial No. | W507EF20000(6935921)
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Working Temperature | (-29 to 60˚)
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Model | PROMAG -10
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Range | NA
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | working pressure | 285 PSI
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Nominal Dia ( MM) | 150 MM
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Calibration Range | NA
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Accuracy | 0.0015
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Material Body | Sensor Material
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | 316 S1 | Repeatability
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Liner | PTFE
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Output | 4-20 mA
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Comunication | HART
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Display Version | Power Supply
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | 90-220 VAC | Protection
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | Flow Meter |  |  | Display unit | Cable length
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Manufacturer – | E&H
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Serial No. | W507EF20000(6935922)
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Working Temperature | (-29 to 60˚)
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Model | PROMAG -10
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Range | NA
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | working pressure | 285 PSI
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Nominal Dia ( MM) | 150 MM
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Calibration Range | NA
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Accuracy | 0.0015
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Material Body | Sensor Material
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | 316 S1 | Repeatability
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Liner | PTFE
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Output | 4-20 mA
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Comunication | HART
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Display Version | Power Supply
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | 90-220 VAC | Protection
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | C Grain Flow Meter |  |  | Display unit | Cable length
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Manufacturer – | Rose mount
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Serial No. | 6205894
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Working Temperature | (-29 to 60˚)
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Model | 8705TSA080C1WOB3
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Range | NA
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | working pressure | 285 PSI
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Nominal Dia ( MM) | 200 MM
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Calibration Range | NA
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Accuracy | 0.0015
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Material Body | Sensor Material
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | 316 S1 | Repeatability
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Liner | PTFE
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Output | 4-20 mA
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Comunication | HART
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Display Version | Power Supply
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | 90-220 VAC | Protection
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | Flow meter |  |  | Display unit | Cable length
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Manufacturer – | Adept
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Serial No. | 1904977
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Working Temperature | (-29 to 60˚)
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Model | Mag Flow 6410
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Range | NA
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | working pressure | 285 PSI
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Nominal Dia ( MM) | 200 MM
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Calibration Range | NA
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Accuracy | 0.0015
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Material Body | Sensor Material
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | 316 S1 | Repeatability
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Liner | PTFE
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Output | 4-20 mA
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Comunication | HART
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Display Version | Power Supply
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | 90-220 VAC | Protection
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | Flow meter |  |  | Display unit | Cable length
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Manufacturer – | Adept
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Serial No. | 1904966
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Working Temperature | (-29 to 60˚)
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Model | Mag Flow 6410
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Range | NA
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | working pressure | 285 PSI
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Nominal Dia ( MM) | 80 MM
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Calibration Range | NA
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Accuracy | 0.0015
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Material Body | Sensor Material
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | 316 S1 | Repeatability
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Liner | PTFE
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Output | 4-20 mA
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Comunication | HART
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Display Version | Power Supply
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | 90-220 VAC | Protection
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | Flow meter |  |  | Display unit | Cable length
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Manufacturer – | Adept
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Serial No. | 1904971
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Working Temperature | (-29 to 60˚)
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Model | Mag Flow 6410
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Range | NA
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | working pressure | 285 PSI
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Nominal Dia ( MM) | 150 MM
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Calibration Range | NA
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Accuracy | 0.0015
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Material Body | Sensor Material
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | 316 S1 | Repeatability
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Liner | PTFE
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Output | 4-20 mA
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Comunication | HART
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Display Version | Power Supply
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | 90-220 VAC | Protection
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Flow Meter |  |  | Display unit | Cable length
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Manufacturer – | Adept
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Serial No. | 1904966
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Working Temperature | (-29 to 60˚)
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Model | Mag Flow 6410
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Range | NA
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | working pressure | 285 PSI
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Nominal Dia ( MM) | 200 MM
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Calibration Range | NA
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Accuracy | 0.0015
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Material Body | Sensor Material
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | 316 S1 | Repeatability
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Liner | PTFE
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Output | 4-20 mA
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Comunication | HART
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Display Version | Power Supply
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | 90-220 VAC | Protection
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Flow meter |  |  | Display unit | Cable length
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Manufacturer – | Adept
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Serial No. | 1904976
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Working Temperature | (-29 to 60˚)
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Model | Mag Flow 6410
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Range | NA
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | working pressure | 285 PSI
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Nominal Dia ( MM) | 150 MM
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Calibration Range | NA
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Accuracy | 0.0015
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Material Body | Sensor Material
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | 316 S1 | Repeatability
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Liner | PTFE
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Output | 4-20 mA
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Comunication | HART
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Display Version | Power Supply
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | 90-220 VAC | Protection
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | Flow meter |  |  | Display unit | Cable length
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Manufacturer – | Adept
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Serial No. | 1901588
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Working Temperature | (-29 to 60˚)
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Model | Mag Flow 6410
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Range | NA
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | working pressure | 285 PSI
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Nominal Dia ( MM) | 150 MM
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Calibration Range | NA
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Accuracy | 0.0015
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Material Body | Sensor Material
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | 316 S1 | Repeatability
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Liner | PTFE
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Output | 4-20 mA
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Comunication | HART
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Display Version | Power Supply
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | 90-220 VAC | Protection
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | Disterlly flow meter |  |  | Display unit | Cable length
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Make | Hi-tech
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Sr.No. | 450/453
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | PLC Make | OMRON POWER
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Model | HT-900
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Year of Manufacture | 2016
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Model | ZEN- 20CIDR-D-V2
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Capacity | 300 Bag/Hr
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Class | Third
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | SOV Make | JANATICS
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Material-Body | SS
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Filling Type | Gravity
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Model | 255SR61-A
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Controller-1 & 2 | C140003 & C140006
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Loadcell - | 1x6
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Proxy Make | JAYSHREE
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Make | Unipulse
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Make | Sensortronics
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Model | SW4051
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Model | HT-900
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Model | 65023-110K-NC-02X
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | AFR Make | Janatics-FRC-136134
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | Duplex weighing Machine |  |  | Level Switch | SAPCON
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Make | Hi-tech
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Sr.No. | 1024/1025
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | PLC Make | Omron
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Model | HT-900
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Year of Manufacture | 2016
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Capacity | 300 Bag/Hr
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Class | Third
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | SOV Make | JANATICS
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Material-Body | SS
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Filling Type | Gravity
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Model | DS255SR61-A
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Controller-1 & 2 | C140004 & C140005
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Loadcell - | 1x6
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Proxy Make | JAYSHREE
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Make | Unipulse
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Make | Sensortronics
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Model | SW4051
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Model | HT-900
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Model | 65023-110K-NC-02X
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | AFR Make | JANATICS -FRC-136134
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Duplex weighing Machine |  |  | Level Switch | Sapcon
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Make | Hi-tech
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Sr.No. | 449/454
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Model | HT-900
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Year of Manufacture | 2016
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Capacity | 300 Bag/Hr
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Class | Third
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | SOV Make | JANATICS
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Material-Body | SS
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Filling Type | Gravity
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Model | DS255SR61-A
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Controller-1 & 2 | B910144 & B910145
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Loadcell - | 1x6
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Proxy Make | JAYSHREE
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Make | Unipulse
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Make | Sensortronics
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Model | SW4051
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Model | HT-900
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Model | 65023-110K-NC-02X
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | AFR Make | JANATICS -FRC-136134
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Duplex weighing Machine |  |  | Level Switch | Sapcon
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Make | Hi-tech
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Sr.No. | 806
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | PLC Make | Omran
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Model | HT-900
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Year of Manufacture | 2016
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Model | ZEN-10C1DR-D-V2
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Capacity | 300 Bag/Hr
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Class | Third
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | SOV Make | JANATICS
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Material-Body | SS
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Filling Type | Gravity
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Model | DS255SR61-A
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Controller-1 | B840208
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Loadcell - | 1x6
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Proxy Make | JAYSHREE
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Make | Unipulse
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Make | Sensortronics
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Model | SW4051
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Model | HT-900
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Model | 65023-110K-NC-02X
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | AFR Make | JANATICS -FRC-136134
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | Simplex Weighing Machine |  |  | Level Switch | Sapcon
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Make | Hi-tech
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Sr.No. | YEAR-211024/1025
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | PLC Make | Omron
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Model | HT-900
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Year of Manufacture | 2016
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Capacity | 300 Bag/Hr
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Class | Third
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | SOV Make | JANATICS
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Material-Body | SS
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Filling Type | Gravity
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Model | DS255SR61-A
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Controller-1 & 2 | C140002 & C140001
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Loadcell - | 1x6
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Proxy Make | JAYSHREE
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Make | Unipulse
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Make | Sensortronics
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Model | SW4051
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Model | HT-900
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Model | 65023-110K-NC-02X
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | AFR Make | JANATICS -FRC-136134
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | Duplex weighing Machine |  |  | Level Switch | Sapcon
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | B Centrifugal Machine |  |  | Make | Energy Tech. Engineers
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | B Centrifugal Machine |  |  | Sr.No.176814 | PLC Make
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | B Centrifugal Machine |  |  | Model | P89
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | B Centrifugal Machine |  |  | Year of Manufacture | 2016
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | B Centrifugal Machine |  |  | Capacity | 1750 Kg/Hr
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | B Centrifugal Machine |  |  | SOV Make | JANATICS
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | B Centrifugal Machine |  |  | B Heavy Tank Level Trans. | Abb/266DDHFSSA2A7-L9B6
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | B Centrifugal Machine |  |  | Make | Energy Tech. Engineers
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | B Centrifugal Machine |  |  | Sr.No.176820 | PLC Make
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | B Centrifugal Machine |  |  | Model | P89
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | B Centrifugal Machine |  |  | Year of Manufacture | 2016
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | B Centrifugal Machine |  |  | Capacity | 1750 Kg/Hr
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | B Centrifugal Machine |  |  | SOV Make | JANATICS
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | B Centrifugal Machine |  |  | Make | Energy Tech. Engineers
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | B Centrifugal Machine |  |  | Sr.No.176818 | PLC Make
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | B Centrifugal Machine |  |  | Model | P89
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | B Centrifugal Machine |  |  | Year of Manufacture | 2016
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | B Centrifugal Machine |  |  | Capacity | 1750 Kg/Hr
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | B Centrifugal Machine |  |  | Class | SOV Make
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | B Centrifugal Machine |  |  | Make | Energy Tech. Engineers
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | B Centrifugal Machine |  |  | Sr.No.371275 | PLC Make
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | B Centrifugal Machine |  |  | Model | P89
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | B Centrifugal Machine |  |  | Year of Manufacture | 2016
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | B Centrifugal Machine |  |  | Capacity | 1750 Kg/Hr
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | B Centrifugal Machine |  |  | Class | SOV Make
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | C Centrifugal Machine |  |  | Make | Energy Tech. Engineers
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | C Centrifugal Machine |  |  | Sr.No.389696 | PLC Make
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | C Centrifugal Machine |  |  | Model | P89
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | C Centrifugal Machine |  |  | Year of Manufacture | 2016
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | C Centrifugal Machine |  |  | Capacity | 1750 Kg/Hr
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | C Centrifugal Machine |  |  | Class | SOV Make
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | C Centrifugal Machine |  |  | C Light Tank Level Transmitter | Abb/266DDHFSSA2A7-L9B6
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | C Centrifugal Machine |  |  | Final Molasses Level Transmitter | Abb/266DDHFSSA2A7-L9B6
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | C Centrifugal Machine |  |  | C Fore PUG MILL Temp. Trans. | Abb/TTF2000Y1A1B1K1C1
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | C Centrifugal Machine |  |  | Final Molasses temp. Tx. | Abb/TTF2000Y1A1B1K1C1
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | C Centrifugal Machine |  |  | Make | Energy Tech. Engineers
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | C Centrifugal Machine |  |  | Sr.No.543503 | PLC Make
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | C Centrifugal Machine |  |  | Model | P89
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | C Centrifugal Machine |  |  | Year of Manufacture | 2016
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | C Centrifugal Machine |  |  | Capacity | 1750 Kg/Hr
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | C Centrifugal Machine |  |  | Class | SOV Make
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | C Centrifugal Machine |  |  | C Fore PUG MILL Temp. Trans. | Abb/TTF2000Y1A1B1K1C1
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | C Centrifugal Machine |  |  | Make | Energy Tech. Engineers
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | C Centrifugal Machine |  |  | Sr.No.505113 | PLC Make
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | C Centrifugal Machine |  |  | Model | P89
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | C Centrifugal Machine |  |  | Year of Manufacture | 2016
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | C Centrifugal Machine |  |  | Capacity | 1750 Kg/Hr
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | C Centrifugal Machine |  |  | Class | SOV Make
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | C Centrifugal Machine |  |  | C Fore PUG MILL Temp. Trans. | Abb/TTF2000Y1A1B1K1C1
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | Raw Centrifugal Machine Drive |  |  | Make | Power Automation
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | Raw Centrifugal Machine Drive |  |  | Year of Installation | 2023
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | Raw Centrifugal Machine Drive |  |  | PLC Make | Delta
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | Raw Centrifugal Machine Drive |  |  | Capacity | 750 Kg/Hr
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | Raw Centrifugal Machine Drive |  |  | Relay Card | Speed Proxy
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | Raw Centrifugal Machine Drive |  |  | AL Tank Level Transmitter | ABB/266DDHFSSA2A7-L9B6
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | Raw Centrifugal Machine Drive |  |  | AH Tank Level Transmitter | ABB/266DDHFSSA2A7-L9B6
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | Refinery Centrifugal Machine Drive |  |  | Make | Power Automation
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | Refinery Centrifugal Machine Drive |  |  | Year of Installation | 2023
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | Refinery Centrifugal Machine Drive |  |  | PLC Make | Delta
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | Refinery Centrifugal Machine Drive |  |  | Capacity | 750 Kg/Hr
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | Refinery Centrifugal Machine Drive |  |  | Relay Card | Speed Proxy
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | Refinery Centrifugal Machine Drive |  |  | R2 Molasses Tank-1 LT | ABB/266DDHFSSA2A7-L9B6
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | Refinery Centrifugal Machine Drive |  |  | R2 Molasses Tank-3 LT | ABB/266DDHFSSA2A7-L9B6
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | Refinery Centrifugal Machine Drive |  |  | R2 Molasses Tank-2 LT | ABB/266DDHFSSA2A7-L9B6
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | Refinery Centrifugal Machine Drive |  |  | R2 Molasses Tank-4 LT | ABB/266DDHFSSA2A7-L9B6
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | Air Compressure |  |  | Make | Chicago Pneumatic
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | Air Compressure |  |  | Sr.No. | PNA415060
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | Air Compressure |  |  | Type | Reciprocating
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | Air Compressure |  |  | Model | NS2HX2T-31/18PA
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | Air Compressure |  |  | Year of Manufacture | 2014
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | Air Compressure |  |  | Cooling Type | Water
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | Air Compressure |  |  | Capacity CFM | 495
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | Air Compressure |  |  | Discharge pressure | 7.7 kg/cm2
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | Air Compressure |  |  | Rated RPM | 952
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | Air Compressure |  |  | Make | Chicago Pneumatic
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | Air Compressure |  |  | Sr.No. | PNA415062
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | Air Compressure |  |  | Type | Reciprocating
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | Air Compressure |  |  | Model | NS2HX2T-31/18PA
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | Air Compressure |  |  | Year of Manufacture | 2014
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | Air Compressure |  |  | Cooling Type | Water
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | Air Compressure |  |  | Capacity CFM | 495
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | Air Compressure |  |  | Discharge pressure | 7.7 kg/cm2
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | Air Compressure |  |  | Rated RPM | 952
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | Air Compressure |  |  | Make | Chicago Pneumatic
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | Air Compressure |  |  | Sr.No. | PNA415061
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | Air Compressure |  |  | Type | Reciprocating
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | Air Compressure |  |  | Model | NS2HX2T-31/18PA
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | Air Compressure |  |  | Year of Manufacture | 2014
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | Air Compressure |  |  | Cooling Type | Water
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | Air Compressure |  |  | Capacity CFM | 495
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | Air Compressure |  |  | Discharge pressure | 7.7 kg/cm2
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | Air Compressure |  |  | Rated RPM | 952
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | Air Compressure |  |  | Make | Chicago Pneumatic
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | Air Compressure |  |  | Sr.No. | PNA720151
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | Air Compressure |  |  | Type | Reciprocating
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | Air Compressure |  |  | Model | HX2T-100NP
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | Air Compressure |  |  | Year of Manufacture | 2014
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | Air Compressure |  |  | Cooling Type | Water
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | Air Compressure |  |  | Capacity CFM | 472
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | Air Compressure |  |  | Discharge pressure | 10 kg/cm2
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | Air Compressure |  |  | Rated RPM | 920
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | Air Compressure |  |  | Make | GEM
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | Air Compressure |  |  | Sr.No. | Type
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | Air Compressure |  |  | Model | Year of Manufacture
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | Air Compressure |  |  | Capacity CFM | Automation Grade
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | Air Compressure |  |  | Reciver Tank PR. Trans. | ABB/266HSHQSBA7-L9B6
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | Air Compressure |  |  | Make | GEM
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | Air Compressure |  |  | Sr.No. | Type
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | Air Compressure |  |  | Model | Year of Manufacture
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | Air Compressure |  |  | Capacity CFM | Automation Grade
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | Air Compressure |  |  | Automatic | Rated RPM
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Make | Pneucon
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Sr.No. | 20A07130
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Type | Diaphragm
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Model | 110PDC 95
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Year of Manufacture | 2000
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Tubing | PU tube
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Size | 100 MM
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Cv | 220
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Hand wheel | NO
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Material Disc/Body | SS-316 / CI
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Characteristic | Equal %
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Positioner | I&S
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Seat Replacement type | PTFE
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Model | PERPOSNATE
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Seat Leakage Class | VI
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Air to fail | Valve Close
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Travel | 38 MM
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Supply Pressure | 2.5 KSC
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | AFR | Janatics
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | P Shut | .2 KSC
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Model | AFR 1361/1563
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Auto Feed control Panel | Instrument System/30232
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Body temperature RTD | MIEPL
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Brix electrode | Instrument System/8-2k4
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Tail pipe temperature RTD | Raviraj Process Control
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Level Sensor | Instrument System
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | Control valve |  |  | Vacuum Gauge | Waaree
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Make | I&S
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Sr.No. | 0068
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Type | Diaphragm
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Model | PERPOSNATE
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Year of Manufacture | 2000
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Tubing | PU tube
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Size | 80 MM
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Cv | 170
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Hand wheel | NO
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Material Disc/Body | SS-316 / WCB
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Characteristic | Equal %
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Positioner | I&S
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Seat Replacement type | PTFE
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Model | PERPOSNATE
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Seat Leakage Class | VI
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Air to fail | Valve Close
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Travel | 38 MM
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Supply Pressure | 2.5 KSC
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | AFR | Janatics
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | P Shut | .2 KSC
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Model | AFR 1361/1563
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Auto Feed control Panel | Instrument System/30232
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Body temperature RTD | MIEPL/T094251
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Brix electrode | Instrument System/8-2k4
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Tail pipe temperature RTD | MIEPL
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Level Sensor | Instrument System
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Control valve |  |  | Vacuum Gauge | Waaree
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Make | Pnecon
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Sr.No. | 20AO01290
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Type | Diaphragm
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Model | 110PDC95
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Year of Manufacture | 2000
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Tubing | PU tube
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Size | 100 MM
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Cv | 170
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Hand wheel | NO
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Material Disc/Body | SS-316 / CI
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Characteristic | Equal %
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Positioner | I&S
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Seat Replacement type | PTFE
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Model | PERPOSNATE
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Seat Leakage Class | VI
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Air to fail | Valve Close
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Sr.No. | 00686 2KG-10
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Travel | 38 MM
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Supply Pressure | 2.5 KSC
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | AFR | Janatics
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | P Shut | .2 KSC
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Model | AFR 1361/1563
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Auto Feed control Panel | Instrument System/30232
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Body temperature RTD | Digiprro
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Brix electrode | Instrument System/10.2K
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Tail pipe temperature RTD | MIEPL
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Level Sensor | Instrument System
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Control valve |  |  | Vacuum Gauge | Waaree
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Make | Pnecon
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Sr.No. | 60644356
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Type | Diaphragm
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Model | 110PDC95
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Year of Manufacture | 2000
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Tubing | PU tube
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Size | 100 MM
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Cv | 220
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Hand wheel | NO
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Material Disc/Body | SS-316 / WBC
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Characteristic | Equal %
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Positioner | I&S
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Seat Replacement type | PTFE
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Model | PERPOSNATE
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Seat Leakage Class | VI
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Air to fail | Valve Close
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Sr.No. | 00691 2KG-10
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Travel | 38 MM
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Supply Pressure | 2.5 KSC
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | AFR | Janatics
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | P Shut | 4 KSC
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Model | AFR 1361/1563
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Auto Feed control Panel | Instrument System
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Body temperature RTD | Digiprro
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Brix electrode | Instrument System/10.2K
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Tail pipe temperature RTD | MIEPL
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Level Sensor | Instrument System
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Control valve |  |  | Vacuum Gauge | Waaree
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Make | Pnecon
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Sr.No. | Type
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Model | 110PDC95
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Year of Manufacture | 2000
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Tubing | PU tube
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Size | 100 MM
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Cv | 220
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Hand wheel | NO
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Material Disc/Body | SS-316 / WBC
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Characteristic | Equal %
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Positioner | Pneucon
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Seat Replacement type | PTFE
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Model | PVP-1
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Seat Leakage Class | VI
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Air to fail | Valve Close
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Sr.No. | 554
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Travel | 38 MM
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Supply Pressure | 2.5 KSC
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | AFR | Janatics
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | P Shut | 4 KSC
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Model | AFR 1361/1563
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Auto Feed control Panel | Instrument System
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Body temperature RTD | Instrument System
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Brix electrode | Instrument System/10.2K
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Tail pipe temperature RTD | Digiprro
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Level Sensor | Instrument System
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Control valve |  |  | Vacuum Gauge | Waaree
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Make | Pnecon
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Sr.No. 20AO71717 | Type
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Model | 110PDC95
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Year of Manufacture | 2000
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Tubing | PU tube
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Size | 100 MM
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Cv | 220
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Hand wheel | NO
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Material Disc/Body | SS-316 / CI
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Characteristic | Equal %
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Positioner | Pneucon
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Seat Replacement type | PTFE
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Model | PVP-1
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Seat Leakage Class | VI
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Air to fail | Valve Close
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Sr.No. | 548
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Travel | 38 MM
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Supply Pressure | 2.5 KSC
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | AFR | Janatics
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | P Shut | 4 KSC
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Model | AFR 1361/1563
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Auto Feed control Panel | Instrument System
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Body temperature RTD | Instrument System
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Brix electrode | Instrument System/10.2K
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Tail pipe temperature RTD | MIEPL
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Level Sensor | Instrument System
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | Control valve |  |  | Vacuum Gauge | Waaree
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Make | Pnecon
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Sr.No. | 20AOY601
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Type | Diaphragm
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Model | 110PDC95
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Year of Manufacture | 2000
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Tubing | PU tube
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Size | 100 MM
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Cv | 220
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Hand wheel | NO
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Material Disc/Body | SS-316 / CI
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Characteristic | Equal %
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Positioner | Pneucon
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Seat Replacement type | PTFE
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Model | PVP-1
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Seat Leakage Class | VI
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Air to fail | Valve Close
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Travel | 38 MM
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Supply Pressure | 2.5 KSC
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | AFR | Janatics
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | P Shut | 4 KSC
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Model | AFR 1361/1563
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Auto Feed control Panel | Instrument System
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Body temperature RTD | Instrument System
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Brix electrode | Instrument System/10.2K
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Tail pipe temperature RTD | Toshniwal
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Level Sensor | Instrument System
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Control valve |  |  | Vacuum Gauge | Waaree
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Make | Pnecon
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Sr.No. | 20AO71295
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Type | Diaphragm
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Model | 110PDC95
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Year of Manufacture | 2000
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Tubing | PU tube
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Size | 100 MM
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Cv | 220
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Hand wheel | NO
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Material Disc/Body | SS-316 / WBC
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Characteristic | Equal %
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Positioner | I&S
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Seat Replacement type | PTFE
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Model | PERPOSNATE
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Seat Leakage Class | VI
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Air to fail | Valve Close
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Sr.No. | 00688 2k6-10
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Travel | 38 MM
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Supply Pressure | 2.5 KSC
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | AFR | Janatics
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | P Shut | 4 KSC
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Model | AFR 1361/1563
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Auto Feed control Panel | Instrument System
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Body temperature RTD | ADCN
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Brix electrode | Instrument System/10.2K
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Tail pipe temperature RTD | Raviraj
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Level Sensor | Instrument System
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Control valve |  |  | Vacuum Gauge | Waaree
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Make | Pnecon
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Sr.No. | 20AO71605
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Type | Diaphragm
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Model | 110PDC95
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Year of Manufacture | 2000
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Tubing | PU tube
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Size | 100 MM
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Cv | 220
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Hand wheel | NO
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Material Disc/Body | SS-316 / WBC
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Characteristic | Equal %
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Positioner | Pneucon
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Seat Replacement type | PTFE
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Model | PVP-1
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Seat Leakage Class | VI
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Air to fail | Valve Close
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Sr.No. | 552
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Travel | 38 MM
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Supply Pressure | 2.5 KSC
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | AFR | Janatics
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | P Shut | 4 KSC
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Model | AFR 1361/1563
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Auto Feed control Panel | Instrument System
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Body temperature RTD | MIEPL
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Brix electrode | Instrument System/10.2K
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Tail pipe temperature RTD | Instrument System
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Level Sensor | Instrument System
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Control valve |  |  | Vacuum Gauge | Waaree
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Make | Pnecon
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Sr.No. | 20AO31083
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Type | Diaphragm
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Model | 110 C/PDC-140
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Year of Manufacture | 2000
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Tubing | PU tube
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Size | 150 MM
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Cv | 440
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Hand wheel | NO
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Material Disc/Body | SS-316 / CCS
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Characteristic | Equal %
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Positioner | I&S
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Seat Replacement type | PTFE
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Model | PERPOSNATE
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Seat Leakage Class | VI
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Air to fail | Valve Close
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Sr.No. | 00692 2k6-10
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Travel | 57 MM
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Supply Pressure | 2.5 KSC
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | AFR | Janatics
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | P Shut | 4 KSC
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Model | AFR 1361/1563
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Auto Feed control Panel | Instrument System
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Body temperature RTD | Instrument System
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Brix electrode | Instrument System/10.2K
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Tail pipe temperature RTD | Instrument System
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Level Sensor | Instrument System
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | Control valve |  |  | Vacuum Gauge | Waaree
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Make | Pnecon
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Sr.No. | 20AO71307
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Type | Diaphragm
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Model | 110/PDC-140
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Year of Manufacture | 2000
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Tubing | PU tube
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Size | 150 MM
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Cv | 220
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Hand wheel | NO
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Material Disc/Body | SS-316 / CCS
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Characteristic | Equal %
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Positioner | I&S
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Seat Replacement type | PTFE
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Model | PERPOSNATE
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Seat Leakage Class | VI
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Air to fail | Valve Close
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Sr.No. | 00687 2k6-10
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Travel | 57 MM
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Supply Pressure | 2.5 KSC
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | AFR | Janatics
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | P Shut | 4 KSC
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Model | AFR 1361/1563
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Auto Feed control Panel | Instrument System
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Body temperature RTD | MIEPL
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Brix electrode | Instrument System/10.2K
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Tail pipe temperature RTD | Instrument System
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Level Sensor | Instrument System
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Control valve |  |  | Vacuum Gauge | Waaree
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Make | Pnec I&S (PROCESS CONTROLS)
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Sr.No. | 127
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Type | Diaphragm
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Model | GLOBE VOLVE
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Year of Manufacture | 2000
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Tubing | PU tube
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Size | 150 MM
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Cv | 220
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Hand wheel | NO
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Material Disc/Body | SS-316 / CAST IRON
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Characteristic | Equal %
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Positioner | I&S
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Seat Replacement type | TEFLON
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Model | PERPOSNATE
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Seat Leakage Class | VI
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Air to fail | Valve Close
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Sr.No. | 000127 2k6-10
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Travel | 57 MM
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Supply Pressure | 2.5 KSC
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | AFR | Janatics
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | P Shut | 4 KSC
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Model | AFR 1361/1563
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Auto Feed control Panel | Instrument System
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Body temperature RTD | Instrument System
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Brix electrode | Instrument System/10.2K
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Tail pipe temperature RTD | Instrument System
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Level Sensor | Instrument System
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Control valve |  |  | Vacuum Gauge | Waaree
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Make | Pnecon
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Sr.No. | 688
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Type | Diaphragm
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Model | PERPOSNATE
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Year of Manufacture | Tubing
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Size | 3''
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Cv | 220
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Hand wheel | NO
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Material Disc/Body | SS-316 / WBC
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Characteristic | Equal %
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Positioner | Pneucon
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Seat Replacement type | PTFE
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Model | PVP-1
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Seat Leakage Class | VI
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Air to fail | Valve Close
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Travel | 38 MM
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Supply Pressure | 2.5 KSC
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | AFR | Janatics
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | P Shut | 4 KSC
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Model | AFR 1361
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Auto Feed control Panel | Instrument System
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Body temperature RTD | Instrument System
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Vacuum Gauge | Waaree
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Brix electrode | Instrument System/2K-6-5
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Control valve |  |  | Level Sensor | Instrument System
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Make | Pnecon
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Sr.No. | 690
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Type | Diaphragm
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Model | PERPOSNATE
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Year of Manufacture | 2000
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Tubing | PU tube
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Size | 3''
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Cv | 220
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Hand wheel | NO
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Material Disc/Body | SS-316 / WBC
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Characteristic | Equal %
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Positioner | Pneucon
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Seat Replacement type | PTFE
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Model | PVP-1
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Seat Leakage Class | VI
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Air to fail | Valve Close
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Travel | 38 MM
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Supply Pressure | 2.5 KSC
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | AFR | Janatics
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | P Shut | 4 KSC
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Model | AFR 1361
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Brix Electrode | Instrument System/2K-6-5
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Body Temperature RTD | Instrument System
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | Control valve |  |  | Vacuum Gauge | Waaree
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Make | Pnecon
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Sr.No. | 639
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Type | Diaphragm
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Model | PERPOSNATE
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Year of Manufacture | 2000
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Tubing | PU tube
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Size | 3''
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Cv | 220
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Hand wheel | NO
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Material Disc/Body | SS-316 / WBC
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Characteristic | Equal %
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Positioner | Pneucon
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Seat Replacement type | PTFE
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Model | PVP-1
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Seat Leakage Class | VI
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Air to fail | Valve Close
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Travel | 38 MM
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Supply Pressure | 2.5 KSC
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | AFR | Janatics
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | 4 KSC | Model
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Brix Electrode | Instrument System/2K-6-5
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Body Temperature RTD | Instrument System
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | Control valve |  |  | Vacuum Gauge | Waaree
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Make | Pnecon
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Sr.No. | 691
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Type | Diaphragm
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Model | PERPOSNATE
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Year of Manufacture | 2000
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Tubing | PU tube
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Size | 3''
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Cv | 220
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Hand wheel | NO
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Material Disc/Body | SS-316 / WBC
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Characteristic | Equal %
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Positioner | Pneucon
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Seat Replacement type | PTFE
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Model | PVP-1
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Seat Leakage Class | VI
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Air to fail | Valve Close
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Travel | 38 MM
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Supply Pressure | 2.5 KSC
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | AFR | Janatics
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | P Shut | 4 KSC
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Model | AFR 1361/1563
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Brix Electrode | Instrument System/2K-6-5
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Body Temperature RTD | Instrument System
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Vacuum Gauge | Waaree
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | Control valve |  |  | Tail Pipe temperature RTD | MIEPL
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Make | Aira
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Sr.No. | Type
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Model | Year of Manufacture
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Tubing | PU TUBE
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Size | 1''
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Cv | Hand wheel
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Material Disc/Body | ss
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Characteristic | Positioner
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Seat Replacement type | PTFE
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Type of Valve | 2way on /off cantrolvalve
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Seat Leakage Class | VI
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Air to fail | n/c
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Sr.No. | SO62423404
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Travel | 25mm
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Supply Pressure | 4.5 to 7bar
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Air pr. Min /Max | 10bar
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | P Shut | Model
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | SOV | Kushako india/K-412-S
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Vacuum transmitter | Barksdale/UPA2
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | Control valve |  |  | Control panel | Masibus
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Make | aira
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Sr.No. | Type
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Model | Year of Manufacture
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Tubing | PU TUBE
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Size | 1''
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Cv | Hand wheel
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Material Disc/Body | ss
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Characteristic | Positioner
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Seat Replacement type | PTFE
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Type of Valve | 2way on /off cantrolvalve
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Seat Leakage Class | VI
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Air to fail | n/c
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Sr.No. | SO62423404
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Travel | 25mm
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Supply Pressure | 4.5 to 7bar
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Air pr. Min /Max | 10bar
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | P Shut | Model
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | SOV | Kushako india/K-412-S
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Vacuum transmitter | Barksdale/UPA2
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | Control valve |  |  | Control panel | Masibus
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Make | aira
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Sr.No. | Type
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Model | Year of Manufacture
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Tubing | PU TUBE
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Size | 1''
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Cv | Hand wheel
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Material Disc/Body | ss
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Characteristic | Positioner
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Seat Replacement type | PTFE
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Type of Valve | 2way on /off cantrolvalve
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Seat Leakage Class | VI
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Air to fail | n/c
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Sr.No. | SO62423404
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Travel | 25mm
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Supply Pressure | 4.5 to 7bar
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Air pr. Min /Max | 10bar
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | P Shut | Model
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | SOV | Kushako india/K-412-S
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Vacuum transmitter | Barksdale/UPA2
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | Control valve |  |  | Control panel | Masibus
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Make | aira
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Sr.No. | Type
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Model | Year of Manufacture
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Tubing | PU TUBE
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Size | 1''
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Cv | Hand wheel
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Material Disc/Body | ss
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Characteristic | Positioner
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Seat Replacement type | PTFE
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Type of Valve | 2way on /off cantrolvalve
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Seat Leakage Class | VI
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Air to fail | n/c
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Sr.No. | SO62423404
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Travel | 25mm
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Supply Pressure | 4.5 to 7bar
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Air pr. Min /Max | 10bar
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | P Shut | Model
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | SOV | Kushako india/K-412-S
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Vacuum transmitter | Barksdale/UPA2
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | Control valve |  |  | Control panel | Masibus
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Make | aira
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Sr.No. | SO62423404
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Model | Year of Manufacture
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Tubing | PU TUBE
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Size | 1''
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Cv | Hand wheel
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Material Disc/Body | ss
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Characteristic | Positioner
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Seat Replacement type | PTFE
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Type of Valve | 2way on /off cantrolvalve
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Seat Leakage Class | VI
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Air to fail | n/c
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Sr.No. | SO62423404
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Travel | 25mm
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Supply Pressure | 4.5 to 7bar
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Air pr. Min /Max | 10bar
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | P Shut | Model
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | SOV | Kushako india/K-412-S
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Vacuum transmitter | Barksdale/UPA2
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | Control valve |  |  | Control panel | Masibus
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Make | aira
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Sr.No. | SO62423404
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Model | Year of Manufacture
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Tubing | PU TUBE
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Size | 1''
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Cv | Hand wheel
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Material Disc/Body | ss
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Characteristic | Positioner
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Seat Replacement type | PTFE
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Type of Valve | 2way on /off cantrolvalve
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Seat Leakage Class | VI
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Air to fail | n/c
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Sr.No. | SO62423404
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Travel | 25mm
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Supply Pressure | 4.5 to 7bar
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Air pr. Min /Max | 10bar
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | P Shut | Model
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | SOV | Kushako india/K-412-S
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Vacuum transmitter | Barksdale/UPA2
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | Control valve |  |  | Control panel | Masibus
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Make | aira
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Sr.No. | SO62423404
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Model | RKS (Angel Type)
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Year of Manufacture | 2024
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Tubing | PU TUBE
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Size | 1''
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Cv | Hand wheel
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Material Disc/Body | ss
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Characteristic | Positioner
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Seat Replacement type | PTFE
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Type of Valve | 2way on /off cantrolvalve
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Seat Leakage Class | VI
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Air to fail | n/c
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Sr.No. | SO62423404
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Travel | 25mm
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Supply Pressure | 4.5 to 7bar
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Air pr. Min /Max | 10bar
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | P Shut | Model
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | SOV | Kushako india/K-412-S
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Vacuum transmitter | Barksdale/UPA2
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | Control valve |  |  | Control panel | Masibus
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Make | Pnecon
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Sr.No. | 171050006
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Type | Diaphram
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Model | 110/DVD 300S
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Year of Manufacture | Tubing
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Size | 300 MM
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Cv | 1350
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Hand wheel | YES
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Material Disc/Body | WCC+IBR
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Characteristic | Equal %
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Positioner | Pneucon
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Seat Replacement type | PTFE
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Model | PVP-1
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Seat Leakage Class | Air to fail
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Valve Close | Sr.No.
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Travel | 90 MM
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Supply Pressure | 50 PSI
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | AFR | Janatics
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | P Shut | 2 KSC
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Model | AFR 1361
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Pressure Transmitter | Siemens/7MF4033-1CA102AC0Z
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | Control valve |  |  | Pressure Gauge | 02 Kg/cm2
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Make | ARKA
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Sr.No. | 811101P
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Type | Diaphram
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Model | A980140
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Year of Manufacture | 1996
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Tubing | SS- tube
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Size | 50 MM
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Cv | 68
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Hand wheel | NO
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Material Disc/Body | SS-A216 / WBC
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Characteristic | Equal %
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Positioner | Pneucon
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Seat Replacement type | SS-
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Model | PVP-1
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Seat Leakage Class | VI
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Air to fail | Valve Close
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Travel | 37 MM
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Supply Pressure | 2.5 KSC
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | AFR | Janatics
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | P Shut | 4 KSC
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Model | AFR 1361
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Temperature Transmitter | Masibus/TT7S10-H
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Exhaust Temperature RTD | Genaral/6mm 450mm
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Pressure Gauge | 40 kg Cm/2
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | Control valve |  |  | Temperature Indicator | Masibus/LC5296
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Make | ARKA
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Sr.No. | 811101
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Type | Diaphram
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Model | A970015
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Year of Manufacture | 1996
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Tubing | Ss-tube
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Size | 50 MM
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Cv | 68
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Hand wheel | NO
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Material Disc/Body | SS-A216 / WBC
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Characteristic | Equal %
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Positioner | Pneucon
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Seat Replacement type | SS
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Model | PVP-1
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Seat Leakage Class | VI
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Air to fail | Valve Close
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Travel | 37 MM
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Supply Pressure | 2.5 KSC
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | AFR | Janatics
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | P Shut | 4 KSC
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | Control valve |  |  | Model | AFR 1361
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Make | EL-O-Matic
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Sr.No. | 2307
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Type | Double Acting
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Model | ED1600/A
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Year of Manufacture | 2016
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Tubing | SS-Tube
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Size | 350 MM
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Cv | Hand wheel
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Material Disc/Body | SS / WBC
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Characteristic | Throttling
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Positioner | YTC
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Seat Replacement type | ****
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Type of Valve | Butterfly
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Model -YT | 1200RD532SO
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Seat Leakage Class | VI
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Air to fail | Valve Locked
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Travel | 90 DEG.
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Supply Pressure | 2.5 KSC
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | AFR | Janatics
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | P Shut | 4 KSC
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Model | AFR 1361
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | RTD | MIEPL
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | Control valve |  |  | Iind Vapore Temp. Indiactor | Masibus/LC5296
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Make | El-O-matic
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Sr.No. | 2311
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Type | Double Acting
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Model | ED 1600/A
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Year of Manufacture | 2016
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Tubing | SS-Tube
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Size | 900 MM
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Cv | Hand wheel
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Material Disc/Body | SS-316 / WBC
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Characteristic | Throttling
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Positioner | YTC
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Seat Replacement type | ****
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Type of Valve | Butterfly
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Model -YT | 1200RD532SO
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Seat Leakage Class | VI
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Air to fail | Valve Locked
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Travel | 90 DEG
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Supply Pressure | 4 KSC
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | AFR | Janatics
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | P Shut | 4 KSC
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Model | AFR 1361
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | RTD | MIEPL
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | Control valve |  |  | Pressure gauge | 02 kg /cm2
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Make | El-O-matic
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Sr.No. | 5991
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Type | Double Acting
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Model | PD2500/A
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Year of Manufacture | 2016
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Tubing | SS-Tube
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Size | 1200 MM
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Cv | Hand wheel
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Material Disc/Body | SS-316 / WBC
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Characteristic | Throttling
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Positioner | YTC
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Seat Replacement type | PTFE
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Type of Valve | Butterfly
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Model -YT | 1200RD532SO
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Seat Leakage Class | VI
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Air to fail | Valve Locked
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Travel | 90DEG
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Supply Pressure | 2.5 KSC
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | AFR | Janatics
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | P Shut | 4 KSC
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Model | AFR 1361
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | RTD | Tosaniwal
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | Control valve |  |  | Pressure gauge | 02 kg /cm2
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Make | El-O-matic
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Sr.No. | 2310
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Type | Double Acting
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Model | ED 1600/A
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Year of Manufacture | 2016
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Tubing | SS
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Size | 900 MM
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Cv | Hand wheel
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Material Disc/Body | SS-316 / WBC
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Characteristic | Throttling
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Positioner | YTC
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Seat Replacement type | Type of Valve
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Butterfly | Model
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Seat Leakage Class | Air to fail
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Valve Locked | Sr.No.
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Travel | 90 DEG
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Supply Pressure | 4 KSC
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | AFR | Janatics
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | P Shut | 4 KSC
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Model | AFR 1361
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | RTD | Tosaniwal
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Pressure gauge | 02 kg /cm2
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | Control valve |  |  | Temperature Indiactor | Masibus/LC5296
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Make | El-O-matic
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Sr.No. | 2317
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Type | Double Acting
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Model | ED1600/A
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Year of Manufacture | 2016
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Tubing | SS-tube
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Size | 900 MM
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Cv | Hand wheel
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Material Disc/Body | SS-316 / WBC
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Characteristic | Throttling
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Positioner | Pneucon
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Seat Replacement type | Type of Valve
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Butterfly | Model
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Seat Leakage Class | Air to fail
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Valve Locked | Sr.No.
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Travel | 90 DEG
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Supply Pressure | 2.5 KSC
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | AFR | Janatics
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | P Shut | 4 KSC
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Model | AFR 1361
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | RTD | Tosaniwal
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Vacuuam Gauge | -760
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | Control valve |  |  | Temperature transmitter | Masibus/LC5296
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Make | EL-o-matic
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Sr.No. | 2306
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Type | Double Acting
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Model | ED 1600-A
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Year of Manufacture | 2016
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Tubing | SS
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Size | 800 MM
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Cv | Hand wheel
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Material Disc/Body | SS-316 / WBC
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Characteristic | Throttling
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Positioner | YTC
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Seat Replacement type | Type of Valve
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Butterfly | Model
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Seat Leakage Class | Air to fail
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Valve Locked | Sr.No.
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Travel | 90 DEG
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Supply Pressure | 2.5 KSC
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | AFR | Janatics
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | P Shut | 4 KSC
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Model | AFR 1361
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | RTD | Tosaniwal
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Vacuuam Gauge | -760
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | Control valve |  |  | Temperature Indicator | Masibus/LC5296
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Make | EL-o-matic
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Sr.No. | 2316
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Type | Double Acting
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Model | ED1600/A
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Year of Manufacture | 2016
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Tubing | SS
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Size | 800 MM
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Cv | Hand wheel
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Material Disc/Body | SS-316 / WBC
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Characteristic | Throttling
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Positioner | YTC
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Seat Replacement type | Type of Valve
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Butterfly | Model
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Seat Leakage Class | Air to fail
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Valve Locked | Sr.No.
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Travel | 90DEG
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Supply Pressure | 2.5 KSC
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | AFR | Janatics
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | P Shut | 4 KSC
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Model | AFR 1361
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | RTD | Tosaniwal
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | Control valve |  |  | Vacuuam Gauge | -760
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Make | EL-o-matic
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Sr.No. | 2315
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Type | Double Acting
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Model | ED1600/A
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Year of Manufacture | 2016
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Tubing | ss
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Size | 800 MM
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Cv | Hand wheel
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Material Disc/Body | SS-316 / WBC
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Characteristic | Throttling
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Positioner | YTC
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Seat Replacement type | Type of Valve
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Butterfly | Model
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Seat Leakage Class | VI
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Air to fail | Valve Locked
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Sr.No. | 1200RD532SO
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Travel | 90DEG
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Supply Pressure | 4 KSC
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | AFR | Janatics
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | P Shut | 4 KSC
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Model | AFR 1361
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | RTD | Tosaniwal
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | Control valve |  |  | Vacuuam Gauge | -760
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Make | EL-o-matic
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Sr.No. | 2308
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Type | Double Acting
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Model | ED1600/A
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Year of Manufacture | 2016
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Tubing | SS
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Size | 800 MM
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Cv | Hand wheel
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Material Disc/Body | SS-316 / WBC
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Characteristic | Throttling
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Positioner | YTC
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Seat Replacement type | Type of Valve
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Butterfly | Model
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Seat Leakage Class | Air to fail
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Valve Locked | Sr.No.
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Travel | 90DEG
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Supply Pressure | 2.5 KSC
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | AFR | Janatics
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | P Shut | 4 KSC
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Model | AFR 1361
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | RTD | Tosaniwal
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | Control valve |  |  | Vacuuam Gauge | -760
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Make | EL-o-matic
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Sr.No. | 2309
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Type | Double Acting
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Model | ED1600/A
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Year of Manufacture | 2016
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Tubing | SS
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Size | 800 MM
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Cv | Hand wheel
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Material Disc/Body | SS-316 / WBC
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Characteristic | Throttling
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Positioner | YTC
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Seat Replacement type | Type of Valve
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Butterfly | Model
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Seat Leakage Class | VI
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Air to fail | Valve Locked
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Sr.No. | 1200RD532SO
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Travel | 90DEG
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Supply Pressure | 4 KSC
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | AFR | Janatics
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | P Shut | 4 KSC
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Model | AFR 1361
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | RTD | Tosaniwal
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Vacuuam Gauge | -760
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | Control valve |  |  | Temperature Indicator | Masibus/LC5296
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Make | EL-o-matic
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Sr.No. | 2314
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Type | Double Acting
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Model | ED1600/A
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Year of Manufacture | 2016
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Tubing | SS
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Size | 1100MM
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Cv | Hand wheel
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Material Disc/Body | SS-316 / WBC
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Characteristic | Throttling
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Positioner | YTC
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Seat Replacement type | Type of Valve
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Butterfly | Model
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Seat Leakage Class | VI
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Air to fail | Valve Locked
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Sr.No. | 1200RD532SO
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Travel | 90DEG
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Supply Pressure | 4 KSC
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | AFR | Janatics
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | P Shut | 4 KSC
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Model | AFR 1361
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | RTD | Tosaniwal
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Vacuuam Gauge | -760
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | Control valve |  |  | Temperature Indicator | Masibus/LC5296
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Make | EL-o-matic
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Sr.No. | 2315
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Type | Double Acting
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Model | ED1600/A
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Year of Manufacture | 2016
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Tubing | SS
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Size | 900MM
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Cv | Hand wheel
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Material Disc/Body | SS-316 / WBC
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Characteristic | Throttling
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Positioner | YTC
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Seat Replacement type | Type of Valve
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Butterfly | Model
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Seat Leakage Class | Air to fail
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Valve Locked | Sr.No.
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Travel | 90DEG
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Supply Pressure | 4 KSC
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | AFR | Janatics
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | P Shut | 4 KSC
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Model | AFR 1361
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | RTD | Tosaniwal
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Vacuuam Gauge | -760
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | Control valve |  |  | Temperature Indicator | Masibus/LC-5296
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Make | Pneucon
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Sr.No. | 20H0611214
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Type | Diaphargm
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Model | 110/PDC-30
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Year of Manufacture | 2000
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Tubing | PU
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Size | 25 MM
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Cv | 5
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Hand wheel | NO
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Material Disc/Body | WCB/IBR
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Characteristic | Equal %
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | SOV | Rotex
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Seat Replacement type | SS 304
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Type of Valve | Globe Valve
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Model | 3012-6G
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Seat Leakage Class | Air to fail
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Valve Closed | Sr.No.
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Travel | 14.3 MM
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Supply Pressure | AFR
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Air pr. Min /Max | P Shut
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Model | 1361
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | RTD | MIEPL
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | Control valve |  |  | Temperature Controller | Masibus
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Make | Pneucon
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Sr.No. | 686
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Type | Diaphargm
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Model | PERPOSNATE
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Year of Manufacture | 2000
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Tubing | PU
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Size | 50 MM
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Cv | 5
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Hand wheel | NO
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Material Disc/Body | WCB/IBR
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Characteristic | Equal %
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Positioner | I&S
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Seat Replacement type | SS 304
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Type of Valve | Globe Valve
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Model | 3012-6G
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Seat Leakage Class | Air to fail
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Valve Closed | Sr.No.
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Travel | 28MM
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Supply Pressure | AFR
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Air pr. Min /Max | P Shut
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Model | 1361
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | Control valve |  |  | Level Transmitter | ABB/266DDHSSA2
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Make | Pnecon
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Sr.No. | 130231407
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Type | DIAPHRAGM
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Model | 230/PDC 055 S
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Year of Manufacture | 2016
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Tubing | SS tube
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Size | 100 MM
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Cv | 275
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Hand wheel | yes
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Material Disc/Body | A216GR/SS-316
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Characteristic | Throttling
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Positioner | Pneucon
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Seat Replacement type | PTFE
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Type of Valve | Butterfly
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Model | PVP-1
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Seat Leakage Class | VI
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Air to fail | Open
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Travel | 90DEG
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Supply Pressure | 2.5 KSC
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | AFR | Janatics
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | P Shut | 5 KSC
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Model | AFR 1361/1361
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | Control valve |  |  | Pressure Gauge-03 | 2,4,7 kg/cm2
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Make | Pnecon
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Sr.No. | 151141501
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Type | Single Acting
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Model | 232/SA125+M
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Year of Mfg. | 2016
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Tubing | ss
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Size | 150 MM
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Cv | 650
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Hand wheel | YES
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Material Disc/Body | A216GR-WCB/SS-304
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Characteristic | Throtling
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Positioner | YTC
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Seat Replacement type | PTFE
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Type of Valve | Butterfly
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Seat Leakage Class | Air to fail
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Valve Open | Sr.No.
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Travel | 90DEG
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Supply Pressure | 2.5 KSC
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | AFR | Janatics
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | P Shut | 4 KSC
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | Control valve |  |  | Model | AFR 1361/1363
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Make | Pnecon
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Sr.No. | 160941991
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Type | Single Acting
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Model | 232/SA-125
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Year of Manufacture | Tubing
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Size | 150 MM
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Cv | 650
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Hand wheel | NO
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Material Disc/Body | SS-316 / A216GR-WCB
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Characteristic | Equal %
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Positioner | YTC
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Seat Replacement type | PTFE
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Type of Valve | Butterfly
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Model -YT | 1200RD532SO
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Seat Leakage Class | VI
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Air to fail | Valve Open
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Sr.No. | MO113499
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Travel | 90 DSG
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Supply Pressure | 4 KSC
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | AFR | Janatics
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | P Shut | 4 KSC
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Model | AFR 1361
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | Control valve |  |  | Pressure Gauge-02 | 2,2 kgcm/2
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Make | RK CONTROL
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Sr.No. | 12130949
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Type | Diaphragm
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Model | SR.80/A3-150H
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Year of Manufacture | Tubing
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Size | 250 MM
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Cv | 1850
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Hand wheel | YES
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Material Disc/Body | CI+EPDM SLEEV
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Characteristic | Equal %
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Positioner | RK CONTROL
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Seat Replacement type | EPDM
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Type of Valve | BUTTERFLY
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Seat Leakage Class | Air to fail
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Valve Close | Sr.No.
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Travel | 2.1/4''
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Supply Pressure | 35 psig
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | AFR | Janatics
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | P Shut | Model
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Temperature transmitter | Masibus/TT7S10-H
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | RTD | Tosaniwal
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Vacuuam gauge | 1
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | Control valve |  |  | Compound Gauge | 1
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Make | Pnecon
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Sr.No. | Type
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Model | 110PDC95
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Year of Manufacture | 2000
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Tubing | PU tube
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Size | 100 MM
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Cv | 220
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Hand wheel | NO
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Material Disc/Body | SS-316 / WBC
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Characteristic | Equal %
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Positioner | Pneucon
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Seat Replacement type | Type of Valve
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Globe Valve(Contoured) | Model
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Seat Leakage Class | Air to fail
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Valve Close | Sr.No.
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Travel | 38 MM
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Supply Pressure | 2.5 KSC
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | AFR | Janatics
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | P Shut | 4 KSC
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | Control valve |  |  | Model | AFR 1361
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Make | Pnecon
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Sr.No. | 130231402
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Type | Diaphram
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Model | 110/PDC030T
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Year of Manufacture | Tubing
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Size | 25 MM
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Cv | 13
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Hand wheel | YES
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Material Disc/Body | A216C-WBC/SS-316
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Characteristic | Equal %
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Positioner | Pneucon
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Seat Replacement type | SS
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Model | PVP-1
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Seat Leakage Class | Air to fail
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Valve Close | Sr.No.
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Travel | 26MM
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Supply Pressure | 2.5 KSC
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | AFR | Janatics
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | P Shut | 4 KSC
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Model | AFR 1361
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Pressure Transmitter | Alfa control
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | Control valve |  |  | Controller | Honeywell/1040
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Make | EL-O-matic
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Sr.No. | 5992
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Type | Doble Acting
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Model | PD 2500/A
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Year of Manufacture | Tubing
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Size | 1200 MM
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Cv | Hand wheel
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Material Disc/Body | SS-316 / WBC
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Characteristic | Throttling
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Positioner | YTC
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Seat Replacement type | Type of Valve
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Butterfly | Model
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Seat Leakage Class | Air to fail
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Valve locked | Sr.No.
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Travel | 90 DEG
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Supply Pressure | 2.5 KSC
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | AFR | Janatics
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | P Shut | 4 KSC
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Model | AFR 1361
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Temperature Transmitter | Masibus
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | RTD | Tosaniwal
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | Control valve |  |  | Level Tx.-03 Nos | Siemens
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Make | EL-O-matic
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Sr.No. | 5993
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Type | Doble Acting
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Model | PD 2500/A
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Year of Manufacture | Tubing
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Size | 1200 MM
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Cv | Hand wheel
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Material Disc/Body | SS-316 / WBC
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Characteristic | Positioner
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Seat Replacement type | Type of Valve
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Butterfly | Model
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Seat Leakage Class | Air to fail
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Valve locked | Sr.No.
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Travel | 90 DEG
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Supply Pressure | 2.5 KSC
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | AFR | Janatics
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | P Shut | 4 KSC
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Model | AFR 1361
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Temperature Transmitter | Masibus
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | RTD | Tosaniwal
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | Control valve |  |  | Pressure Gauge-02 | 2 kgcm/2
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Make | Pnecon
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Sr.No. | 130231403
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Type | Diaphram
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Model | 230PDS140S
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Year of Manufacture | 2016
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Tubing | SS
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Size | 250 MM
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Cv | Hand wheel
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Material Disc/Body | A216GR-WBC/SS-316
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Characteristic | Positioner
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Seat Replacement type | PTFE
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Type of Valve | BUTTERFLY
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Model | PVP-1
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Seat Leakage Class | Air to fail
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Valve opens | Sr.No.
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Travel | 90ᵒ
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Supply Pressure | 2.5 KSC
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | AFR | Janatics
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | P Shut | 4 KSC
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | Model | AFR 1361
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | AH Common IL Temp. Tx. | Masibus
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | AH2 OL Molasses Temp. Tx. | Masibus
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | AH1 OL Molasses Temp. Tx. | Masibus
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | AH Common IL Temp RTD | Tosaniwal
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | AH2 OL Molasses Temp. RTD | Tosaniwal
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | Control valve |  |  | AH1 OL Molasses Temp. RTD | Tosaniwal
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Make | Continental
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Sr.No. | nil
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Type | Single Acting
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Model | 3102
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Year of Manufacture | 2022
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Tubing | SS
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Size | 100 MM
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Cv | Hand wheel
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Material Disc/Body | SS-316 / WBC
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Characteristic | Equal %
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Positioner | YTC
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Seat Replacement type | PTFE
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Type of Valve | Butterfly
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Model | EP-1000RSN
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Seat Leakage Class | Air to fail
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Close | Sr.No.
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Travel | 90 DEG
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Supply Pressure | 2.5 KSC
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | P Shut | 4 KSC
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | Control valve |  |  | Level Indicator-01 | Masibus/5296
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Make | Pneucon
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Sr.No. | 20H0611221
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Type | Diaphargm
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Model | 110/PDC-30
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Year of Mfg. | 2007
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Tubing | PU
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Size | 25 MM
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Cv | 13
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Hand wheel | NO
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Material Disc/Body | WCB
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Characteristic | Equal %
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Positioner | SOV
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Seat Replacement type | SS 304
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Type of Valve | Globe Valve
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Model | 3012-6G
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Seat Leakage Class | Air to fail
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Valve Closed | Sr.No.
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Travel | 14.3 MM
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Supply Pressure | AFR
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Air pr. Min /Max | P Shut
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Model | 136134
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Level controller-01 | Masibus
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | RTD-01 | MIEPL
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Temperature controller-02 | Masibus
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | Control valve |  |  | Level Transmitter-01 | Siemens
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Make | Pneucon
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Sr.No. | 20H0611212
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Type | Diaphargm
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Model | 110/PDC-30
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Year of Manufacture | Tubing
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Size | 25 MM
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Cv | 5
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Hand wheel | NO
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Material Disc/Body | WCB/IBR
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Characteristic | Equal %
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Positioner | SOV
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Seat Replacement type | SS 304
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Type of Valve | Globe Valve
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Model | 3012-6G
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Seat Leakage Class | Air to fail
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Valve Closed | Sr.No.
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Travel | 14.3 MM
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Supply Pressure | AFR
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Air pr. Min /Max | P Shut
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Model | 136134
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Level Sensor | Temell/PV1-C4E
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | Control valve |  |  | Brix sensor | SAMAR
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Make | Continental Valve limited
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Sr.No. | 13107
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Type | Single Acting
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Model | Year of Manufacture
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Tubing | PU tube
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Size | 250 MM
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Cv | 1900
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Hand wheel | NO
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Material Disc/Body | WBC/CF8
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Characteristic | Equal %
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Positioner | Dome switch
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Seat Replacement type | PTFE
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Type of Valve | Butterfly
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Seat Leakage Class | VI
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Air to fail | Valve Close
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Travel | 38 MM
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Supply Pressure | 2.5 KSC
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | AFR | Shavo
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | P Shut | 4 KSC
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Model-SB-11-4SN | 200 M 1/4"
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Level Transmitter | ABB
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Control Panel Make | Parsia molen
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Load Cell-03 | Capacity -10 Ton
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Control valve |  |  | Control Panel Model | I410
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Make | Continental Valve limited
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Sr.No. | 13106
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Type | Single Acting
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Model | Year of Manufacture
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Tubing | PU tube
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Size | 250 MM
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Cv | 1900
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Hand wheel | NO
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Material Disc/Body | WBC/CF8
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Characteristic | Equal %
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Positioner | Dome switch
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Seat Replacement type | PTFE
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Type of Valve | Butterfly
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Seat Leakage Class | VI
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Air to fail | Valve Close
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Travel | 38 MM
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Supply Pressure | 2.5 KSC
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | AFR | Shavo
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | P Shut | 4 KSC
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Model-SB-11-4SN | 200 M 1/4"
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | Control valve |  |  | Check Indicator | make-RKD
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Make | Revo
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Sr.No. | RD5050007000000
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Type | Double Acting
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Model | Year of Manufacture
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Tubing | PU tube
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Size | 200 MM
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Cv | 1225
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Hand wheel | NO
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Material Disc/Body | WBC/CF8
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Characteristic | Equal %
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Positioner | Dome switch
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Seat Replacement type | PTFE
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Type of Valve | Butterfly
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Seat Leakage Class | VI
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Air to fail | Valve locked
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Travel | 38 MM
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Supply Pressure | 2.5 KSC
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | AFR | Shavo
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | P Shut | 4 KSC
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Model-SB-11-4SN | 200 M 1/4"
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Control Panel | Precia molen
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | Control valve |  |  | Model | I410
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Make | Pnecon
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Sr.No. | 1602 41992
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Type | Double Acting
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Model | 232 SA-150 M
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Year of Manufacture | 2015
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Tubing | PU tube
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Size | 200 MM
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Cv | 1225
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Hand wheel | NO
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Material Disc/Body | A216GR WBC/SS 304
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Characteristic | On-off
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Positioner | Dome switch
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Seat Replacement type | PTFE
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Type of Valve | Butterfly
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Seat Leakage Class | VI
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Air to fail | Valve closed
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Travel | 38 MM
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Supply Pressure | 2.5 KSC
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | AFR | Shavo
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | P Shut | 4 KSC
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Model-SB-11-4SN | 200 M 1/4"
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | Control valve |  |  | Check Indicator-01 | Make- ESSPEE
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Make | Deltorq
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Sr.No. | 21000448-01
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Type | Single Acting
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Model | 350-10
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Year of Manufacture | 2019
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Tubing | PU tube
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Size | 350 MM
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Cv | 1900
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Hand wheel | NO
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Material Disc/Body | WBC/CF8
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Characteristic | Equal %
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Dome switch | Rotex
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Seat Replacement type | PTFE
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Type of Valve | Butterfly
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Seat Leakage Class | VI
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Air to fail | Valve Close
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Travel | 38 MM
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Supply Pressure | 2.5 KSC
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | AFR | Shavo
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | P Shut | 4 KSC
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Model-SB-11-4SN | 200 M 1/4"
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Level Transmitter | ABB/3KB21900114342
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Control Panel Make | Parsia molen
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Load Cell-03 | Capacity -10 Ton
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Control valve |  |  | Control Panel Model | I410
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Make | Deltorq
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Sr.No. | 13003926-01
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Type | Single Acting
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Model | 350-10
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Year of Manufacture | 2019
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Tubing | PU tube
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Size | 350 MM
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Cv | 1900
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Hand wheel | NO
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Material Disc/Body | WBC/CF8
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Characteristic | Equal %
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Dome switch | Rotex
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Seat Replacement type | PTFE
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Type of Valve | Butterfly
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Seat Leakage Class | VI
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Air to fail | Valve Close
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Travel | 38 MM
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Supply Pressure | 2.5 KSC
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | AFR | Shavo
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | P Shut | 4 KSC
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Control valve |  |  | Model-SB-11-4SN | 200 M 1/4"
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Make | Pnecon
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Sr.No. | 1602 44993
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Type | Double Acting
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Model | 232 SA-150 M
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Year of Manufacture | 2016
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Tubing | PU tube
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Size | 200 MM
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Cv | 1225
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Hand wheel | NO
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Material Disc/Body | A216GR WBC/SS 304
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Characteristic | On-off
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Positioner | Dome switch
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Seat Replacement type | PTFE
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Type of Valve | Butterfly
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Seat Leakage Class | VI
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Air to fail | Valve closed
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Travel | 38 MM
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Supply Pressure | 2.5 KSC
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | AFR | Shavo
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | P Shut | 4 KSC
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | Control valve |  |  | Model-SB-11-4SN | 200 M 1/4"
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Make | TRANSTORK
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Sr.No. | 9200
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Type | Double Acting
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Model | MOR-100
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Year of Manufacture | 2025
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Tubing | PU tube
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Size | 100 MM
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Cv | 1225
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Hand wheel | NO
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Material Disc/Body | A216GR WBC/SS 304
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Characteristic | On-off
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Positioner | Dome switch
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Seat Replacement type | PTFE
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Type of Valve | Butterfly
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Seat Leakage Class | VI
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Air to fail | Valve closed
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Travel | 38 MM
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Supply Pressure | 2.5 KSC
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | AFR | Shavo
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | P Shut | 4 KSC
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Model-SB-11-4SN | 200 M 1/4"
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Actuator Make/model | Crane/B24P 1774
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Vibration Tx.-01 | GEA/ID no:00005-1848-0,BW:10-1000 Hz,FS: 50mm/S
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Level Trans. | Rosemount/2051CD2A22A1AS1M4Q4
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Magnetic Flow Meter | Emerson (Rosemount) /8712EMR1A1M4
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | Control valve |  |  | Magnetic Flow Meter tube | Emerson (Rosemount)/8705TSA030C1W0
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Make | TRANSTORK
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Sr.No. | 7153
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Type | Double Acting
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Model | MOR-60
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Year of Manufacture | 2025
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Tubing | PU tube
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Size | 80 MM
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Cv | 1225
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Hand wheel | NO
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Material Disc/Body | A216GR WBC/SS 304
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Characteristic | On-off
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Positioner | Dome switch
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Seat Replacement type | PTFE
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Type of Valve | Butterfly
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Seat Leakage Class | VI
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Air to fail | Valve closed
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Travel | 38 MM
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Supply Pressure | 2.5 KSC
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | AFR | Shavo
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | P Shut | 4 KSC
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Model-SB-11-4SN | 200 M 1/4"
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | Control valve |  |  | Actuator Make/model | Crane/B24P 1774
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Make | TRANSTORK
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Sr.No. | 6835
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Type | Double Acting
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Model | MOR-60
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Year of Manufacture | 2025
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Tubing | PU tube
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Size | 80 MM
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Cv | 1225
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Hand wheel | NO
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Material Disc/Body | A216GR WBC/SS 304
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Characteristic | On-off
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Positioner | Dome switch
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Seat Replacement type | PTFE
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Type of Valve | Butterfly
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Seat Leakage Class | VI
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Air to fail | Valve closed
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Travel | 38 MM
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Supply Pressure | 2.5 KSC
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | AFR | Shavo
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | P Shut | 4 KSC
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Model-SB-11-4SN | 200 M 1/4"
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | Control valve |  |  | Actuator Make/model | Crane/B24P 1774
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Make | TRANSTORK
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Sr.No. | 9198
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Type | Double Acting
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Model | MOR-100
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Year of Manufacture | 2025
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Tubing | PU tube
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Size | 100 MM
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Cv | 1225
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Hand wheel | NO
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Material Disc/Body | A216GR WBC/SS 304
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Characteristic | On-off
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Positioner | Rotex
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Seat Replacement type | PTFE
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Type of Valve | Butterfly
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Model | RTX1600-R_0-2_R0-2G-4R-ST-FD-C
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Seat Leakage Class | VI
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Air to fail | Valve closed
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Travel | 38 MM
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Supply Pressure | 2.5 KSC
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | AFR | Shavo
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | P Shut | 4 KSC
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Model-SB-11-4SN | 200 M 1/4"
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | Control valve |  |  | Actuator | REVO/ETY9020020A
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Make | Aira
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Sr.No.1 | Type
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Model | RKS (Angel Type)
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Year of Manufacture | 2000
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Tubing | SS tube
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Size | 2''
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Cv | Hand wheel
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Material Disc/Body | SS-316
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Characteristic | ON- Off
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Positioner/SOV | Rotex
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Seat Replacement type | PTFE
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Type of Valve | Angle Valve(Contoured)
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Model | 3012-6-2G
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Seat Leakage Class | VI
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Air to fail | Valve Close
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Travel | Supply Pressure
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | 2.5 KSC | AFR
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | P Shut | 4 KSC
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Model | AFR 1361
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | Control Panel | Masibus
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | Control valve |  |  | RTD | MIEPL
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Make | Aira
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Sr.No.-2 | Type
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Model | RKS (Angel Type)
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Year of Manufacture | 2000
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Tubing | SS tube
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Size | 2''
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Cv | Hand wheel
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Material Disc/Body | SS-316
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Characteristic | ON- Off
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Positioner/SOV | Rotex
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Seat Replacement type | PTFE
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Type of Valve | Angle Valve(Contoured)
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Model | 3012-6-2G
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Seat Leakage Class | VI
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Air to fail | Valve Close
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Travel | Supply Pressure
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | 2.5 KSC | AFR
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | P Shut | 4 KSC
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Model | AFR 1361
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | Control Panel | Masibus
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | Control valve |  |  | RTD | MIEPL
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Make | Aira
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Sr.No.-3 | Type
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Model | RKS (Angel Type)
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Year of Manufacture | 2000
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Tubing | SS tube
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Size | 2''
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Cv | Hand wheel
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Material Disc/Body | SS-316
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Characteristic | ON- Off
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Positioner/SOV | Rotex
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Seat Replacement type | PTFE
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Type of Valve | Angle Valve(Contoured)
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Model | 3012-6-2G
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Seat Leakage Class | VI
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Air to fail | Valve Close
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Travel | Supply Pressure
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | 2.5 KSC | AFR
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | P Shut | 4 KSC
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Model | AFR 1361
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | Control Panel | Masibus
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | Control valve |  |  | RTD | MIEPL
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Make | Aira
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Sr.No.4 | Type
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Model | RKS (Angel Type)
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Year of Manufacture | 2000
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Tubing | SS tube
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Size | 2''
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Cv | Hand wheel
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Material Disc/Body | SS-316
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Characteristic | ON- Off
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Positioner/SOV | Rotex
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Seat Replacement type | PTFE
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Type of Valve | Angle Valve(Contoured)
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Model | 3012-6-2G
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Seat Leakage Class | VI
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Air to fail | Valve Close
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Travel | Supply Pressure
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | 2.5 KSC | AFR
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | P Shut | 4 KSC
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Model | AFR 1361
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | Control Panel | Masibus
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | Control valve |  |  | RTD | MIEPL
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Make | Aira
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Sr.No.5 | Type
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Model | RKS (Angel Type)
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Year of Manufacture | 2000
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Tubing | SS tube
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Size | 2''
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Cv | Hand wheel
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Material Disc/Body | SS-316
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Characteristic | ON- Off
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Positioner/SOV | Rotex
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Seat Replacement type | PTFE
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Type of Valve | Angle Valve(Contoured)
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Model | 3012-6-2G
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Seat Leakage Class | VI
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Air to fail | Valve Close
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Travel | Supply Pressure
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | 2.5 KSC | AFR
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | P Shut | 4 KSC
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Model | AFR 1361
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | Control Panel | Masibus
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | Control valve |  |  | RTD | MIEPL
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Make | Pneucon
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Sr.No.6 | 2409934F9
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Type | Gate
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Model | 12/PYD-100
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Year of Manufacture | 2024
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Tubing | SS tube
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Size | 40mm
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Cv | 30
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Hand wheel | NO
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Material Disc/Body | SS-304
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Characteristic | ON- Off
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Seat Replacement type | PTFE
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Type of Valve | Model
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Seat Leakage Class | VI
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Air to fail | Valve Close
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Travel | 19MM
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Supply Pressure | 60-85pSIG
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Air pr. Min /Max | 8bar
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | P Shut | 8bar(G)
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | Control Panel | Salect
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | Control valve |  |  | RTD | MIEPL
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | Control valve |  |  | Make | Sr.No.
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | Control valve |  |  | Model | Year of Manufacture
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | Control valve |  |  | Size | Cv
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | Control valve |  |  | Material Disc/Body | Characteristic
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | Control valve |  |  | Seat Replacement type | Type of Valve
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | Control valve |  |  | Seat Leakage Class | Air to fail
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | Control valve |  |  | Travel | Supply Pressure
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | Control valve |  |  | Air pr. Min /Max | P Shut
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | Control valve |  |  | Control panel | Masibus
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | Control valve |  |  | Pressure Transmitter | Siemense
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | Control valve |  |  | Make | Sr.No.
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | Control valve |  |  | Model | Year of Manufacture
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | Control valve |  |  | Size | Cv
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | Control valve |  |  | Material Disc/Body | Characteristic
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | Control valve |  |  | Seat Replacement type | Type of Valve
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | Control valve |  |  | Seat Leakage Class | Air to fail
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | Control valve |  |  | Travel | Supply Pressure
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | Control valve |  |  | Air pr. Min /Max | P Shut
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | Control valve |  |  | Make | Sr.No.
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | Control valve |  |  | Model | Year of Manufacture
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | Control valve |  |  | Size | Cv
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | Control valve |  |  | Material Disc/Body | Characteristic
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | Control valve |  |  | SOV | Rotex
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | Control valve |  |  | Seat Replacement type | Type of Valve
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | Control valve |  |  | Model | SR-3012
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | Control valve |  |  | Seat Leakage Class | Air to fail
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | Control valve |  |  | Travel | Supply Pressure
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | Control valve |  |  | Air pr. Min /Max | P Shut
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | Control valve |  |  | RTD | MIEPL
da94085bd25e | Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | ZIL/SUG./SULPHER/PANEL | Temperature Indicator |  |  | Temperature Indicator | Masibus/LC5296
da94085bd25e | Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | ZIL/SUG./SULPHER/PANEL | Temperature Indicator |  |  | Thermocouple | K-type
c2b506d4463f | Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | ZIL/SUG./FILM/PANEL | Temperature Indicator |  |  | Temperature Indicator | Masibus/LC5296
c2b506d4463f | Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | ZIL/SUG./FILM/PANEL | Temperature Indicator |  |  | Thermocouple | K-type
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | DS Centrifugal Machine Drive |  |  | Make | Power Automation
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | DS Centrifugal Machine Drive |  |  | Year of Installation | 2000
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | DS Centrifugal Machine Drive |  |  | PLC Make | Delta
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | DS Centrifugal Machine Drive |  |  | Capacity | 1000Kg/Hr
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | DS Centrifugal Machine Drive |  |  | Relay Card | Speed Proxy
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Manufacturer – | ENDRESS+HAUSER
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Serial No. | H3021E20000
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Working Temperature | 120 DEEGRI
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Model | PROMAG P
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Range | 0-500 M3/hr
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | working pressure | 10 KG/CM2
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Nominal Dia ( MM) | 250 MM
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Calibration Range | 0-500 M3/hr
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Material Body | Sensor Material
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Liner | PTFE
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Output | 4 -20mA
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Display Version | Power Supply
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | 220VAC | Comunication
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Display unit | 2 line LCD
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Cable length | 5 Mtr.
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | Flow Meter |  |  | Protection | Earthing
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Manufacturer – | ENDRESS+HAUSER
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Serial No. | H3021 B2 0000
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Working Temperature | 120 DEEGRI
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Model | PROMAG P
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Range | 0-300 M3/hr
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | working pressure | 10 KG/CM2
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Nominal Dia ( MM) | 150 MM
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Calibration Range | 0-300 M3/hr
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Material Body | Sensor Material
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Liner | PTFE
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Output | 4 -20mA
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Display Version | Power Supply
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | 220VAC | Comunication
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Display unit | 2 line LCD
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Cable length | 5 Mtr.
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | Flow Meter |  |  | Protection | Earthing
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Manufacturer – | ENDRESS+HAUSER
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Serial No. | H3021 - D2 0000
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Working Temperature | 120 DEEGRI
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Model | PROMAG P
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Range | 0-150 M3/hr
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | working pressure | 10 KG/CM2
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Nominal Dia ( MM) | 150 MM
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Calibration Range | 0-150 M3/hr
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Material Body | Sensor Material
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Liner | PTFE
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Output | 4 -20mA
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Display Version | Power Supply
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | 220VAC | Comunication
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Display unit | 2 line LCD
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Cable length | 5 Mtr.
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | Flow Meter |  |  | Protection | Earthing
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Manufacturer – | ENDRESS+HAUSER
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Serial No. | H3021 - F2 0000
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Working Temperature | 120 DEEGRI
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Model | PROMAG P
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Range | 0-150 M3/hr
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | working pressure | 10 KG/CM2
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Nominal Dia ( MM) | 150MM
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Calibration Range | 0-150 M3/hr
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Material Body | Sensor Material
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Liner | PTFE
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Output | 4 -20mA
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Display Version | Power Supply
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | 220VAC | Comunication
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Display unit | 2 line LCD
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Cable length | 5 Mtr.
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | Flow Meter |  |  | Protection | Earthing
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Manufacturer – | Forbasmarsal
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Serial No. | 699
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Working Temperature | 120 DEEGRI
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Model | K300DN40HC
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Range | 0.1-15 M3/hr
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | working pressure | 10 KG/CM2
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Nominal Dia ( MM) | 40 MM
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Calibration Range | 0.1-15 M3/hr
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Material Body | Sensor Material
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Liner | PTFE
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Output | 4 -20mA
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Display Version | Power Supply
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | 220VAC | Comunication
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Display unit | 2 line LCD
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Cable length | 5 Mtr.
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | Flow Meter |  |  | Protection | Earthing
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Manufacturer – | Adept
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Serial No. | 2115723
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Working Temperature | 120 DEEGRI
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Model | 6410
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Range | working pressure
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Nominal Dia ( MM) | 100 MM
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Calibration Range | 0-100 M3/hr
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Material Body | Sensor Material
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Liner | PTFE
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Output | 4 -20mA
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Display Version | Power Supply
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | 220VAC | Comunication
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Display unit | 2 line LCD
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Cable length | 5 Mtr.
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | Flow Meter |  |  | Protection | Earthing
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Manufacturer – | Krohne Marshal
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Serial No. | 116408102
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Working Temperature | 120 DEEGRI
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Model | IFC100
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Range | working pressure
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Nominal Dia ( MM) | 50 MM
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Calibration Range | 0-10 M3/Hr.
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Material Body | 0
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Sensor Material | Linearity
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Liner | PTFE
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Output | 4 -20mA
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Display Version | Power Supply
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | 220VAC | Comunication
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Display unit | 2 line LCD
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Cable length | 5 Mtr.
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | Flow Meter |  |  | Protection | Earthing
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Manufacturer – | Krohne Marshal
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Serial No. | 116408097
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Working Temperature | 120 DEEGRI
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Model | IFC100
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Range | working pressure
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Nominal Dia ( MM) | 50 MM
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Calibration Range | 0-10 M3/Hr.
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Material Body | Sensor Material
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Liner | PTFE
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Output | 4 -20mA
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Display Version | Power Supply
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | 220VAC | Comunication
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Display unit | 2 line LCD
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Cable length | 5 Mtr.
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | Flow Meter |  |  | Protection | Earthing
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Manufacturer – | Adept
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Serial No. | 1904972
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Working Temperature | 120 DEEGRI
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Model | 6410
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Range | working pressure
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Nominal Dia ( MM) | 150 MM
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Calibration Range | 0-150 M3/Hr.
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Material Body | Sensor Material
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Liner | PTFE
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Output | 4 -20mA
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Display Version | Power Supply
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | 220VAC | Comunication
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Display unit | 2 line LCD
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Cable length | 5 Mtr.
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | Flow Meter |  |  | Protection | Earthing
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Manufacturer – | Adept
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Serial No. | 1904970
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Working Temperature | 120 DEEGRI
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Model | 6410
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Range | working pressure
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Nominal Dia ( MM) | 100 MM
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Calibration Range | 0-100 M3/Hr.
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Material Body | Sensor Material
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Liner | PTFE
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Output | 4 -20mA
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Display Version | Power Supply
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | 220VAC | Comunication
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Display unit | 2 line LCD
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Cable length | 5 Mtr.
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | Flow Meter |  |  | Protection | Earthing
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Manufacturer – | Adept
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Serial No. | 2107292
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Working Temperature | 120 DEEGRI
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Model | 6410
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Range | working pressure
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Nominal Dia ( MM) | 50MM
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Calibration Range | 0-10 M3/Hr.
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Material Body | Sensor Material
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Liner | PTFE
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Output | 4 -20mA
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Display Version | Power Supply
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | 220VAC | Comunication
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Display unit | 2 line LCD
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Cable length | 5 Mtr.
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | Flow Meter |  |  | Protection | Earthing
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Manufacturer – | Adept
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Serial No. | 1904068
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Working Temperature | 120 DEEGRI
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Model | 6410
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Range | working pressure
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Nominal Dia ( MM) | 100 MM
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Calibration Range | 0-100 M3/Hr.
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Material Body | Sensor Material
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Liner | PTFE
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Output | 4 -20mA
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Display Version | Power Supply
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | 220VAC | Comunication
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Display unit | 2 line LCD
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Cable length | 5 Mtr.
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | Flow Meter |  |  | Protection | Earthing
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Manufacturer – | Adept
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Serial No. | 1904969
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Working Temperature | 120 DEEGRI
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Model | 6410
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Range | working pressure
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Nominal Dia ( MM) | 100 MM
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Calibration Range | 0-100 M3/Hr.
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Material Body | Sensor Material
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Liner | PTFE
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Output | 4 -20mA
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Display Version | Power Supply
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | 220VAC | Comunication
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Display unit | 2 line LCD
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Cable length | 5 Mtr.
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | Flow Meter |  |  | Protection | Earthing
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Manufacturer – | Adept
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Serial No. | 1901588
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Working Temperature | 120 DEEGRI
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Model | 6415
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Range | working pressure
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Nominal Dia ( MM) | 150 MM
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Calibration Range | 0-150 M3/Hr.
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Material Body | Sensor Material
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Liner | PTFE
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Output | 4 -20mA
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Display Version | Power Supply
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | 220VAC | Comunication
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Display unit | 2 line LCD
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Cable length | 5 Mtr.
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | Flow Meter |  |  | Protection | Earthing
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Manufacturer – | Adept
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Serial No. | 1904964
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Working Temperature | 120 DEEGRI
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Model | 6410
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Range | working pressure
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Nominal Dia ( MM) | 50 MM
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Calibration Range | 0-30 M3/Hr.
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Material Body | Sensor Material
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Liner | PTFE
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Output | 4 -20mA
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Display Version | Power Supply
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | 220VAC | Comunication
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Display unit | 2 line LCD
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Cable length | 5 Mtr.
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | Flow Meter |  |  | Protection | Earthing
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Manufacturer – | Adept
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Serial No. | 230808171
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Working Temperature | 120 DEEGRI
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Model | Range
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | 60 M3/hr | working pressure
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Nominal Dia ( MM) | 80MM
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Calibration Range | .1-60 M3/hr
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Material Body | Sensor Material
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | ss | Linearity
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Liner | PTFE
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Output | 4 -20mA
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Display Version | Power Supply
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | 220VAC | Comunication
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Display unit | 2 line LCD
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Cable length | 5 Mtr.
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | Flow Meter |  |  | Protection | Earthing
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Manufacturer – | Adept
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Serial No. | 1904973
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Working Temperature | 120 DEEGRI
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Model | 6410
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Range | working pressure
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Nominal Dia ( MM) | 150MM
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Calibration Range | 0-150 M3/Hr.
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Material Body | Sensor Material
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Liner | PTFE
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Output | 4 -20mA
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Display Version | Power Supply
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | 220VAC | Comunication
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Display unit | 2 line LCD
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Cable length | 5 Mtr.
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | Flow Meter |  |  | Protection | Earthing
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Manufacturer – | Emerson
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Serial No. | F0005425ECAZEZZZZ
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Working Temperature | 120 DEEGRI
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Model | 13463488
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Range | working pressure
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Nominal Dia ( MM) | 100 MM
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Calibration Range | 0-60 M3/Hr.
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Material Body | Sensor Material
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Liner | Output
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | 4 -20mA | Repeatability
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Display Version | Power Supply
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | 220VAC | Comunication
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Display unit | 2 line LCD
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Cable length | 5 Mtr.
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | MASS Flow Meter |  |  | Protection | Earthing
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Manufacturer – | Adept
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Serial No. | 230808229
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Working Temperature | 120 DEEGRI
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Model | 6415
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Range | 0-30 M3/Hr.
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | working pressure | 10 KG/CM2
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Nominal Dia ( MM) | 50 MM
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Calibration Range | 0-30 M3/Hr.
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Material Body | Sensor Material
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Liner | PTFE
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Output | 4 -20mA
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Display Version | Power Supply
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | 220VAC | Comunication
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Display unit | 2 line LCD
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Cable length | 5 Mtr.
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | Flow Meter |  |  | Protection | Earthing
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Manufacturer – | Adept
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Serial No. | 230808177
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Working Temperature | 120 DEEGRI
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Model | 6415
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Range | 0-60m3
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | working pressure | 10 KG/CM2
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Nominal Dia ( MM) | 80mm
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Calibration Range | 0-60m3
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Material Body | Sensor Material
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Liner | PTFE
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Output | 4 -20mA
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Display Version | Power Supply
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | 220VAC | Comunication
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Display unit | 2 line LCD
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Cable length | 5 Mtr.
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | Flow Meter |  |  | Protection | Earthing
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Manufacturer – | Adept
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Serial No. | 231209940
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Working Temperature | 120 DEEGRI
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Model | 6415
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Range | 0-150 M3/Hr.
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | working pressure | 10 KG/CM2
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Nominal Dia ( MM) | 150mm
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Calibration Range | 0-150 M3/Hr.
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Material Body | Sensor Material
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Liner | PTFE
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Output | 4 -20mA
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Display Version | Power Supply
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | 220VAC | Comunication
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Display unit | 2 line LCD
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Cable length | 5 Mtr.
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | Flow Meter |  |  | Protection | Earthing
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Manufacturer – | Rose-mount
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Serial No. | 13870476
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Working Temperature | 120 DEEGRI
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Model | 8705TSA030C1W0
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Range | 0-30 M3/Hr.
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | working pressure | 10 KG/CM2
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Nominal Dia ( MM) | 80 MM
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Calibration Range | .1-30 M3/Hr.
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Material Body | Sensor Material
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | SS316 | Linearity
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Liner | PTFE
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Output | 4 -20mA
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Display Version | Power Supply
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | 220VAC | Comunication
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Display unit | 2 line LCD
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Cable length | 5 Mtr.
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | Flow Meter |  |  | Protection | Earthing
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Manufacturer – | Rose-mount
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Serial No. | 13870480
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Working Temperature | 120 DEEGRI
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Model | 8705TSA030C1WO
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Range | 0-30 M3/Hr.
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | working pressure | 10 KG/CM2
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Nominal Dia ( MM) | 80MM
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Calibration Range | .1-30 M3/Hr.
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Material Body | Sensor Material
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | SS316 | Linearity
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Liner | PTFE
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Output | 4 -20mA
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Display Version | Power Supply
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | 220VAC | Comunication
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Display unit | 2 line LCD
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Cable length | 5 Mtr.
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | Flow Meter |  |  | Protection | Earthing
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Manufacturer – | Rose-mount
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Serial No. | Working Temperature
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Model | 8705TSA020C1W0
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Range | 0-30 M3/Hr.
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | working pressure | 10 KG/CM2
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Nominal Dia ( MM) | 80 MM
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Calibration Range | .1-30 M3/Hr.
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Material Body | Sensor Material
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | SS316 | Linearity
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Liner | PTFE
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Output | 4 -20mA
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Display Version | Power Supply
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | 220VAC | Comunication
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Display unit | 2 line LCD
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Cable length | 5 Mtr.
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | Flow Meter |  |  | Protection | Earthing
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Manufacturer – | Rose-mount
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Serial No. | 13870478
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Working Temperature | 120 DEEGRI
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Model | 8705TSA020C1W0
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Range | 0-30 M3/Hr.
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | working pressure | 10 KG/CM2
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Nominal Dia ( MM) | 80 MM
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Calibration Range | .1-30 M3/Hr.
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Material Body | Sensor Material
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | SS316 | Linearity
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Liner | PTFE
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Output | 4 -20mA
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Display Version | Power Supply
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | 220VAC | Comunication
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Display unit | 2 line LCD
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Cable length | 5 Mtr.
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | Flow Meter |  |  | Protection | Earthing
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Manufacturer – | Rose-mount
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Serial No. | 13870474
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Working Temperature | 120 DEEGRI
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Model | 8705TSA020C1W0
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Range | 0-30 M3/Hr.
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | working pressure | 10 KG/CM2
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Nominal Dia ( MM) | 80 MM
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Calibration Range | .1-30 M3/Hr.
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Material Body | Sensor Material
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | SS316 | Linearity
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Liner | PTFE
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Output | 4 -20mA
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Display Version | Power Supply
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | 220VAC | Comunication
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Display unit | 2 line LCD
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Cable length | 5 Mtr.
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | Flow Meter |  |  | Protection | Earthing
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Make | Kilosker
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Year of Manufacturer | A18EDL000348
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Pressure Tx.-03 | MEAS
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Model | GMC1.5225
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Oil Pump | GOTECEST-75-PC-230
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Model | US681-PT0002-005BA
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Capacity | 1.5 HP
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Pressure Switch-02 | Donfose
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | SOV-03 | Rotex
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Oil Pump | GOTECEST-75-PC-230
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Model | 24101-4-2GB2
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Pressure Switch-02 | Donfose
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | SOV-01 | Rotex
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | SEDL Condenser |  |  | Model | 24101-25-8G85
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Make | SEDL
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Year of Manufacturer | 2006
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Code.No. | 140002008371
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | DI Module Make | ICP-CON
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Model | US681-PT0002-005BA
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Capacity | 19T/hr
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | DI Module Model | 7041D
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Material | SS316
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | DO Module Make | ICP-CON
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Model | US281-CT0002-001BA
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 24mm/33
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | DO Module Model | 7042D
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | SOV Make | Rotex
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 22mm/25
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | AI Module Make | ICP-CON
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Model | 30126-5-3G-B2
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 18mm/15
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | AI Module Model | 7017
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | NRV Size | 100mm
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Power Supply | 24 VDC
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Make | SEDL
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Year of Manufacturer | 2006
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Code.No. | 140010020086384
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | DI Module Make | ICP-CON
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Model | US681-PT0002-005BA
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Capacity | 28T/hr
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | DI Module Model | 7041D
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Material | SS316
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | DO Module Make | ICP-CON
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Model | US281-CT0002-001BA
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 24mm/33
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | DO Module Model | 7042D
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | SOV Make | Rotex
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 22mm/25
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | AI Module Make | ICP-CON
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Model | 30126-5-3G-B2
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 18mm/15
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | AI Module Model | 7017
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | NRV Size | 100mm
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Power Supply | 24 VDC
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Make | SEDL
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Year of Manufacturer | 2006
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Code.No. | 140002608372
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | DI Module Make | ICP-CON
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Model | US681-PT0002-005BA
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Capacity | 26T/hr
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | DI Module Model | 7041D
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Material | SS316
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | DO Module Make | ICP-CON
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Model | US281-CT0002-001BA
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 24mm/33
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | DO Module Model | 7042D
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | SOV Make | Rotex
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 22mm/25
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | AI Module Make | ICP-CON
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Model | 30126-5-3G-B2
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 18mm/15
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | AI Module Model | 7017
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | NRV Size | 100mm
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Power Supply | 24 VDC
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Make | SEDL
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Year of Manufacturer | 2006
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Code.No. | 110060200373
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | DI Module Make | ICP-CON
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Model | US681-PT0002-005BA
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Capacity | 12Ton/hr
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | DI Module Model | 7041D
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Material | SS316
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | DO Module Make | ICP-CON
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Model | US281-CT0002-001BA
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 22mm/17
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | DO Module Model | 7042D
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | SOV Make | Rotex
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 18mm/14
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | AI Module Make | ICP-CON
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Model | 30126-5-3G-B2
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 22mm/7
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | AI Module Model | 7017
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | NRV Size | 100mm
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Power Supply | 24 VDC
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Relay Type | RU2SD24 nos-06
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Make | SEDL
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Year of Manufacturer | 2006
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Code.No. | DI Module Make
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | ICP-CON | Model
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Capacity | 12Ton/hr
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | DI Module Model | 7041D
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Material | SS316
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | DO Module Make | ICP-CON
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Model | US281-CT0002-001BA
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 22mm/17
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | DO Module Model | 7042D
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | SOV Make | Rotex
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 18mm/14
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | AI Module Make | ICP-CON
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Model | 30126-5-3G-B2
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 22mm/7
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | AI Module Model | 7017
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | NRV Size | 100mm
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Power Supply | 24 VDC
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Make | SEDL
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Year of Manufacturer | 2006
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Code.No. | DI Module Make
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | ICP-CON | Model
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Capacity | 12Ton/hr
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | DI Module Model | 7041D
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Material | SS316
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | DO Module Make | ICP-CON
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Model | US281-CT0002-001BA
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 22mm/17
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | DO Module Model | 7042D
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | SOV Make | Rotex
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 18mm/14
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | AI Module Make | ICP-CON
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Model | 30126-5-3G-B2
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 22mm/7
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | AI Module Model | 7017
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | NRV Size | 100mm
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Power Supply | 24 VDC
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Make | SEDL
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Year of Manufacturer | 2006
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Code.No. | DI Module Make
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | ICP-CON | Model
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Capacity | 12Ton/hr
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | DI Module Model | 7041D
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Material | SS316
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | DO Module Make | ICP-CON
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Model | US281-CT0002-001BA
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 22mm/17
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | DO Module Model | 7042D
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | SOV Make | Rotex
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 18mm/14
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | AI Module Make | ICP-CON
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Model | 30126-5-3G-B2
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 22mm/7
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | AI Module Model | 7017
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | NRV Size | 100mm
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Power Supply | 24 VDC
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Make | SEDL
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Year of Manufacturer | 2006
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Code.No. | 1100502006374
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | DI Module Make | ICP-CON
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Model | US681-PT0002-005BA
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Capacity | 12Ton/hr
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | DI Module Model | 7041D
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Material | SS316
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | DO Module Make | ICP-CON
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Model | US281-CT0002-001BA
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 22mm/17
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | DO Module Model | 7042D
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | SOV Make | Rotex
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 18mm/14
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | AI Module Make | ICP-CON
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Model | 30126-5-3G-B2
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 22mm/7
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | AI Module Model | 7017
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | NRV Size | 100mm
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Power Supply | 24 VDC
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Make | SEDL
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Year of Manufacturer | 2006
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Code.No. | 1100802006377
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | DI Module Make | ICP-CON
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Model | US681-PT0002-005BA
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Capacity | 14Ton/hr
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | DI Module Model | 7041D
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Material | SS316
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | DO Module Make | ICP-CON
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Model | US281-CT0002-001BA
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 22mm/17
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | DO Module Model | 7042D
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | SOV Make | Rotex
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 18mm/14
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | AI Module Make | ICP-CON
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Model | 30126-5-3G-B2
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 22mm/7
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | AI Module Model | 7017
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | NRV Size | 100mm
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Power Supply | 24 VDC
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Make | SEDL
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Year of Manufacturer | 2006
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Code.No. | 1100602006379
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | DI Module Make | ICP-CON
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Model | US681-PT0002-005BA
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Capacity | 14Ton/hr
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | DI Module Model | 7041D
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Material | SS316
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | DO Module Make | ICP-CON
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Model | US281-CT0002-001BA
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 24mm/17
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | DO Module Model | 7042D
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | SOV Make | Rotex
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 22mm/14
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | AI Module Make | ICP-CON
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Model | 30126-5-3G-B2
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 26mm/7
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | AI Module Model | 7017
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | NRV Size | 100mm
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Power Supply | 24 VDC
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Make | SEDL
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Year of Manufacturer | 2006
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Code.No. | 1300802006380
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | DI Module Make | ICP-CON
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Model | US681-PT0002-005BA
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Capacity | 18Ton/hr
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | DI Module Model | 7041D
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Material | SS316
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | DO Module Make | ICP-CON
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Model | US281-CT0002-001BA
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 24mm/21
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | DO Module Model | 7042D
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | SOV Make | Rotex
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 26mm/16
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | AI Module Make | ICP-CON
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Model | 30126-5-3G-B2
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 18mm/16
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | AI Module Model | 7017
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | NRV Size | 100mm
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Power Supply | 24 VDC
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Make | SEDL
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Year of Manufacturer | 2006
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Code.No. | DI Module Make
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | ICP-CON | Model
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Capacity | 22Ton/hr
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | DI Module Model | 7041D
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Material | SS316
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | DO Module Make | ICP-CON
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Model | US281-CT0002-001BA
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 24mm/33
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | DO Module Model | 7042D
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | SOV Make | Rotex
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 26mm/25
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | AI Module Make | ICP-CON
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Model | 30126-5-3G-B2
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 26mm/15
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | AI Module Model | 7017
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | NRV Size | 100mm
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Power Supply | 24 VDC
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Make | SEDL
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Year of Manufacturer | 2006
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Code.No. | DI Module Make
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | ICP-CON | Model
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Capacity | 22Ton/hr
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | DI Module Model | 7041D
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Material | SS316
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | DO Module Make | ICP-CON
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Model | US281-CT0002-001BA
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 24mm/33
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | DO Module Model | 7042D
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | SOV Make | Rotex
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 26mm/25
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | AI Module Make | ICP-CON
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Model | 30126-5-3G-B2
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 26mm/15
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | AI Module Model | 7017
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | NRV Size | 100mm
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Power Supply | 24 VDC
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Make | SEDL
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Year of Manufacturer | 2006
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Pressure Tx. Make | MEAS
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Code.No. | 1300C0NT2006383
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | DI Module Make | ICP-CON
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Model | US681-PT0002-005BA
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Capacity | 18Ton/hr
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | DI Module Model | 7041D
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Vaccum Tx. Make | MEAS
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Material | SS316
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | DO Module Make | ICP-CON
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Model | US281-CT0002-001BA
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Jet Nozzle Size/Nos. | 24mm/21
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | DO Module Model | 7042D
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | SOV Make | Rotex
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Do Nozzle Size/Nos. | 26mm/16
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | AI Module Make | ICP-CON
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Model | 30126-5-3G-B2
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | DC Nozzle Size/Nos. | 26mm/16
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | AI Module Model | 7017
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Temp. Tx. Make | SEDL
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | NRV Size | 100mm
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Power Supply | 24 VDC
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Relay Type/Model | DPDT/RU2SD24 nos-06
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | SEDL Condenser |  |  | Water Pressure | 1.2 TO 1.5 KG/CM2
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Make | Hi-tech
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Sr.No. | 529
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | PLC Make | Omran
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Model | HT-009
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Year of Manufacture | 2016
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Model | ZEN-10C1DR-D-V2
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Capacity | 300 Bag/Hr
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Class | Third
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | SOV Make | JANATICS
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Material-Body | SS
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Filling Type | Gravity
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Model | DS255SR61-A
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Controller-1 | B840208
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Loadcell - | 1x3
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Proxy Make | JAYSHREE
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Make | Unipulse
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Make | Sensortronics
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Model | SW4051
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Model | HT-900
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Model | 65023-110K-NC-02X
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | AFR Make-JANATICS | FRC-136134
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | DS Bagging Machine |  |  | Level Switch | SBM
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Make | Hi-tech
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Sr.No. | 731
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | PLC Make | Omran
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Model | HT-900
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Year of Manufacture | 2016
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Model | ZEN-10C1DR-D-V2
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Capacity | 300 Bag/Hr
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Class | Third
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | SOV Make | JANATICS
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Material-Body | SS
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Filling Type | Gravity
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Model | DS255SR61-A
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Controller-1 | B840208
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Loadcell - | 1x3
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Proxy Make | JAYSHREE
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Make | Unipulse
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Make | Sensortronics
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Model | SW4051
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Model | HT-900
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | Model | 65023-110K-NC-02X
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | DS Bagging Machine |  |  | AFR Make | JANATICS -FRC-136134
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Make | Hi-tech
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Sr.No. | 410
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | PLC Make | Omran
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Model | PANTHER-C750
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Year of Manufacture | 2016
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Model | ZEN-10C1DR-D-V2
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Capacity | 300 Bag/Hr
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Class | Third
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | SOV Make | JANATICS
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Material-Body | SS
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Filling Type | Gravity
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Model | DS255SR61-A
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Controller Sr. no. | Loadcell -
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | 1x3 | Proxy Make
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Make | Metlar Toledo
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Make | Sensortronics
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Model | SW4051
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Model | C750
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Model | 65023-110K-NC-02X
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | AFR Make | JANATICS -FRC-136134
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | DS Bagging Machine |  |  | Level switch | SBM
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Make | Hi-tech
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Sr.No. | 528
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | PLC Make | Omran
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Model | HT-009
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Year of Manufacture | 2016
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Model | ZEN-10C1DR-D-V2
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Capacity | 300 Bag/Hr
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Class | Third
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | SOV Make | JANATICS
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Material-Body | SS
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Filling Type | Gravity
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Model | DS255SR61-A
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Controller-1 | B840208
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Loadcell - | 1x3
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Proxy Make | JAYSHREE
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Make | Unipulse
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Make | Sensortronics
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Model | SW4051
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Model | HT-900
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Model | 65023-110K-NC-02X
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | AFR Make | JANATICS -FRC-136134
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | Level switch | SBM
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | DS Bagging Machine |  |  | AFR Make | JANATICS -FRC-136134
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Make | Pneucon
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Sr. No. | 1602 41923
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Type | Rotary single acting
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Model | 232/SA -100+M
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Year of Mfg. | 2014
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Tubing | SS-304
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Size | 100 MM
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Cv | 175
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Hand wheel | YES
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Characteristic | THROTTLING
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Positioner | Seimens
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Seat Replacement type | PTFE
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Type of Valve | Butterfly valve
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Model | Sipart PS2
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Seat Leakage Class | VI
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Air to fail | Valve Close
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Sr. No. | N1H1057494308
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Travel | 90ᵒ
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Supply Pressure | 4 KSC
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | AFR | Savo
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | P Shut | 1 KSC
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Model | SB-10
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Drain Header Pr. Trans. | Yokogawa/EJA530E-JAS40N-012EL
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Liqour Feed I/L Flow Meter | Rosemount/8732EMT1A1M4
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Feed Tank Level Tx. | Yokogawa/EJA210E-JMS5J-912EN-WA13A1S
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Untreated Liqour Buffer Tank Level Tx. | Yokogawa/EJA210E-JMS5J-912EN-WA13A1S
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | Control valve |  |  | Backwash tank Temp. Tx. | Yokogawa/YTA 110 - EA2DB
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Make | Pneucon
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Sr. No. | 1602 41915
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Type | Rotary single acting
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Model | 232/SA -100+M
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Year of Mfg. | 2014
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Tubing | SS-304
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Size | 100 MM
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Cv | 175
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Hand wheel | YES
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Material Disc/Body | SS-316 / A216GR WCB
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Characteristic | On-off
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Positioner | Pneucon
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Seat Replacement type | PTFE
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Type of Valve | Butterfly valve
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Model | LSWP
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Seat Leakage Class | VI
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Air to fail | Valve Close
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Travel | 90ᵒ
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Supply Pressure | 4 KSC
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | AFR | Savo
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | P Shut | 1 KSC
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | Control valve- |  |  | Model | SB-10
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Make | Pneucon
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Sr. No. | 1602 41914
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Type | Rotary single acting
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Model | 232/SA -100+M
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Year of Mfg. | 2014
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Tubing | SS-304
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Size | 100 MM
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Cv | 175
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Hand wheel | YES
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Characteristic | On-off
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Positioner | Pneucon
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Seat Replacement type | PTFE
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Type of Valve | Butterfly valve
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Model | LSWP
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Seat Leakage Class | VI
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Air to fail | Valve Close
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Travel | 90ᵒ
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Supply Pressure | 4 KSC
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | AFR | Savo
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | P Shut | 1 KSC
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | Control valve |  |  | Model | SB-10
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Make | Pneucon
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Sr. No. | 1602 41917
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Type | Rotary single acting
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Model | 232/SA -100+M
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Year of Mfg. | 2014
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Tubing | SS-304
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Size | 100 MM
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Cv | 175
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Hand wheel | YES
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Characteristic | On-off
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Positioner | Pneucon
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Seat Replacement type | PTFE
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Type of Valve | Butterfly valve
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Model | LSWP
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Seat Leakage Class | VI
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Air to fail | Valve Close
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Travel | 90ᵒ
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Supply Pressure | 4 KSC
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | AFR | Savo
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | P Shut | 1 KSC
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | Control valve |  |  | Model | SB-10
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Make | Pneucon
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Sr. No. | 1602 41918
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Type | Rotary single acting
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Model | 232/SA -100+M
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Year of Mfg. | 2014
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Tubing | SS-304
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Size | 100 MM
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Cv | 175
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Hand wheel | YES
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Characteristic | On-off
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Positioner | Pneucon
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Seat Replacement type | PTFE
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Type of Valve | Butterfly valve
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Model | LSWP
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Seat Leakage Class | VI
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Air to fail | Valve Close
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Travel | 90ᵒ
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Supply Pressure | 4 KSC
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | AFR | Savo
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | P Shut | 1 KSC
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | Control valve |  |  | Model | SB-10
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Make | Pneucon
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Sr. No. | 1602 41919
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Type | Rotary single acting
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Model | 232/SA 75+M
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Year of Mfg. | 2014
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Tubing | SS-304
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Size | 50 MM
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Cv | 100
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Hand wheel | YES
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Characteristic | On-off
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Positioner | Pneucon
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Seat Replacement type | PTFE
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Type of Valve | Butterfly valve
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Model | LSWP
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Seat Leakage Class | VI
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Air to fail | Valve Close
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Travel | 90ᵒ
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Supply Pressure | 4 KSC
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | AFR | Savo
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | P Shut | 1 KSC
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | Control valve |  |  | Model | SB-10
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Make | Pneucon
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Sr. No. | 1602 41920
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Type | Rotary single acting
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Model | 232/SA -100+M
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Year of Mfg. | 2014
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Tubing | SS-304
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Size | 100 MM
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Cv | 175
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Hand wheel | YES
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Characteristic | On-off
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Positioner | Pneucon
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Seat Replacement type | PTFE
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Type of Valve | Butterfly valve
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Model | LSWP
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Seat Leakage Class | VI
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Air to fail | Valve Close
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Travel | 90ᵒ
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Supply Pressure | 4 KSC
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | AFR | Savo
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | P Shut | 1 KSC
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Control valve |  |  | Model | SB-10
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Make | Pneucon
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Sr. No. | 1602 41922
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Type | Rotary single acting
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Model | 232/SA -100+M
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Year of Mfg. | 2014
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Tubing | SS-304
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Size | 100 MM
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Cv | 175
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Hand wheel | YES
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Characteristic | On-Off
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Positioner | Pneucon
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Seat Replacement type | PTFE
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Type of Valve | Butterfly valve
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Model | LSWP
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Seat Leakage Class | VI
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Air to fail | Valve Close
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Travel | 90ᵒ
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Supply Pressure | 4 KSC
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | AFR | Savo
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | P Shut | 1 KSC
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | Control valve |  |  | Model | SB-10
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Make | Pneucon
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Sr. No. | 1602 41921
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Type | Rotary single acting
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Model | 232/SA -100+M
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Year of Mfg. | 2014
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Tubing | SS-304
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Size | 100 MM
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Cv | 175
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Hand wheel | YES
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Characteristic | On-Off
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Positioner | Pneucon
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Seat Replacement type | PTFE
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Type of Valve | Butterfly valve
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Model | LSWP
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Seat Leakage Class | VI
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Air to fail | Valve Close
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Travel | 90ᵒ
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Supply Pressure | 4 KSC
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | AFR | Savo
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | P Shut | 1 KSC
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | Control valve |  |  | Model | SB-10
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Make | Pneucon
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Sr. No. | 1602 41924
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Type | Rotary single acting
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Model | 232/SA -100+M
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Year of Mfg. | 2014
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Tubing | SS-304
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Size | 100 MM
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Cv | 175
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Hand wheel | YES
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Characteristic | On-Off
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Positioner | Pneucon
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Seat Replacement type | PTFE
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Type of Valve | Butterfly valve
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Model | LSWP
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Seat Leakage Class | VI
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Air to fail | Valve Close
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Travel | 90ᵒ
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Supply Pressure | 4 KSC
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | AFR | Savo
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | P Shut | 1 KSC
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | Control valve |  |  | Model | SB-10
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Make | Pneucon
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Sr. No. | 1602 41927
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Type | Rotary single acting
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Model | 232/SA -100+M
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Year of Mfg. | 2014
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Tubing | SS-304
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Size | 100 MM
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Cv | 175
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Hand wheel | YES
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Characteristic | On-Off
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Positioner | Pneucon
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Seat Replacement type | PTFE
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Type of Valve | Butterfly valve
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Model | LSWP
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Seat Leakage Class | VI
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Air to fail | Valve Close
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Travel | 90ᵒ
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Supply Pressure | 4 KSC
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | AFR | Savo
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | P Shut | 1 KSC
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | Control valve |  |  | Model | SB-10
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Make | Pneucon
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Sr. No. | 1602 41926
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Type | Rotary single acting
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Model | 232/SA 75+M
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Year of Mfg. | 2014
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Tubing | SS-304
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Size | 50 MM
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Cv | 100
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Hand wheel | YES
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Characteristic | On-Off
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Positioner | Pneucon
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Seat Replacement type | PTFE
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Type of Valve | Butterfly valve
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Model | LSWP
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Seat Leakage Class | VI
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Air to fail | Valve Close
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Travel | 90ᵒ
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Supply Pressure | 4 KSC
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | AFR | Savo
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | P Shut | 1 KSC
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | Control valve |  |  | Model | SB-10
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Make | Pneucon
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Sr. No. | 1602 41925
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Type | Rotary single acting
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Model | 232/SA -100+M
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Year of Mfg. | 2014
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Tubing | SS-304
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Size | 100 MM
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Cv | 175
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Hand wheel | YES
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Characteristic | On-Off
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Positioner | Pneucon
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Seat Replacement type | PTFE
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Type of Valve | Butterfly valve
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Model | LSWP
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Seat Leakage Class | VI
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Air to fail | Valve Close
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Travel | 90ᵒ
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Supply Pressure | 4 KSC
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | AFR | Savo
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | P Shut | 1 KSC
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | Control valve |  |  | Model | SB-10
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Make | Pneucon
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Sr. No. | 1602 41913
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Type | Rotary single acting
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Model | 232/SA -125+M
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Year of Mfg. | 2014
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Tubing | SS-304
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Size | 150 MM
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Cv | 650
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Hand wheel | YES
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Characteristic | Throttling
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Positioner | Siemens
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Seat Replacement type | PTFE
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Type of Valve | Butterfly valve
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Model | Sipart PS2
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Seat Leakage Class | VI
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Air to fail | Valve Close
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Sr. No. | N1F9097475717
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Travel | 90ᵒ
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Supply Pressure | 4 KSC
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | AFR | Savo
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | P Shut | 1 KSC
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Model | SB-10
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | Control valve |  |  | Backwash flow meter | Rosemount/8732EMT1A1M4
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Make | Pneucon
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Sr.No. | 1602 41946
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Type | Rotary single acting
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Model | 232 SA 100 M
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Year of Mfg. | 2014
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Tubing | SS-304
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Size | 100 MM
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Cv | 275
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Hand wheel | YES
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Characteristic | THROTTLING
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Positioner | Seimens
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Seat Replacement type | PTFE
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Type of Valve | Butterfly valve
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Model | Sipart PS2
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Seat Leakage Class | VI
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Air to fail | Valve Close
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Sr.No. | N1H1057494239
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Travel | 90ᵒ
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Supply Pressure | 4 KSC
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | AFR | Savo
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | P Shut | 1 KSC
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Model | SB-10
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | IER-1 Lower Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | IER-1 Level Switch | AUTOMAT/2600-A-2-E-40C-0.1-3-W
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Pressure gauge | General
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | IER-1 Middle Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Melt I/L Flow Meter | Rosemount/8732EMT1A1M4
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | Caustic Soda Tank LT | Yokogawa/EJA210E-JMS5J
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | IER-1 Upper Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | IER Feed Tank Level Tx. | Yokogawa/EJA210E-JMS5J-912EN-WA13A1S
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | Control valve |  |  | HCL Tank Level Tx. | Yokogawa/EJA210E-JMS5J
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Make | Pneucon
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Sr.No. | 1602 41951
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Type | Rotary single acting
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Model | 232 SA 100 M
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Year of Mfg. | 2014
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Tubing | SS-304
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Size | 100 MM
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Cv | 275
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Hand wheel | YES
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Characteristic | On- Off
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Positioner | Pneucon
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Seat Replacement type | PTFE
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Type of Valve | Butterfly valve
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Model | LSWP
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Seat Leakage Class | VI
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Air to fail | Valve Close
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Travel | 90ᵒ
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Supply Pressure | 4 KSC
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | AFR | Savo
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | P Shut | 1 KSC
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | Control valve |  |  | Model | SB-10
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Make | Pneucon
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Sr.No. | 1602 41948
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Type | Rotary single acting
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Model | 232 SA 85 M
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Year of Mfg. | 2014
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Tubing | SS-304
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Size | 80 MM
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Cv | 170
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Hand wheel | YES
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Characteristic | On- Off
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Positioner | Pneucon
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Seat Replacement type | PTFE
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Type of Valve | Butterfly valve
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Model | LSWP
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Seat Leakage Class | VI
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Air to fail | Valve Close
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Travel | 90ᵒ
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Supply Pressure | 4 KSC
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | AFR | Savo
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | P Shut | 1 KSC
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Control valve |  |  | Model | SB-10
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Make | Pneucon
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Sr.No. | 1602 41949
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Type | Rotary single acting
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Model | 232 SA 100 M
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Year of Mfg. | 2014
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Tubing | SS-304
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Size | 100 MM
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Cv | 275
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Hand wheel | YES
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Characteristic | On- Off
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Positioner | Pneucon
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Seat Replacement type | PTFE
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Type of Valve | Butterfly valve
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Model | LSWP
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Seat Leakage Class | VI
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Air to fail | Valve Close
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Travel | 90ᵒ
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Supply Pressure | 4 KSC
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | AFR | Savo
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | P Shut | 1 KSC
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | Control valve |  |  | Model | SB-10
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Make | Pneucon
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Sr.No. | 1602 41950
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Type | Rotary single acting
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Model | 232 SA 100 M
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Year of Mfg. | 2014
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Tubing | SS-304
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Size | 100 MM
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Cv | 275
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Hand wheel | YES
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Characteristic | On- Off
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Positioner | Pneucon
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Seat Replacement type | PTFE
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Type of Valve | Butterfly valve
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Model | LSWP
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Seat Leakage Class | VI
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Air to fail | Valve Close
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Travel | 90ᵒ
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Supply Pressure | 4 KSC
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | AFR | Savo
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | P Shut | 1 KSC
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | Control valve |  |  | Model | SB-10
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Make | Pneucon
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Sr.No. | 13129
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Type | Rotary single acting
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Model | 232 SA 100 M
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Year of Mfg. | 2014
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Tubing | SS-304
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Size | 100 MM
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Cv | 275
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Hand wheel | YES
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Characteristic | On- Off
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Positioner | Pneucon
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Seat Replacement type | PTFE
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Type of Valve | Butterfly valve
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Model | LSWP
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Seat Leakage Class | VI
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Air to fail | Valve Close
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Travel | 90ᵒ
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Supply Pressure | 4 KSC
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | AFR | Savo
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | P Shut | 1 KSC
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | Control valve |  |  | Model | SB-10
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Make | Pneucon
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Sr.No. | 41988
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Type | Rotary single acting
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Model | 232 SA 085+M
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Year of Mfg. | 2014
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Tubing | SS-304
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Size | 80 MM
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Cv | 170
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Hand wheel | YES
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Characteristic | On- Off
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Positioner | Pneucon
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Seat Replacement type | PTFE
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Type of Valve | Butterfly valve
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Model | LSWP
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Seat Leakage Class | VI
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Air to fail | Valve Close
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Travel | 90ᵒ
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Supply Pressure | 4 KSC
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | AFR | Savo
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | P Shut | 1 KSC
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | Control valve |  |  | Model | SB-10
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Make | Pneucon
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Sr.No. | 1602 41953
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Type | Rotary single acting
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Model | 232 SA 100+M
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Year of Mfg. | 2014
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Tubing | SS-304
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Size | 100 MM
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Cv | 275
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Hand wheel | YES
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Characteristic | On- Off
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Positioner | Pneucon
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Seat Replacement type | PTFE
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Type of Valve | Butterfly valve
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Model | LSWP
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Seat Leakage Class | VI
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Air to fail | Valve Close
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Travel | 90ᵒ
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Supply Pressure | 4 KSC
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | AFR | Savo
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | P Shut | 1 KSC
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | Control valve |  |  | Model | SB-10
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Make | Pneucon
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Sr.No. | 1602 41954
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Type | Rotary single acting
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Model | 232/SA075 M
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Year of Mfg. | 2014
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Tubing | SS-304
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Size | 50 MM
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Cv | 68
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Hand wheel | YES
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Characteristic | On- Off
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Positioner | Pneucon
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Seat Replacement type | PTFE
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Type of Valve | Butterfly valve
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Model | LSWP
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Seat Leakage Class | VI
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Air to fail | Valve Close
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Travel | 90ᵒ
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Supply Pressure | 4 KSC
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | AFR | Savo
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | P Shut | 1 KSC
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Control valve |  |  | Model | SB-10
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Make | Pneucon
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Sr.No. | 1602 41955
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Type | Rotary single acting
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Model | 232 SA 100 M
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Year of Mfg. | 2014
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Tubing | SS-304
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Size | 100 MM
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Cv | 275
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Hand wheel | YES
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Characteristic | On- Off
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Positioner | Pneucon
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Seat Replacement type | PTFE
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Type of Valve | Butterfly valve
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Model | LSWP
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Seat Leakage Class | VI
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Air to fail | Valve Close
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Travel | 90ᵒ
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Supply Pressure | 4 KSC
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | AFR | Savo
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | P Shut | 1 KSC
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | Control valve |  |  | Model | SB-10
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Make | Pneucon
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Sr.No. | 1602 41956
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Type | Rotary single acting
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Model | 232 SA 100 M
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Year of Mfg. | 2014
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Tubing | SS-304
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Size | 100 MM
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Cv | 275
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Hand wheel | YES
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Characteristic | On- Off
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Positioner | Pneucon
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Seat Replacement type | PTFE
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Type of Valve | Butterfly valve
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Model | LSWP
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Seat Leakage Class | VI
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Air to fail | Valve Close
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Travel | 90ᵒ
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Supply Pressure | 4 KSC
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | AFR | Savo
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | P Shut | 1 KSC
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | Control valve |  |  | Model | SB-10
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Make | Pneucon
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Sr.No. | 1602 41957
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Type | Rotary single acting
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Model | 232 SA 100 M
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Year of Mfg. | 2014
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Tubing | SS-304
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Size | 100 MM
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Cv | 275
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Hand wheel | YES
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Characteristic | On- Off
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Positioner | Pneucon
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Seat Replacement type | PTFE
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Type of Valve | Butterfly valve
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Model | LSWP
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Seat Leakage Class | VI
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Air to fail | Valve Close
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Travel | 90ᵒ
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Supply Pressure | 4 KSC
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | AFR | Savo
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | P Shut | 1 KSC
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | Control valve |  |  | Model | SB-10
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Make | Pneucon
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Sr.No. | 1602 41958
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Type | Rotary single acting
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Model | 232 SA 100 M
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Year of Mfg. | 2014
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Tubing | SS-304
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Size | 100 MM
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Cv | 275
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Hand wheel | YES
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Characteristic | On- Off
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Positioner | Pneucon
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Seat Replacement type | PTFE
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Type of Valve | Butterfly valve
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Model | LSWP
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Seat Leakage Class | VI
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Air to fail | Valve Close
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Travel | 90ᵒ
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Supply Pressure | 4 KSC
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | AFR | Savo
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | P Shut | 1 KSC
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | Control valve |  |  | Model | SB-10
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Make | Pneucon
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Sr.No. | 1602 41959
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Type | Rotary single acting
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Model | 232 SA 100 M
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Year of Mfg. | 2014
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Tubing | SS-304
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Size | 100 MM
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Cv | 275
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Hand wheel | YES
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Characteristic | THROTTLING
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Positioner | Seimens
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Seat Replacement type | PTFE
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Type of Valve | Butterfly valve
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Model | Sipart PS2
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Seat Leakage Class | VI
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Air to fail | Valve Close
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Sr.No. | N1H1057494239
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Travel | 90ᵒ
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Supply Pressure | 4 KSC
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | AFR | Savo
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | P Shut | 1 KSC
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Model | SB-10
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | IER-2 Lower Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | IER-1 Level Switch | AUTOMAT/2600-A-2-E-40C-0.1-3-W
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Pressure gauge | General
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | IER-2 Middle Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | Melt I/L Flow Meter | Rosemount/8732EMT1A1M4
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Control valve |  |  | IER-2 Upper Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Make | Pneucon
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Sr.No. | 1602 41960
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Type | Rotary single acting
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Model | 232 SA 100 M
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Year of Mfg. | 2014
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Tubing | SS-304
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Size | 100 MM
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Cv | 275
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Hand wheel | YES
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Characteristic | On- Off
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Positioner | Pneucon
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Seat Replacement type | PTFE
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Type of Valve | Butterfly valve
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Model | LSWP
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Seat Leakage Class | VI
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Air to fail | Valve Close
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Travel | 90ᵒ
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Supply Pressure | 4 KSC
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | AFR | Savo
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | P Shut | 1 KSC
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Control valve |  |  | Model | SB-10
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Make | Pneucon
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Sr.No. | 1602 41961
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Type | Rotary single acting
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Model | 232 SA 85 M
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Year of Mfg. | 2014
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Tubing | SS-304
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Size | 80 MM
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Cv | 170
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Hand wheel | YES
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Characteristic | On- Off
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Positioner | Pneucon
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Seat Replacement type | PTFE
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Type of Valve | Butterfly valve
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Model | LSWP
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Seat Leakage Class | VI
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Air to fail | Valve Close
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Travel | 90ᵒ
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Supply Pressure | 4 KSC
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | AFR | Savo
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | P Shut | 1 KSC
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | Control valve |  |  | Model | SB-10
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Make | Pneucon
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Sr.No. | 1602 41962
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Type | Rotary single acting
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Model | 232 SA 100 M
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Year of Mfg. | 2014
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Tubing | SS-304
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Size | 100 MM
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Cv | 275
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Hand wheel | YES
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Characteristic | On- Off
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Positioner | Pneucon
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Seat Replacement type | PTFE
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Type of Valve | Butterfly valve
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Model | LSWP
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Seat Leakage Class | VI
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Air to fail | Valve Close
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Travel | 90ᵒ
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Supply Pressure | 4 KSC
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | AFR | Savo
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | P Shut | 1 KSC
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | Control valve |  |  | Model | SB-10
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Make | Pneucon
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Sr.No. | 1602 41963
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Type | Rotary single acting
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Model | 232 SA 100 M
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Year of Mfg. | 2014
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Tubing | SS-304
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Size | 100 MM
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Cv | 275
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Hand wheel | YES
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Characteristic | On- Off
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Positioner | Pneucon
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Seat Replacement type | PTFE
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Type of Valve | Butterfly valve
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Model | LSWP
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Seat Leakage Class | VI
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Air to fail | Valve Close
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Travel | 90ᵒ
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Supply Pressure | 4 KSC
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | AFR | Savo
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | P Shut | 1 KSC
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | Control valve |  |  | Model | SB-10
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Make | Pneucon
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Sr.No. | 1602 41964
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Type | Rotary single acting
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Model | 232 SA 100 M
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Year of Mfg. | 2014
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Tubing | SS-304
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Size | 100 MM
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Cv | 275
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Hand wheel | YES
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Characteristic | On- Off
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Positioner | Pneucon
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Seat Replacement type | PTFE
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Type of Valve | Butterfly valve
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Model | LSWP
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Seat Leakage Class | VI
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Air to fail | Valve Close
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Travel | 90ᵒ
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Supply Pressure | 4 KSC
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | AFR | Savo
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | P Shut | 1 KSC
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | Control valve |  |  | Model | SB-10
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Make | Pneucon
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Sr.No. | 1602 41965
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Type | Rotary single acting
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Model | 232 SA 085+M
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Year of Mfg. | 2014
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Tubing | SS-304
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Size | 80 MM
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Cv | 170
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Hand wheel | YES
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Characteristic | On- Off
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Positioner | Pneucon
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Seat Replacement type | PTFE
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Type of Valve | Butterfly valve
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Model | LSWP
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Seat Leakage Class | VI
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Air to fail | Valve Close
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Travel | 90ᵒ
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Supply Pressure | 4 KSC
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | AFR | Savo
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | P Shut | 1 KSC
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | Control valve |  |  | Model | SB-10
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Make | Pneucon
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Sr.No. | 1602 41966
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Type | Rotary single acting
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Model | 232 SA 100+M
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Year of Mfg. | 2014
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Tubing | SS-304
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Size | 100 MM
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Cv | 275
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Hand wheel | YES
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Characteristic | On- Off
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Positioner | Pneucon
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Seat Replacement type | PTFE
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Type of Valve | Butterfly valve
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Model | LSWP
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Seat Leakage Class | VI
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Air to fail | Valve Close
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Travel | 90ᵒ
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Supply Pressure | 4 KSC
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | AFR | Savo
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | P Shut | 1 KSC
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Control valve |  |  | Model | SB-10
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Make | Pneucon
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Sr.No. | 1602 41967
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Type | Rotary single acting
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Model | 232/SA075 M
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Year of Mfg. | 2014
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Tubing | SS-304
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Size | 50 MM
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Cv | 68
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Hand wheel | YES
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Characteristic | On- Off
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Positioner | Pneucon
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Seat Replacement type | PTFE
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Type of Valve | Butterfly valve
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Model | LSWP
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Seat Leakage Class | VI
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Air to fail | Valve Close
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Travel | 90ᵒ
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Supply Pressure | 4 KSC
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | AFR | Savo
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | P Shut | 1 KSC
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | Control valve |  |  | Model | SB-10
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Make | Pneucon
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Sr.No. | 1602 41968
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Type | Rotary single acting
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Model | 232 SA 100 M
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Year of Mfg. | 2014
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Tubing | SS-304
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Size | 100 MM
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Cv | 275
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Hand wheel | YES
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Characteristic | On- Off
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Positioner | Pneucon
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Seat Replacement type | PTFE
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Type of Valve | Butterfly valve
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Model | LSWP
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Seat Leakage Class | VI
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Air to fail | Valve Close
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Travel | 90ᵒ
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Supply Pressure | 4 KSC
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | AFR | Savo
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | P Shut | 1 KSC
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | Control valve |  |  | Model | SB-10
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Make | Pneucon
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Sr.No. | 1602 41969
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Type | Rotary single acting
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Model | 232 SA 100 M
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Year of Mfg. | 2014
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Tubing | SS-304
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Size | 100 MM
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Cv | 275
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Hand wheel | YES
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Characteristic | On- Off
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Positioner | Pneucon
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Seat Replacement type | PTFE
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Type of Valve | Butterfly valve
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Model | LSWP
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Seat Leakage Class | VI
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Air to fail | Valve Close
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Travel | 90ᵒ
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Supply Pressure | 4 KSC
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | AFR | Savo
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | P Shut | 1 KSC
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | Control valve |  |  | Model | SB-10
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Make | Pneucon
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Sr.No. | 1602 41970
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Type | Rotary single acting
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Model | 232 SA 100 M
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Year of Mfg. | 2014
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Tubing | SS-304
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Size | 100 MM
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Cv | 275
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Hand wheel | YES
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Characteristic | On- Off
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Positioner | Pneucon
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Seat Replacement type | PTFE
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Type of Valve | Butterfly valve
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Model | LSWP
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Seat Leakage Class | VI
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Air to fail | Valve Close
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Travel | 90ᵒ
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Supply Pressure | 4 KSC
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | AFR | Savo
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | P Shut | 1 KSC
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | Control valve |  |  | Model | SB-10
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Make | Pneucon
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Sr.No. | 1602 41971
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Type | Rotary single acting
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Model | 232 SA 100 M
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Year of Mfg. | 2014
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Tubing | SS-304
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Size | 100 MM
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Cv | 275
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Hand wheel | YES
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Characteristic | On- Off
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Positioner | Pneucon
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Seat Replacement type | PTFE
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Type of Valve | Butterfly valve
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Model | LSWP
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Seat Leakage Class | VI
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Air to fail | Valve Close
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Travel | 90ᵒ
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Supply Pressure | 4 KSC
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | AFR | Savo
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | P Shut | 1 KSC
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | Control valve |  |  | Model | SB-10
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Make | Pneucon
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Sr.No. | 1602 41972
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Type | Rotary single acting
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Model | 232 SA 100 M
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Year of Mfg. | 2014
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Tubing | SS-304
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Size | 100 MM
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Cv | 275
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Hand wheel | YES
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Characteristic | THROTTLING
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Positioner | Seimens
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Seat Replacement type | PTFE
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Type of Valve | Butterfly valve
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Model | Sipart PS2
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Seat Leakage Class | VI
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Air to fail | Valve Close
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Sr.No. | N1H1057494239
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Travel | 90ᵒ
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Supply Pressure | 4 KSC
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | AFR | Savo
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | P Shut | 1 KSC
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Model | SB-10
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | IER-2 Lower Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | IER-1 Level Switch | AUTOMAT/2600-A-2-E-40C-0.1-3-W
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Pressure gauge | General
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | IER-2 Middle Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | Melt I/L Flow Meter | Rosemount/8732EMT1A1M4
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | Control valve |  |  | IER-2 Upper Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Make | Pneucon
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Sr.No. | 1602 41973
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Type | Rotary single acting
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Model | 232 SA 100 M
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Year of Mfg. | 2014
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Tubing | SS-304
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Size | 100 MM
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Cv | 275
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Hand wheel | YES
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Characteristic | On- Off
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Positioner | Pneucon
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Seat Replacement type | PTFE
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Type of Valve | Butterfly valve
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Model | LSWP
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Seat Leakage Class | VI
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Air to fail | Valve Close
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Travel | 90ᵒ
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Supply Pressure | 4 KSC
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | AFR | Savo
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | P Shut | 1 KSC
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | Control valve |  |  | Model | SB-10
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Make | Pneucon
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Sr.No. | 1602 41974
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Type | Rotary single acting
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Model | 232 SA 85 M
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Year of Mfg. | 2014
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Tubing | SS-304
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Size | 80 MM
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Cv | 170
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Hand wheel | YES
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Characteristic | On- Off
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Positioner | Pneucon
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Seat Replacement type | PTFE
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Type of Valve | Butterfly valve
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Model | LSWP
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Seat Leakage Class | VI
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Air to fail | Valve Close
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Travel | 90ᵒ
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Supply Pressure | 4 KSC
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | AFR | Savo
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | P Shut | 1 KSC
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | Control valve |  |  | Model | SB-10
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Make | Pneucon
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Sr.No. | 1602 41975
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Type | Rotary single acting
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Model | 232 SA 100 M
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Year of Mfg. | 2014
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Tubing | SS-304
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Size | 100 MM
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Cv | 275
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Hand wheel | YES
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Characteristic | On- Off
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Positioner | Pneucon
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Seat Replacement type | PTFE
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Type of Valve | Butterfly valve
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Model | LSWP
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Seat Leakage Class | VI
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Air to fail | Valve Close
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Travel | 90ᵒ
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Supply Pressure | 4 KSC
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | AFR | Savo
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | P Shut | 1 KSC
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | Control valve |  |  | Model | SB-10
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Make | Pneucon
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Sr.No. | 1602 41976
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Type | Rotary single acting
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Model | 232 SA 100 M
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Year of Mfg. | 2014
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Tubing | SS-304
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Size | 100 MM
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Cv | 275
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Hand wheel | YES
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Characteristic | On- Off
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Positioner | Pneucon
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Seat Replacement type | PTFE
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Type of Valve | Butterfly valve
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Model | LSWP
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Seat Leakage Class | VI
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Air to fail | Valve Close
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Travel | 90ᵒ
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Supply Pressure | 4 KSC
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | AFR | Savo
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | P Shut | 1 KSC
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | Control valve |  |  | Model | SB-10
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Make | Pneucon
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Sr.No. | 1602 41977
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Type | Rotary single acting
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Model | 232 SA 100 M
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Year of Mfg. | 2014
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Tubing | SS-304
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Size | 100 MM
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Cv | 275
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Hand wheel | YES
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Characteristic | On- Off
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Positioner | Pneucon
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Seat Replacement type | PTFE
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Type of Valve | Butterfly valve
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Model | LSWP
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Seat Leakage Class | VI
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Air to fail | Valve Close
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Travel | 90ᵒ
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Supply Pressure | 4 KSC
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | AFR | Savo
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | P Shut | 1 KSC
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | Control valve |  |  | Model | SB-10
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Make | Pneucon
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Sr.No. | 1602 41989
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Type | Rotary single acting
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Model | 232 SA 085+M
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Year of Mfg. | 2014
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Tubing | SS-304
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Size | 80 MM
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Cv | 170
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Hand wheel | YES
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Characteristic | On- Off
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Positioner | Pneucon
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Seat Replacement type | PTFE
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Type of Valve | Butterfly valve
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Model | LSWP
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Seat Leakage Class | VI
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Air to fail | Valve Close
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Travel | 90ᵒ
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Supply Pressure | 4 KSC
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | AFR | Savo
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | P Shut | 1 KSC
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | Control valve |  |  | Model | SB-10
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Make | Pneucon
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Sr.No. | 1602 44989
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Type | Rotary single acting
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Model | 232 SA 100+M
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Year of Mfg. | 2014
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Tubing | SS-304
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Size | 100 MM
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Cv | 275
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Hand wheel | YES
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Characteristic | On- Off
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Positioner | Pneucon
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Seat Replacement type | PTFE
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Type of Valve | Butterfly valve
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Model | LSWP
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Seat Leakage Class | VI
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Air to fail | Valve Close
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Travel | 90ᵒ
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Supply Pressure | 4 KSC
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | AFR | Savo
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | P Shut | 1 KSC
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | Control valve |  |  | Model | SB-10
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Make | Pneucon
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Sr.No. | 1602 41980
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Type | Rotary single acting
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Model | 232/SA075 M
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Year of Mfg. | 2014
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Tubing | SS-304
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Size | 50 MM
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Cv | 68
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Hand wheel | YES
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Characteristic | On- Off
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Positioner | Pneucon
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Seat Replacement type | PTFE
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Type of Valve | Butterfly valve
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Model | LSWP
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Seat Leakage Class | VI
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Air to fail | Valve Close
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Travel | 90ᵒ
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Supply Pressure | 4 KSC
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | AFR | Savo
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | P Shut | 1 KSC
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | Control valve |  |  | Model | SB-10
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Make | Pneucon
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Sr.No. | 1602 41981
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Type | Rotary single acting
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Model | 232 SA 100 M
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Year of Mfg. | 2014
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Tubing | SS-304
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Size | 100 MM
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Cv | 275
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Hand wheel | YES
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Characteristic | On- Off
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Positioner | Pneucon
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Seat Replacement type | PTFE
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Type of Valve | Butterfly valve
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Model | LSWP
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Seat Leakage Class | VI
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Air to fail | Valve Close
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Travel | 90ᵒ
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Supply Pressure | 4 KSC
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | AFR | Savo
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | P Shut | 1 KSC
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | Control valve |  |  | Model | SB-10
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Make | Pneucon
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Sr.No. | 1602 41982
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Type | Rotary single acting
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Model | 232 SA 100 M
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Year of Mfg. | 2014
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Tubing | SS-304
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Size | 100 MM
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Cv | 275
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Hand wheel | YES
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Characteristic | On- Off
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Positioner | Pneucon
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Seat Replacement type | PTFE
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Type of Valve | Butterfly valve
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Model | LSWP
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Seat Leakage Class | VI
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Air to fail | Valve Close
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Travel | 90ᵒ
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Supply Pressure | 4 KSC
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | AFR | Savo
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | P Shut | 1 KSC
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Control valve |  |  | Model | SB-10
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Make | Pneucon
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Sr.No. | 1602 41983
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Type | Rotary single acting
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Model | 232 SA 100 M
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Year of Mfg. | 2014
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Tubing | SS-304
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Size | 100 MM
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Cv | 275
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Hand wheel | YES
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Characteristic | On- Off
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Positioner | Pneucon
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Seat Replacement type | PTFE
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Type of Valve | Butterfly valve
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Model | LSWP
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Seat Leakage Class | VI
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Air to fail | Valve Close
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Travel | 90ᵒ
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Supply Pressure | 4 KSC
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | AFR | Savo
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | P Shut | 1 KSC
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | Control valve |  |  | Model | SB-10
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Make | Pneucon
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Sr.No. | 1602 41984
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Type | Rotary single acting
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Model | 232 SA 100 M
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Year of Mfg. | 2014
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Tubing | SS-304
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Size | 100 MM
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Cv | 275
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Hand wheel | YES
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Characteristic | On- Off
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Positioner | Pneucon
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Seat Replacement type | PTFE
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Type of Valve | Butterfly valve
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Model | LSWP
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Seat Leakage Class | VI
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Air to fail | Valve Close
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Travel | 90ᵒ
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Supply Pressure | 4 KSC
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | AFR | Savo
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | P Shut | 1 KSC
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | Control valve |  |  | Model | SB-10
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Make | Pneucon
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Sr.No. | 1602 41985
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Type | Rotary single acting
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Model | 232 SA 100 M
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Year of Mfg. | 2014
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Tubing | SS-304
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Size | 100 MM
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Cv | 275
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Hand wheel | YES
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Characteristic | On- Off
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Positioner | Pneucon
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Seat Replacement type | PTFE
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Type of Valve | Butterfly valve
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Model | LSWP
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Seat Leakage Class | VI
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Air to fail | Valve Close
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Travel | 90ᵒ
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Supply Pressure | 4 KSC
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | AFR | Savo
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | P Shut | 1 KSC
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | Control valve |  |  | Model | SB-10
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Make | Pneucon
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Sr.No. | 1602 41986
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Type | Rotary single acting
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Model | 232 SA 100 M
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Year of Mfg. | 2014
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Tubing | SS-304
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Size | 100 MM
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Cv | 275
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Hand wheel | YES
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Characteristic | On- Off
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Positioner | Pneucon
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Seat Replacement type | PTFE
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Type of Valve | Butterfly valve
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Model | LSWP
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Seat Leakage Class | VI
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Air to fail | Valve Close
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Travel | 90ᵒ
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Supply Pressure | 4 KSC
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | AFR | Savo
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | P Shut | 1 KSC
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | Control valve |  |  | Model | SB-10
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Make | Pneucon
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Sr.No. | 1602 41987
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Type | Rotary single acting
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Model | 232 SA 100 M
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Year of Mfg. | 2014
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Tubing | SS-304
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Size | 100 MM
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Cv | 275
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Hand wheel | YES
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Characteristic | On- Off
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Positioner | Pneucon
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Seat Replacement type | PTFE
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Type of Valve | Butterfly valve
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Model | LSWP
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Seat Leakage Class | VI
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Air to fail | Valve Close
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Travel | 90ᵒ
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Supply Pressure | 4 KSC
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | AFR | Savo
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | P Shut | 1 KSC
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | Control valve |  |  | Model | SB-10
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Make | Pneucon
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Sr.No. | 1602 41989
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Type | Rotary single acting
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Model | 232 SA 100 M
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Year of Mfg. | 2014
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Tubing | SS-304
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Size | 100 MM
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Cv | 275
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Hand wheel | YES
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Characteristic | On- Off
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Positioner | Pneucon
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Seat Replacement type | PTFE
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Type of Valve | Butterfly valve
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Model | LSWP
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Seat Leakage Class | VI
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Air to fail | Valve Close
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Travel | 90ᵒ
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Supply Pressure | 4 KSC
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | AFR | Savo
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | P Shut | 1 KSC
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | Control valve |  |  | Model | SB-10
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Make | Pneucon
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Sr.No. | 1602 41988
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Type | Rotary single acting
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Model | 232 SA 100 M
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Year of Mfg. | 2014
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Tubing | SS-304
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Size | 100 MM
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Cv | 275
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Hand wheel | YES
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Characteristic | On- Off
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Positioner | Pneucon
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Seat Replacement type | PTFE
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Type of Valve | Butterfly valve
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Model | LSWP
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Seat Leakage Class | VI
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Air to fail | Valve Close
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Travel | 90ᵒ
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Supply Pressure | 4 KSC
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | AFR | Savo
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | P Shut | 1 KSC
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | Control valve |  |  | Model | SB-10
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Make | Pneucon
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Sr.No. | 1602 41939
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Type | Rotary single acting
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Model | 232 SA 125 M
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Year of Mfg. | 2014
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Tubing | SS-304
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Size | 150 MM
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Cv | 1100
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Hand wheel | YES
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Characteristic | On- Off
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Positioner | Seimens
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Seat Replacement type | PTFE
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Type of Valve | Butterfly valve
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Model | Sipart ps2
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Seat Leakage Class | VI
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Air to fail | Valve Close
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Sr.No. | N1F8067473080
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Travel | 90ᵒ
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Supply Pressure | 4 KSC
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | AFR | Savo
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | P Shut | 1 KSC
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Make | Pneucon
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Sr.No. | 1602 41937
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Type | Rotary single acting
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Model | 232 SA 100 M
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Year of Mfg. | 2014
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Tubing | SS-304
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Size | 100 MM
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Cv | 275
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Hand wheel | YES
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Characteristic | On- Off
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Positioner | Penucon
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Seat Replacement type | PTFE
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Type of Valve | Butterfly valve
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Model | LSWP
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Seat Leakage Class | VI
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Air to fail | Valve Close
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Travel | 90ᵒ
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Supply Pressure | 4 KSC
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | AFR | Savo
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | P Shut | 1 KSC
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | Control valve |  |  | Model | SB 10
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Make | Pneucon
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Sr.No. | 1602 41936
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Type | Rotary single acting
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Model | 232 SA 085 M
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Year of Mfg. | 2014
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Tubing | SS-304
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Size | 80 MM
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Cv | 170
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Hand wheel | YES
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Characteristic | On- Off
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Positioner | Penucon
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Seat Replacement type | PTFE
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Type of Valve | Butterfly valve
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Model | LSWP
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Seat Leakage Class | VI
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Air to fail | Valve Close
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Travel | 90ᵒ
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Supply Pressure | 4 KSC
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | AFR | Savo
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | P Shut | 1 KSC
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | Control valve |  |  | Model | SB 10
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Make | Pneucon
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Sr.No. | 1602 41938
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Type | Rotary single acting
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Model | 232 SA 125 M
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Year of Mfg. | 2014
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Tubing | SS-304
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Size | 150 MM
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Cv | 1100
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Hand wheel | YES
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Characteristic | On- Off
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Positioner | Penucon
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Seat Replacement type | PTFE
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Type of Valve | Butterfly valve
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Model | LSWP
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Seat Leakage Class | VI
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Air to fail | Valve Close
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Travel | 90ᵒ
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Supply Pressure | 4 KSC
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | AFR | Savo
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | P Shut | 1 KSC
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | Control valve |  |  | Model | SB 10
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Make | Revo
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Sr.No. | RS5025005A0000
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Type | Rotary single acting
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Model | ETY9020020A
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Year of Mfg. | 2025
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Tubing | SS-304
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Size | 100 MM
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Cv | 275
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Hand wheel | YES
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Characteristic | Throttling
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Positioner | Rotex
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Seat Replacement type | PTFE
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Type of Valve | Butterfly valve
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Model | RTX 1000
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Seat Leakage Class | VI
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Air to fail | Valve Close
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Travel | 90ᵒ
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Supply Pressure | 4 KSC
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | AFR | Savo
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | P Shut | 1 KSC
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Model | SB-10
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | IER-4 Lower Pr. Transmitter | Abb/Acc-HS26RAHE1SFSM2N1SNNN
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Melt I/L Flow Meter | Abb/Process Master 610
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Pressure gauge | General
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | IER-4 Middle Pr. Transmitter | Abb/Acc-HS26RAHE1SFSM2N1SNNN
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | Model | FET612.YO.F2.70.F2.A6.CWY.KO.MS.TC
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Control valve |  |  | IER-4 Upper Pr. Transmitter | Abb/Acc-HS26RAHE1SFSM2N1SNNN
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Make | Pneucon
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Sr.No. | 1602 41910
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Type | Rotary single acting
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Model | 232/SA 150
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Year of Mfg. | 2014
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Tubing | SS-304
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Size | 200 MM
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Cv | 2200
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Hand wheel | YES
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Characteristic | THROTTLING
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Positioner | Seimens
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Seat Replacement type | PTFE
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Type of Valve | Butterfly valve
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Model | Sipart PS2
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Seat Leakage Class | VI
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Air to fail | Valve Close
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Sr.No. | N1H1057494239
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Travel | 90ᵒ
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Supply Pressure | 4 KSC
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | AFR | Savo
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | P Shut | 1 KSC
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | Model | SB-10
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | Control valve |  |  | DCH MELT Temp trans. | Yokogawa/YTA 110 - EA2DB
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Make | Pneucon
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Sr.No. | 1602 41911
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Type | Rotary single acting
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Model | 232/SA 125+M
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Year of Mfg. | 2014
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Tubing | SS-304
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Size | 150 MM
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Cv | 1100
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Hand wheel | YES
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Characteristic | THROTTLING
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Positioner | Seimens
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Seat Replacement type | PTFE
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Type of Valve | Butterfly valve
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Model | Sipart PS2
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Seat Leakage Class | VI
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Air to fail | Valve Close
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Sr.No. | N1H1057494239
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Travel | 90ᵒ
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Supply Pressure | 4 KSC
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | AFR | Savo
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | P Shut | 1 KSC
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Model | SB-10
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | Control valve |  |  | Melt flow control valve | Rosemount/8732EMT1A1M4
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Make | Pneucon
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Sr.No. | 1511 41534
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Type | Rotary single acting
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Model | 232/SA 85+M
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Year of Mfg. | 2014
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Tubing | SS-304
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Size | 80 MM
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Cv | 170
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Hand wheel | YES
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Characteristic | THROTTLING
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Positioner | Seimens
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Seat Replacement type | PTFE
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Type of Valve | Butterfly valve
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Model | Sipart PS2
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Seat Leakage Class | VI
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Air to fail | Valve Close
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Sr.No. | N1F8067473092
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Travel | 90ᵒ
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Supply Pressure | 4 KSC
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | AFR | Savo
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | P Shut | 1 KSC
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Model | SB-10
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | R1 Molasses tank LT | EJA 118E -JMS0J-912 EB-EA13A1S
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | Level Switch | AUTOMAT
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | R1-Mol. Pump dis. Head. Temp tx. | YTA 110 - EA2DB
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | Control valve |  |  | R1 molasses O/L TO R1 Mol. Tank temp trans. | YTA 110 - EA2DB
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Make | Pneucon
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Sr.No. | 1511 41535
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Type | Rotary single acting
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Model | 232/SA 85+M
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Year of Mfg. | 2014
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Tubing | SS-304
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Size | 80 MM
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Cv | 170
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Hand wheel | YES
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Characteristic | THROTTLING
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Positioner | Seimens
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Seat Replacement type | PTFE
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Type of Valve | Butterfly valve
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Model | Sipart PS2
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Seat Leakage Class | VI
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Air to fail | Valve Close
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Sr.No. | N1F9097475721
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Travel | 90ᵒ
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Supply Pressure | 4 KSC
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | AFR | Savo
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | P Shut | 1 KSC
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Model | SB-10
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | R2 Molasses tank LT | EJA 118E -JMS0J-912 EB-EA13A1S
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | R1/R2 Molasses tank LT | EJA 118E -JMS0J-912 EB-EA13A1S
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | R2-Mol. Pump dis. Head. Temp tx. | Yokogawa/YTA 110 - EA2DB
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | R2 molasses O/L TO R1 Mol. Tank temp trans. | Yokogawa/YTA 110 - EA2DB
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | Control valve |  |  | Level Switch | AUTOMAT
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Make | Pneucon
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Sr.No. | 1602 41929
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Type | Rotary single acting
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Model | 232 SA 85+ M
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Year of Mfg. | 2014
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Tubing | SS-304
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Size | 80 MM
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Cv | 170
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Hand wheel | YES
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Characteristic | On- Off
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Positioner | Pneucon
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Seat Replacement type | PTFE
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Type of Valve | Butterfly valve
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Model | LSWP
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Seat Leakage Class | VI
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Air to fail | Valve Close
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Travel | 90ᵒ
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Supply Pressure | 4 KSC
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | AFR | Savo
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | P Shut | 1 KSC
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Model | SB-10
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Hot Water tank temp. trans. | Yokogawa/YTA 110 - EA2DB
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | Control valve |  |  | Hot Water tank level. trans. | Yokogawa/EJA210E-JMS5J-912EN-WA13A1S
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Make | Pneucon
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Sr.No. | 1602 41930
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Type | Rotary single acting
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Model | 232 SA 85+ M
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Year of Mfg. | 2014
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Tubing | SS-304
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Size | 80 MM
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Cv | 170
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Hand wheel | YES
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Characteristic | On- Off
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Positioner | Pneucon
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Seat Replacement type | PTFE
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Type of Valve | Butterfly valve
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Model | LSWP
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Seat Leakage Class | VI
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Air to fail | Valve Close
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Travel | 90ᵒ
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Supply Pressure | 4 KSC
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | AFR | Savo
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | P Shut | 1 KSC
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | Control valve |  |  | Model | SB-10
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Make | Pneucon
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Sr.No. | 1602 41931
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Type | Rotary single acting
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Model | 232 SA 85+ M
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Year of Mfg. | 2014
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Tubing | SS-304
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Size | 80 MM
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Cv | 170
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Hand wheel | YES
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Characteristic | On- Off
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Positioner | Pneucon
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Seat Replacement type | PTFE
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Type of Valve | Butterfly valve
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Model | LSWP
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Seat Leakage Class | VI
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Air to fail | Valve Close
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Travel | 90ᵒ
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Supply Pressure | 4 KSC
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | AFR | Savo
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | P Shut | 1 KSC
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | Control valve |  |  | Model | SB-10
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Make | Pneucon
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Sr.No. | 1602 41934
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Type | Rotary single acting
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Model | 232 SA 85+ M
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Year of Mfg. | 2014
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Tubing | SS-304
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Size | 80 MM
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Cv | 170
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Hand wheel | YES
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Characteristic | On- Off
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Positioner | Pneucon
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Seat Replacement type | PTFE
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Type of Valve | Butterfly valve
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Model | LSWP
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Seat Leakage Class | VI
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Air to fail | Valve Close
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Travel | 90ᵒ
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Supply Pressure | 4 KSC
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | AFR | Savo
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | P Shut | 1 KSC
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | Control valve |  |  | Model | SB-10
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Make | Pneucon
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Sr.No. | 1602 41935
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Type | Rotary single acting
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Model | 232 SA 85+ M
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Year of Mfg. | 2014
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Tubing | SS-304
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Size | 80 MM
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Cv | 170
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Hand wheel | YES
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Characteristic | On- Off
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Positioner | Pneucon
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Seat Replacement type | PTFE
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Type of Valve | Butterfly valve
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Model | LSWP
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Seat Leakage Class | VI
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Air to fail | Valve Close
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Travel | 90ᵒ
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Supply Pressure | 4 KSC
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | AFR | Savo
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | P Shut | 1 KSC
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | Control valve |  |  | Model | SB-10
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Make | Pneucon
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Sr.No. | 1602 41933
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Type | Rotary single acting
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Model | 232 SA 100+ M
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Year of Mfg. | 2014
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Tubing | SS-304
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Size | 100 MM
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Cv | 275
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Hand wheel | YES
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Characteristic | On- Off
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Positioner | Pneucon
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Seat Replacement type | PTFE
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Type of Valve | Butterfly valve
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Model | LSWP
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Seat Leakage Class | VI
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Air to fail | Valve Close
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Travel | 90ᵒ
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Supply Pressure | 4 KSC
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | AFR | Savo
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | P Shut | 1 KSC
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Control valve |  |  | Model | SB-10
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Make | Pneucon
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Sr.No. | 1602 41932
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Type | Rotary single acting
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Model | 232 SA 100+ M
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Year of Mfg. | 2014
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Tubing | SS-304
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Size | 100 MM
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Cv | 275
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Hand wheel | YES
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Characteristic | On- Off
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Positioner | Pneucon
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Seat Replacement type | PTFE
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Type of Valve | Butterfly valve
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Model | LSWP
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Seat Leakage Class | VI
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Air to fail | Valve Close
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Travel | 90ᵒ
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Supply Pressure | 4 KSC
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | AFR | Savo
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | P Shut | 1 KSC
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Model | SB-10
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | Control valve |  |  | Recovered Tank LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Make | Pneucon
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Sr.No. | 1602 41940
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Type | Rotary single acting
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Model | 232 SA 75+ M
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Year of Mfg. | 2014
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Tubing | SS-304
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Size | 50 MM
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Cv | 68
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Hand wheel | YES
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Characteristic | On- Off
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Positioner | Pneucon
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Seat Replacement type | PTFE
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Type of Valve | Butterfly valve
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Model | LSWP
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Seat Leakage Class | VI
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Air to fail | Valve Close
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Travel | 90ᵒ
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Supply Pressure | 4 KSC
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | AFR | Savo
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | P Shut | 1 KSC
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | Control valve |  |  | Model | SB-10
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Make | Pneucon
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Sr.No. | 1602 41941
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Type | Rotary single acting
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Model | 232 SA75+ M
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Year of Mfg. | 2014
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Tubing | SS-304
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Size | 50 MM
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Cv | 170
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Hand wheel | YES
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Characteristic | On- Off
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Positioner | Pneucon
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Seat Replacement type | PTFE
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Type of Valve | Butterfly valve
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Model | LSWP
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Seat Leakage Class | VI
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Air to fail | Valve Close
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Travel | 90ᵒ
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Supply Pressure | 4 KSC
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | AFR | Savo
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | P Shut | 1 KSC
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Model | SB-10
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | Control valve |  |  | Saturated Brine Tank | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Make | Pneucon
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Sr.No. | 1602 41944
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Type | Rotary single acting
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Model | 232 SA 075+ M
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Year of Mfg. | 2014
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Tubing | SS-304
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Size | 85 MM
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Cv | 170
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Hand wheel | YES
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Characteristic | On- Off
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Positioner | Pneucon
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Seat Replacement type | PTFE
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Type of Valve | Butterfly valve
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Model | LSWP
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Seat Leakage Class | VI
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Air to fail | Valve Close
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Travel | 90ᵒ
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Supply Pressure | 4 KSC
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | AFR | Savo
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | P Shut | 1 KSC
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Model | SB-10
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Hot Water Tank Level Tx. | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | Control valve |  |  | Recovered Water Tank Level Tx. | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Make | Pneucon
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Sr.No. | 1602 41907
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Type | Rotary single acting
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Model | 232 SA 075+ M
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Year of Mfg. | 2014
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Tubing | SS-304
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Size | 85 MM
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Cv | 170
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Hand wheel | YES
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Characteristic | On- Off
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Positioner | Pneucon
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Seat Replacement type | PTFE
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Type of Valve | Butterfly valve
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Model | LSWP
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Seat Leakage Class | VI
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Air to fail | Valve Close
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Travel | 90ᵒ
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Supply Pressure | 4 KSC
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | AFR | Savo
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | P Shut | 1 KSC
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Model | SB-10
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Sweet Water tank LT | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | Control valve |  |  | Sweet Water tank Temp. Tx. | YOKOGAWA/YTA 110 - EA2DB
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Make | Pneucon
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Sr.No. | 1602 41943
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Type | Rotary single acting
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Model | 232 SA 85+ M
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Year of Mfg. | 2014
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Tubing | SS-304
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Size | 80 MM
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Cv | 170
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Hand wheel | YES
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Characteristic | On- Off
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Positioner | Pneucon
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Seat Replacement type | PTFE
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Type of Valve | Butterfly valve
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Model | LSWP
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Seat Leakage Class | VI
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Air to fail | Valve Close
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Travel | 90ᵒ
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Supply Pressure | 4 KSC
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | AFR | Savo
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | P Shut | 1 KSC
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Model | SB-10
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | Control valve |  |  | Hot Water tank Temp. Tx. | Yokogawa/YTA 110 - EA2DB
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Make | Pneucon
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Sr.No. | 1602 41903
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Type | Rotary single acting
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Model | 310/RS-100
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Year of Mfg. | 2014
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Tubing | SS-304
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Size | 50 MM
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Cv | 68
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Hand wheel | YES
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Characteristic | On- Off
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Positioner | Pneucon
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Seat Replacement type | PTFE
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Type of Valve | Bal Valve
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Model | LSWP
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Seat Leakage Class | VI
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Air to fail | Valve Close
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Travel | 90ᵒ
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Supply Pressure | 4 KSC
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | AFR | Savo
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | P Shut | 1 KSC
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Model | SB-10
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | Control valve |  |  | Sweet Water tank Temp. tx. | Yokogawa/YTA 110 - EA2DB
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Make | Pneucon
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Sr.No. | 1511 41537
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Type | Rotary single acting
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Model | 232 SA 85+ M
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Year of Mfg. | 2014
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Tubing | SS-304
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Size | 80 MM
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Cv | 170
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Hand wheel | YES
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Characteristic | On- Off
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Positioner | Pneucon
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Seat Replacement type | PTFE
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Type of Valve | Butterfly valve
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Model | LSWP
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Seat Leakage Class | VI
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Air to fail | Valve Close
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Travel | 90ᵒ
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Supply Pressure | 4 KSC
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | AFR | Savo
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | P Shut | 1 KSC
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | Model | SB-10
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | Control valve |  |  | FBD Heater temp. trans. | Yokogawa/YTA 110 - EA2DB
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Make | Pneucon
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Sr.No. | 1511 41535
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Type | Rotary single acting
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Model | 232 SA 75+ M
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Year of Mfg. | 2014
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Tubing | SS-304
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Size | 50 MM
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Cv | 68
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Hand wheel | YES
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Characteristic | On- Off
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Positioner | Pneucon
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Seat Replacement type | PTFE
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Type of Valve | Butterfly valve
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Model | LSWP
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Seat Leakage Class | VI
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Air to fail | Valve Close
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Travel | 90ᵒ
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Supply Pressure | 4 KSC
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | AFR | Savo
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | P Shut | 1 KSC
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Model | SB-10
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | Control valve |  |  | Primary Tank Level transmiter | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Make | Pneucon
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Sr.No. | 1602 41978
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Type | Diapharm
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Model | 110 /PDC 030
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Year of Mfg. | 2014
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Tubing | SS-304
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Size | 65 MM
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Cv | 90
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Hand wheel | No
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Characteristic | Equal
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Positioner | Rotex
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Seat Replacement type | PTFE
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Type of Valve | Globe valve
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Seat Leakage Class | VI
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Air to fail | Valve Close
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Travel | 90ᵒ
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Supply Pressure | 4 KSC
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | AFR | Savo
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | P Shut | 1 KSC
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Model | SB-10
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Hot water reciver to R/f C/F PT(Refinery Batch) | ABB/266HSHQSBA7-L9B6R1
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Hot water reciver to R/f C/F TT(Refinery Batch) | ABB/TTF2000Y1A1B1K1C1
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | Control valve |  |  | Pressure gauge | General
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Make | Pneucon
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Sr.No. | 1601 42981
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Type | Diaphram
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Model | 110/PDC 030
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Year of Mfg. | 2014
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Tubing | SS-304
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Size | 50 MM
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Cv | 50
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Hand wheel | No
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Characteristic | Equal
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Positioner | Rotex
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Seat Replacement type | SS-304
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Type of Valve | Globe valve
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Seat Leakage Class | VI
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Air to fail | Valve Close
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Travel | 28 mm
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Supply Pressure | 2.5 KSC
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | AFR | Savo
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | P Shut | 4 KSC
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Model | SB-10
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Ex. Steam to PHE I/L PT(Refinery Batch) | ABB/266HSHQSBA7-L9B6R1
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | R/F Batch Machine SHWW TT | ABB/TTF2000Y1A1B1K1C1
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | Control valve |  |  | Pressure gauge | General
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Make | R K Valve
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Sr.No. | 1516 0899
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Type | Diapharm
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Model | 10-765/A30/5T
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Year of Mfg. | 2014
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Tubing | SS-304
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Size | 38 MM
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Cv | 3.2
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Hand wheel | YES
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Material Disc/Body | A351 CR CF8
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Characteristic | Equal %
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Positioner | YTC
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Seat Replacement type | SS-316FH
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Type of Valve | Globe valve
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Seat Leakage Class | VI
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Air to fail | Valve Open
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Travel | 28 mm
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Supply Pressure | 2.5 KSC
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | AFR | Savo
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | P Shut | 4 KSC
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Model | SB-10
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | BRS Brine I/L Pres.. Trans. | ABB/266HSHPSBA1L1B6
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Membrane PT | ABB/266HSHPSBA1L1B6
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Permit Tank LT | ABB/3K872014220011
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | BRS Hi Pre. Trans. | ABB/266HSHPSBA1L1B6
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | BRS water O/L temp trans. | ABB/TTF2000Y1A1B1K1C1
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | Control valve |  |  | Reject Tank LT | ABB/3K872014220011
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Make | Pneucon
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Sr.No. | 1511 41515
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Type | Diaphram
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Model | 110/PDC 140 S
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Year of Mfg. | 2014
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Tubing | SS-304
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Size | 150 MM
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Cv | 220
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Hand wheel | YES
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Characteristic | Equal
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Positioner | Siemens
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Seat Replacement type | PTFE
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Type of Valve | Globe Valve(Contoured)
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Model | Sipart PS2
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Seat Leakage Class | VI
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Air to fail | Valve Close
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Sr.No. | N1F8037470861
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Travel | 57 MM
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Supply Pressure | 2.5 KSC
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | AFR | Savo
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | P Shut | .2 KSC
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Model | SB-11-4SN 200 M 1/4"
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Level Transmitter | Yokogawa/EJA 118E -JMS0J-912 EB-EA13A1S
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Body Temp. Transmitter | Yokogawa/YTA 110 - EA2DB
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Brix transmitter | Birth Hold/LB565
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Body Vacuum Transmitter | Yokogawa/EJA530E-JAS40N-012EL
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Calendria temp. Transmitter | Yokogawa/YTA 110 - EA2DB
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Auto feed Panel | GN engineering
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Calendria Pr. Transmitter | Yokogawa/EJA530E-JAS40N-012EL
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Tail pipe temp Transmitter | Yokogawa/YTA 110 - EA2DB
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | Control valve |  |  | Vacuum/Pr. /temp. Gauge | General
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Make | Pneucon
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Sr.No. | 1610 45380
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Type | Rotary single acting
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Model | 232SA 200+M
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Year of Mfg. | 2014
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Tubing | SS-304
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Size | 300 MM
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Cv | 2750
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Hand wheel | YES
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Characteristic | On-off
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Positioner | Pneucon
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Seat Replacement type | PTFE
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Type of Valve | Butterfly valve
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Model | LSWP
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Seat Leakage Class | VI
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Air to fail | Valve Open
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Travel | 90ᵒ
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Supply Pressure | 4 KSC
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | AFR | Savo
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | P Shut | 1 KSC
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | Control valve |  |  | Model | SB-10
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Make | Pneucon
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Sr.No. | 1610 45375
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Type | Rotary single acting
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Model | 232SA 115+M
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Year of Mfg. | 2014
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Tubing | SS-304
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Size | 125 MM
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Cv | 425
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Hand wheel | YES
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Characteristic | On-off
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Positioner | Pneucon
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Seat Replacement type | PTFE
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Type of Valve | Butterfly valve
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Model | LSWP
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Seat Leakage Class | VI
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Air to fail | Valve Open
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Travel | 90ᵒ
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Supply Pressure | 4 KSC
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | AFR | Savo
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | P Shut | 1 KSC
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | Control valve |  |  | Model | SB-10
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Make | Pneucon
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Sr.No. | 1610 45368
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Type | Rotary single acting
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Model | 232SA 115+M
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Year of Mfg. | 2014
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Tubing | SS-304
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Size | 125 MM
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Cv | 425
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Hand wheel | YES
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Characteristic | On-off
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Positioner | Pneucon
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Seat Replacement type | PTFE
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Type of Valve | Butterfly valve
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Model | LSWP
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Seat Leakage Class | VI
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Air to fail | Valve Open
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Travel | 90ᵒ
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Supply Pressure | 4 KSC
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | AFR | Savo
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | P Shut | 1 KSC
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | Control valve |  |  | Model | SB-10
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Make | Pneucon
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Sr.No. | 1610 45370
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Type | Rotary single acting
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Model | 232SA 115+M
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Year of Mfg. | 2014
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Tubing | SS-304
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Size | 125 MM
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Cv | 425
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Hand wheel | YES
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Characteristic | On-off
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Positioner | Pneucon
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Seat Replacement type | PTFE
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Type of Valve | Butterfly valve
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Model | LSWP
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Seat Leakage Class | VI
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Air to fail | Valve Open
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Travel | 90ᵒ
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Supply Pressure | 4 KSC
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | AFR | Savo
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | P Shut | 1 KSC
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | Control valve |  |  | Model | SB-10
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Make | Pneucon
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Sr.No. | 1511 41547
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Type | Rotary single acting
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Model | 232SA 115+M
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Year of Mfg. | 2014
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Tubing | SS-304
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Size | 125 MM
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Cv | 425
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Hand wheel | YES
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Characteristic | On-off
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Positioner | Pneucon
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Seat Replacement type | PTFE
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Type of Valve | Butterfly valve
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Model | LSWP
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Seat Leakage Class | VI
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Air to fail | Valve Open
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Travel | 90ᵒ
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Supply Pressure | 4 KSC
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | AFR | Savo
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | P Shut | 1 KSC
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | Control valve |  |  | Model | SB-10
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Make | Pneucon
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Sr.No. | 1511 41546
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Type | Rotary single acting
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Model | 232SA 115+M
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Year of Mfg. | 2014
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Tubing | SS-304
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Size | 125 MM
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Cv | 425
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Hand wheel | YES
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Characteristic | On-off
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Positioner | Pneucon
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Seat Replacement type | PTFE
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Type of Valve | Butterfly valve
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Model | LSWP
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Seat Leakage Class | VI
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Air to fail | Valve Open
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Travel | 90ᵒ
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Supply Pressure | 4 KSC
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | AFR | Savo
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | P Shut | 1 KSC
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | Control valve |  |  | Model | SB-10
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Make | Pneucon
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Sr.No. | 1511 41578
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Type | Rotary single acting
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Model | 232SA 115+M
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Year of Mfg. | 2014
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Tubing | SS-304
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Size | 125 MM
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Cv | 2750
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Hand wheel | YES
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Characteristic | On-off
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Positioner | Pneucon
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Seat Replacement type | PTFE
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Type of Valve | Butterfly valve
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Model | LSWP
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Seat Leakage Class | VI
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Air to fail | Valve Open
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Travel | 90ᵒ
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Supply Pressure | 4 KSC
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | AFR | Savo
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | P Shut | 1 KSC
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | Control valve |  |  | Model | SB-10
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Make | Pneucon
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Sr.No. | 1511 41570
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Type | Rotary single acting
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Model | 232SA 115+M
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Year of Mfg. | 2014
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Tubing | SS-304
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Size | 125 MM
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Cv | 2750
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Hand wheel | YES
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Characteristic | On-off
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Positioner | Pneucon
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Seat Replacement type | PTFE
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Type of Valve | Butterfly valve
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Model | LSWP
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Seat Leakage Class | VI
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Air to fail | Valve Open
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Travel | 90ᵒ
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Supply Pressure | 4 KSC
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | AFR | Savo
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | P Shut | 1 KSC
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | Control valve |  |  | Model | SB-10
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Make | Pneucon
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Sr.No. | 1511 41571
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Type | Rotary single acting
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Model | 232SA 125+M
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Year of Mfg. | 2014
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Tubing | SS-304
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Size | 150 MM
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Cv | 425
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Hand wheel | YES
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Characteristic | On-off
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Positioner | Pneucon
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Seat Replacement type | PTFE
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Type of Valve | Butterfly valve
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Model | LSWP
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Seat Leakage Class | VI
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Air to fail | Valve Open
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Travel | 90ᵒ
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Supply Pressure | 4 KSC
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | AFR | Savo
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | P Shut | 1 KSC
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | Control valve |  |  | Model | SB-10
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Make | Pneucon
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Sr.No. | 1610 46382
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Type | Rotary single acting
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Model | 232SA 200+M
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Year of Mfg. | 2014
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Tubing | SS-304
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Size | 400 MM
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Cv | 8000
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Hand wheel | YES
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Characteristic | On-off
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Positioner | Pneucon
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Seat Replacement type | PTFE
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Type of Valve | Butterfly valve
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Model | LSWP
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Seat Leakage Class | VI
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Air to fail | Valve Open
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Travel | 90ᵒ
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Supply Pressure | 4 KSC
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | AFR | Savo
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | P Shut | 1 KSC
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | Control valve |  |  | Model | SB-10
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Make | Pneucon
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Sr.No. | 1610 45369
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Type | Rotary single acting
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Model | 232SA 115+M
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Year of Mfg. | 2014
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Tubing | SS-304
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Size | 125 MM
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Cv | 425
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Hand wheel | YES
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Characteristic | On-off
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Positioner | Pneucon
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Seat Replacement type | PTFE
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Type of Valve | Butterfly valve
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Model | LSWP
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Seat Leakage Class | VI
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Air to fail | Valve Open
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Travel | 90ᵒ
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Supply Pressure | 4 KSC
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | AFR | Savo
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | P Shut | 1 KSC
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | Control valve |  |  | Model | SB-10
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Make | Pneucon
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Sr.No. | 1610 45315
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Type | Rotary single acting
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Model | 232SA 115+M
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Year of Mfg. | 2014
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Tubing | SS-304
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Size | 125 MM
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Cv | 425
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Hand wheel | YES
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Characteristic | On-off
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Positioner | Pneucon
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Seat Replacement type | PTFE
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Type of Valve | Butterfly valve
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Model | LSWP
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Seat Leakage Class | VI
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Air to fail | Valve Open
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Travel | 90ᵒ
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Supply Pressure | 4 KSC
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | AFR | Savo
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | P Shut | 1 KSC
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | Control valve |  |  | Model | SB-10
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Make | Pneucon
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Sr.No. | 1610 45372
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Type | Rotary single acting
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Model | 232SA 115+M
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Year of Mfg. | 2014
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Tubing | SS-304
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Size | 125 MM
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Cv | 425
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Hand wheel | YES
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Characteristic | On-off
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Positioner | Pneucon
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Seat Replacement type | PTFE
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Type of Valve | Butterfly valve
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Model | LSWP
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Seat Leakage Class | VI
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Air to fail | Valve Open
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Travel | 90ᵒ
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Supply Pressure | 4 KSC
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | AFR | Savo
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | P Shut | 1 KSC
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | Control valve |  |  | Model | SB-10
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Make | Pneucon
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Sr.No. | 1610 47378
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Type | Rotary single acting
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Model | 232SA 125+M
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Year of Mfg. | 2014
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Tubing | SS-304
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Size | 150 MM
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Cv | 425
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Hand wheel | YES
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Characteristic | On-off
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Positioner | Pneucon
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Seat Replacement type | PTFE
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Type of Valve | Butterfly valve
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Model | LSWP
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Seat Leakage Class | VI
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Air to fail | Valve Open
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Travel | 90ᵒ
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Supply Pressure | 4 KSC
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | AFR | Savo
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | P Shut | 1 KSC
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | Control valve |  |  | Model | SB-10
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Make | Pneucon
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Sr.No. | 1610 45379
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Type | Rotary single acting
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Model | 232SA 175+M
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Year of Mfg. | 2014
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Tubing | SS-304
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Size | 250 MM
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Cv | 1900
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Hand wheel | YES
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Characteristic | On-off
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Positioner | Pneucon
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Seat Replacement type | PTFE
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Type of Valve | Butterfly valve
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Model | LSWP
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Seat Leakage Class | VI
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Air to fail | Valve Open
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Travel | 90ᵒ
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Supply Pressure | 4 KSC
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | AFR | Savo
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | P Shut | 1 KSC
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | Control valve |  |  | Model | SB-10
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Make | Pneucon
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Sr.No. | 1610 45365
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Type | Rotary single acting
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Model | 232SA 100+M
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Year of Mfg. | 2014
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Tubing | SS-304
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Size | 100 MM
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Cv | 450
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Hand wheel | YES
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Characteristic | On-off
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Positioner | Pneucon
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Seat Replacement type | PTFE
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Type of Valve | Butterfly valve
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Model | LSWP
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Seat Leakage Class | VI
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Air to fail | Valve Open
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Travel | 90ᵒ
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Supply Pressure | 4 KSC
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | AFR | Savo
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | P Shut | 1 KSC
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | Control valve |  |  | Model | SB-10
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Make | Pneucon
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Sr.No. | 1610 45366
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Type | Rotary single acting
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Model | 232SA 100+M
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Year of Mfg. | 2014
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Tubing | SS-304
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Size | 100 MM
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Cv | 450
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Hand wheel | YES
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Characteristic | On-off
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Positioner | Pneucon
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Seat Replacement type | PTFE
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Type of Valve | Butterfly valve
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Model | LSWP
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Seat Leakage Class | VI
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Air to fail | Valve Open
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Travel | 90ᵒ
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Supply Pressure | 4 KSC
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | AFR | Savo
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | P Shut | 1 KSC
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | Control valve |  |  | Model | SB-10
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Make | Pneucon
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Sr.No. | 1511 41541
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Type | Rotary single acting
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Model | 232SA 200+M
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Year of Mfg. | 2014
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Tubing | SS-304
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Size | 300 MM
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Cv | 2750
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Hand wheel | YES
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Characteristic | On-off
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Positioner | Pneucon
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Seat Replacement type | PTFE
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Type of Valve | Butterfly valve
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Model | LSWP
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Seat Leakage Class | VI
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Air to fail | Valve Open
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Travel | 90ᵒ
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Supply Pressure | 4 KSC
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | AFR | Savo
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | P Shut | 1 KSC
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | Control valve |  |  | Model | SB-10
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Make | Pneucon
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Sr.No. | 1511 41555
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Type | Rotary single acting
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Model | 232SA 115+M
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Year of Mfg. | 2014
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Tubing | SS-304
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Size | 125 MM
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Cv | 450
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Hand wheel | YES
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Characteristic | On-off
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Positioner | Pneucon
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Seat Replacement type | PTFE
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Type of Valve | Butterfly valve
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Model | LSWP
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Seat Leakage Class | VI
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Air to fail | Valve Open
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Travel | 90ᵒ
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Supply Pressure | 4 KSC
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | AFR | Savo
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | P Shut | 1 KSC
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | Control valve |  |  | Model | SB-10
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Make | Pneucon
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Sr.No. | 1511 41556
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Type | Rotary single acting
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Model | 232SA 115+M
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Year of Mfg. | 2014
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Tubing | SS-304
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Size | 125 MM
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Cv | 450
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Hand wheel | YES
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Characteristic | On-off
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Positioner | Pneucon
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Seat Replacement type | PTFE
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Type of Valve | Butterfly valve
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Model | LSWP
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Seat Leakage Class | VI
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Air to fail | Valve Open
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Travel | 90ᵒ
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Supply Pressure | 4 KSC
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | AFR | Savo
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | P Shut | 1 KSC
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | Control valve |  |  | Model | SB-10
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Make | Pneucon
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Sr.No. | 1511 41557
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Type | Rotary single acting
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Model | 232 SA 115+M
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Year of Mfg. | 2014
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Tubing | SS-304
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Size | 125 MM
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Cv | 450
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Hand wheel | YES
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Characteristic | On-off
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Positioner | Pneucon
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Seat Replacement type | PTFE
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Type of Valve | Butterfly valve
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Model | LSWP
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Seat Leakage Class | VI
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Air to fail | Valve Open
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Travel | 90ᵒ
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Supply Pressure | 4 KSC
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | AFR | Savo
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | P Shut | 1 KSC
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | Control valve |  |  | Model | SB-10
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Make | Pneucon
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Sr.No. | 1511 41576
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Type | Rotary single acting
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Model | 232SA 100+M
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Year of Mfg. | 2014
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Tubing | SS-304
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Size | 100 MM
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Cv | 450
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Hand wheel | YES
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Characteristic | On-off
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Positioner | Pneucon
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Seat Replacement type | PTFE
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Type of Valve | Butterfly valve
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Model | LSWP
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Seat Leakage Class | VI
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Air to fail | Valve Open
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Travel | 90ᵒ
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Supply Pressure | 4 KSC
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | AFR | Savo
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | P Shut | 1 KSC
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | Control valve |  |  | Model | SB-10
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Make | Pneucon
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Sr.No. | 1511 41575
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Type | Rotary single acting
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Model | 232SA 100+M
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Year of Mfg. | 2014
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Tubing | SS-304
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Size | 100 MM
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Cv | 450
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Hand wheel | YES
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Characteristic | On-off
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Positioner | Pneucon
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Seat Replacement type | PTFE
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Type of Valve | Butterfly valve
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Model | LSWP
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Seat Leakage Class | VI
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Air to fail | Valve Open
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Travel | 90ᵒ
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Supply Pressure | 4 KSC
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | AFR | Savo
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | P Shut | 1 KSC
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | Control valve |  |  | Model | SB-10
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Make | Pneucon
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Sr.No. | 1511 41574
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Type | Rotary single acting
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Model | 232SA 115+M
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Year of Mfg. | 2014
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Tubing | SS-304
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Size | 100 MM
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Cv | 450
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Hand wheel | YES
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Characteristic | On-off
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Positioner | Pneucon
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Seat Replacement type | PTFE
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Type of Valve | Butterfly valve
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Model | LSWP
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Seat Leakage Class | VI
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Air to fail | Valve Open
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Travel | 90ᵒ
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Supply Pressure | 4 KSC
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | AFR | Savo
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | P Shut | 1 KSC
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | Control valve |  |  | Model | SB-10
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Make | Pneucon
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Sr.No. | 1511 41572
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Type | Rotary single acting
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Model | 232 SA 100+M
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Year of Mfg. | 2014
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Tubing | SS-304
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Size | 250 MM
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Cv | 450
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Hand wheel | YES
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Characteristic | On-off
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Positioner | Pneucon
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Seat Replacement type | PTFE
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Type of Valve | Butterfly valve
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Model | LSWP
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Seat Leakage Class | VI
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Air to fail | Valve Open
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Travel | 90ᵒ
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Supply Pressure | 4 KSC
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | AFR | Savo
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | P Shut | 1 KSC
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | Control valve |  |  | Model | SB-10
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Make | Pneucon
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Sr.No. | 1511 41540
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Type | Rotary single acting
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Model | 232SA 200+M
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Year of Mfg. | 2014
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Tubing | SS-304
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Size | 125 MM
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Cv | 2750
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Hand wheel | YES
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Characteristic | On-off
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Positioner | Pneucon
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Seat Replacement type | PTFE
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Type of Valve | Butterfly valve
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Model | LSWP
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Seat Leakage Class | VI
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Air to fail | Valve Open
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Travel | 90ᵒ
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Supply Pressure | 4 KSC
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | AFR | Savo
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | P Shut | 1 KSC
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | Control valve |  |  | Model | SB-10
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Make | Pneucon
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Sr.No. | 1511 41552
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Type | Rotary single acting
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Model | 232SA 115+M
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Year of Mfg. | 2014
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Tubing | SS-304
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Size | 125 MM
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Cv | 425
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Hand wheel | YES
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Characteristic | On-off
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Positioner | Pneucon
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Seat Replacement type | PTFE
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Type of Valve | Butterfly valve
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Model | LSWP
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Seat Leakage Class | VI
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Air to fail | Valve Open
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Travel | 90ᵒ
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Supply Pressure | 4 KSC
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | AFR | Savo
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | P Shut | 1 KSC
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | Control valve |  |  | Model | SB-10
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Make | Pneucon
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Sr.No. | 1511 41553
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Type | Rotary single acting
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Model | 232SA 115+M
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Year of Mfg. | 2014
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Tubing | SS-304
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Size | 125 MM
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Cv | 425
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Hand wheel | YES
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Characteristic | On-off
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Positioner | Pneucon
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Seat Replacement type | PTFE
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Type of Valve | Butterfly valve
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Model | LSWP
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Seat Leakage Class | VI
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Air to fail | Valve Open
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Travel | 90ᵒ
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Supply Pressure | 4 KSC
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | AFR | Savo
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | P Shut | 1 KSC
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | Control valve |  |  | Model | SB-10
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Make | Pneucon
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Sr.No. | 1511 41554
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Type | Rotary single acting
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Model | 232SA 115+M
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Year of Mfg. | 2014
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Tubing | SS-304
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Size | 125 MM
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Cv | 425
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Hand wheel | YES
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Characteristic | On-off
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Positioner | Pneucon
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Seat Replacement type | PTFE
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Type of Valve | Butterfly valve
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Model | LSWP
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Seat Leakage Class | VI
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Air to fail | Valve Open
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Travel | 90ᵒ
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Supply Pressure | 4 KSC
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | AFR | Savo
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | P Shut | 1 KSC
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | Control valve |  |  | Model | SB-10
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Make | Pneucon
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Sr.No. | 1511 41539
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Type | Rotary single acting
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Model | 232SA 200+M
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Year of Mfg. | 2014
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Tubing | SS-304
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Size | 300 MM
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Cv | 2750
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Hand wheel | YES
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Characteristic | On-off
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Positioner | Pneucon
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Seat Replacement type | PTFE
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Type of Valve | Butterfly valve
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Model | LSWP
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Seat Leakage Class | VI
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Air to fail | Valve Open
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Travel | 90ᵒ
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Supply Pressure | 4 KSC
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | AFR | Savo
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | P Shut | 1 KSC
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | Control valve |  |  | Model | SB-10
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Make | Pneucon
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Sr.No. | 1511 41549
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Type | Rotary single acting
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Model | 232SA 115+M
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Year of Mfg. | 2014
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Tubing | SS-304
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Size | 125 MM
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Cv | 425
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Hand wheel | YES
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Characteristic | On-off
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Positioner | Pneucon
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Seat Replacement type | PTFE
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Type of Valve | Butterfly valve
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Model | LSWP
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Seat Leakage Class | VI
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Air to fail | Valve Open
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Travel | 90ᵒ
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Supply Pressure | 4 KSC
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | AFR | Savo
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | P Shut | 1 KSC
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | Control valve |  |  | Model | SB-10
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Make | Pneucon
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Sr.No. | 1511 41550
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Type | Rotary single acting
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Model | 232SA 115+M
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Year of Mfg. | 2014
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Tubing | SS-304
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Size | 125 MM
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Cv | 425
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Hand wheel | YES
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Characteristic | On-off
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Positioner | Pneucon
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Seat Replacement type | PTFE
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Type of Valve | Butterfly valve
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Model | LSWP
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Seat Leakage Class | VI
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Air to fail | Valve Open
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Travel | 90ᵒ
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Supply Pressure | 4 KSC
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | AFR | Savo
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | P Shut | 1 KSC
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | Control valve |  |  | Model | SB-10
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Make | Pneucon
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Sr.No. | 1511 41551
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Type | Rotary single acting
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Model | 232SA 115+M
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Year of Mfg. | 2014
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Tubing | SS-304
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Size | 125 MM
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Cv | 425
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Hand wheel | YES
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Characteristic | On-off
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Positioner | Pneucon
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Seat Replacement type | PTFE
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Type of Valve | Butterfly valve
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Model | LSWP
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Seat Leakage Class | VI
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Air to fail | Valve Open
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Travel | 90ᵒ
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Supply Pressure | 4 KSC
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | AFR | Savo
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | P Shut | 1 KSC
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | Control valve |  |  | Model | SB-10
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Make | Pneucon
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Sr.No. | 1511 41538
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Type | Rotary single acting
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Model | 232SA 200+M
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Year of Mfg. | 2014
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Tubing | SS-304
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Size | 300 MM
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Cv | 2750
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Hand wheel | YES
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Characteristic | On-off
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Positioner | Pneucon
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Seat Replacement type | PTFE
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Type of Valve | Butterfly valve
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Model | LSWP
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Seat Leakage Class | VI
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Air to fail | Valve Open
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Travel | 90ᵒ
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Supply Pressure | 4 KSC
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | AFR | Savo
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | P Shut | 1 KSC
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | Control valve |  |  | Model | SB-10
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Make | Pneucon
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Sr.No. | 1511 41543
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Type | Rotary single acting
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Model | 232SA 115+M
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Year of Mfg. | 2014
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Tubing | SS-304
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Size | 125 MM
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Cv | 425
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Hand wheel | YES
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Characteristic | On-off
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Positioner | Pneucon
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Seat Replacement type | PTFE
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Type of Valve | Butterfly valve
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Model | LSWP
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Seat Leakage Class | VI
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Air to fail | Valve Open
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Travel | 90ᵒ
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Supply Pressure | 4 KSC
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | AFR | Savo
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | P Shut | 1 KSC
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | Control valve |  |  | Model | SB-10
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Make | Pneucon
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Sr.No. | 1511 41544
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Type | Rotary single acting
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Model | 232SA 115+M
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Year of Mfg. | 2014
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Tubing | SS-304
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Size | 125 MM
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Cv | 425
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Hand wheel | YES
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Characteristic | On-off
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Positioner | Pneucon
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Seat Replacement type | PTFE
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Type of Valve | Butterfly valve
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Model | LSWP
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Seat Leakage Class | VI
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Air to fail | Valve Open
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Travel | 90ᵒ
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Supply Pressure | 4 KSC
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | AFR | Savo
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | P Shut | 1 KSC
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | Control valve |  |  | Model | SB-10
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Make | Pneucon
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Sr.No. | 1511 41545
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Type | Rotary single acting
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Model | 232SA 115+M
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Year of Mfg. | 2014
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Tubing | SS-304
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Size | 125 MM
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Cv | 425
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Hand wheel | YES
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Characteristic | On-off
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Positioner | Pneucon
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Seat Replacement type | PTFE
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Type of Valve | Butterfly valve
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Model | LSWP
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Seat Leakage Class | VI
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Air to fail | Valve Open
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Travel | 90ᵒ
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Supply Pressure | 4 KSC
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | AFR | Savo
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | P Shut | 1 KSC
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | Control valve |  |  | Model | SB-10
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Make | Pneucon
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Sr.No. | 1511 41542
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Type | Rotary single acting
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Model | 232SA 200+M
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Year of Mfg. | 2014
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Tubing | SS-304
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Size | 300 MM
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Cv | 2750
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Hand wheel | YES
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Characteristic | On-off
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Positioner | Pneucon
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Seat Replacement type | PTFE
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Type of Valve | Butterfly valve
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Model | LSWP
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Seat Leakage Class | VI
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Air to fail | Valve Open
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Travel | 90ᵒ
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Supply Pressure | 4 KSC
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | AFR | Savo
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | P Shut | 1 KSC
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | Control valve |  |  | Model | SB-10
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Make | Pneucon
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Sr.No. | 1511 41573
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Type | Rotary single acting
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Model | 232SA 115+M
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Year of Mfg. | 2014
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Tubing | SS-304
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Size | 125 MM
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Cv | 425
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Hand wheel | YES
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Characteristic | On-off
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Positioner | Pneucon
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Seat Replacement type | PTFE
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Type of Valve | Butterfly valve
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Model | LSWP
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Seat Leakage Class | VI
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Air to fail | Valve Open
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Travel | 90ᵒ
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Supply Pressure | 4 KSC
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | AFR | Savo
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | P Shut | 1 KSC
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | Control valve |  |  | Model | SB-10
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Make | Pneucon
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Sr.No. | 1511 41559
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Type | Rotary single acting
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Model | 232SA 115+M
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Year of Mfg. | 2014
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Tubing | SS-304
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Size | 125 MM
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Cv | 425
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Hand wheel | YES
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Characteristic | On-off
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Positioner | Pneucon
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Seat Replacement type | PTFE
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Type of Valve | Butterfly valve
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Model | LSWP
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Seat Leakage Class | VI
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Air to fail | Valve Open
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Travel | 90ᵒ
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Supply Pressure | 4 KSC
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | AFR | Savo
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | P Shut | 1 KSC
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | Control valve |  |  | Model | SB-10
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Make | Pneucon
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Sr.No. | 1511 41573
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Type | Rotary single acting
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Model | 232SA 115+M
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Year of Mfg. | 2014
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Tubing | SS-304
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Size | 125 MM
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Cv | 425
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Hand wheel | YES
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Characteristic | On-off
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Positioner | Pneucon
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Seat Replacement type | PTFE
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Type of Valve | Butterfly valve
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Model | LSWP
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Seat Leakage Class | VI
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Air to fail | Valve Open
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Travel | 90ᵒ
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Supply Pressure | 4 KSC
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | AFR | Savo
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | P Shut | 1 KSC
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | Control valve |  |  | Model | SB-10
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Make | Pneucon
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Sr.No. | 1511 41566
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Type | Rotary single acting
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Model | 232/SA 200+M
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Year of Mfg. | 2014
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Tubing | SS-304
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Size | 400 MM
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Cv | 8000
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Hand wheel | YES
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Characteristic | On-off
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Positioner | SIEMENS
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Seat Replacement type | PTFE
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Type of Valve | Butterfly valve
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Model | SIPART PS2
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Seat Leakage Class | VI
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Air to fail | Valve Open
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Sr.No. | N1F9097475739
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Travel | 90ᵒ
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Supply Pressure | 4 KSC
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | AFR | Savo
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | P Shut | 1 KSC
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | Control valve |  |  | Model | SB-10
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Make | Pneucon
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Sr.No. | 1511 41560
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Type | Rotary single acting
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Model | 232SA 115+M
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Year of Mfg. | 2014
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Tubing | SS-304
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Size | 125 MM
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Cv | 425
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Hand wheel | YES
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Characteristic | On-off
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Positioner | Pneucon
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Seat Replacement type | PTFE
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Type of Valve | Butterfly valve
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Model | LSWP
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Seat Leakage Class | VI
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Air to fail | Valve Open
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Travel | 90ᵒ
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Supply Pressure | 4 KSC
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | AFR | Savo
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | P Shut | 1 KSC
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | Control valve |  |  | Model | SB-10
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Make | Pneucon
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Sr.No. | 1511 41561
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Type | Rotary single acting
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Model | 232SA 115+M
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Year of Mfg. | 2014
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Tubing | SS-304
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Size | 125 MM
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Cv | 425
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Hand wheel | YES
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Characteristic | On-off
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Positioner | Pneucon
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Seat Replacement type | PTFE
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Type of Valve | Butterfly valve
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Model | LSWP
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Seat Leakage Class | VI
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Air to fail | Valve Open
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Travel | 90ᵒ
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Supply Pressure | 4 KSC
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | AFR | Savo
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | P Shut | 1 KSC
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | Control valve |  |  | Model | SB-10
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Make | Pneucon
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Sr.No. | 1511 41562
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Type | Rotary single acting
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Model | 232SA 115+M
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Year of Mfg. | 2014
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Tubing | SS-304
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Size | 125 MM
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Cv | 425
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Hand wheel | YES
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Characteristic | On-off
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Positioner | Pneucon
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Seat Replacement type | PTFE
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Type of Valve | Butterfly valve
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Model | LSWP
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Seat Leakage Class | VI
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Air to fail | Valve Open
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Travel | 90ᵒ
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Supply Pressure | 4 KSC
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | AFR | Savo
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | P Shut | 1 KSC
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | Control valve |  |  | Model | SB-10
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Make | Pneucon
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Sr.No. | 1511 41577
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Type | Rotary single acting
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Model | 232/SA 125+M
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Year of Mfg. | 2014
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Tubing | SS-304
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Size | 150 MM
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Cv | 650
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Hand wheel | YES
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Characteristic | On-off
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Positioner | Pneucon
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Seat Replacement type | PTFE
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Type of Valve | Butterfly valve
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Model | LSWP
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Seat Leakage Class | VI
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Air to fail | Valve Open
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Travel | 90ᵒ
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Supply Pressure | 4 KSC
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | AFR | Savo
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | P Shut | 1 KSC
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Control valve |  |  | Model | SB-10
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Make | Pneucon
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Sr.No. | 1511 41567
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Type | Rotary single acting
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Model | 232/SA 200+M
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Year of Mfg. | 2014
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Tubing | SS-304
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Size | 400 MM
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Cv | 8000
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Hand wheel | YES
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Characteristic | On-off
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Positioner | SIEMENS
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Seat Replacement type | PTFE
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Type of Valve | Butterfly valve
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Model | SIPART PS2
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Seat Leakage Class | VI
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Air to fail | Valve Open
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Sr.No. | N1F9097475672
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Travel | 90ᵒ
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Supply Pressure | 4 KSC
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | AFR | Savo
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | P Shut | 1 KSC
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | Control valve |  |  | Model | SB-10
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Make | Pneucon
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Sr.No. | 1511 41563
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Type | Rotary single acting
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Model | 232SA 115+M
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Year of Mfg. | 2014
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Tubing | SS-304
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Size | 125 MM
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Cv | 425
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Hand wheel | YES
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Characteristic | On-off
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Positioner | Pneucon
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Seat Replacement type | PTFE
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Type of Valve | Butterfly valve
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Model | LSWP
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Seat Leakage Class | VI
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Air to fail | Valve Open
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Travel | 90ᵒ
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Supply Pressure | 4 KSC
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | AFR | Savo
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | P Shut | 1 KSC
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | Control valve |  |  | Model | SB-10
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Make | Pneucon
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Sr.No. | 1511 41564
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Type | Rotary single acting
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Model | 232SA 115+M
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Year of Mfg. | 2014
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Tubing | SS-304
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Size | 125 MM
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Cv | 425
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Hand wheel | YES
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Characteristic | On-off
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Positioner | Pneucon
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Seat Replacement type | PTFE
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Type of Valve | Butterfly valve
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Model | LSWP
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Seat Leakage Class | VI
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Air to fail | Valve Open
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Travel | 90ᵒ
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Supply Pressure | 4 KSC
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | AFR | Savo
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | P Shut | 1 KSC
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | Control valve |  |  | Model | SB-10
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Make | Pneucon
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Sr.No. | 1511 41565
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Type | Rotary single acting
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Model | 232SA 115+M
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Year of Mfg. | 2014
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Tubing | SS-304
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Size | 125 MM
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Cv | 425
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Hand wheel | YES
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Characteristic | On-off
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Positioner | Pneucon
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Seat Replacement type | PTFE
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Type of Valve | Butterfly valve
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Model | LSWP
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Seat Leakage Class | VI
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Air to fail | Valve Open
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Travel | 90ᵒ
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Supply Pressure | 4 KSC
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | AFR | Savo
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | P Shut | 1 KSC
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | Control valve |  |  | Model | SB-10
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Make | Pneucon
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Sr.No. | 1511 41569
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Type | Rotary single acting
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Model | 232/SA 125+M
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Year of Mfg. | 2014
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Tubing | SS-304
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Size | 150 MM
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Cv | 650
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Hand wheel | YES
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Characteristic | On-off
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Positioner | Pneucon
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Seat Replacement type | PTFE
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Type of Valve | Butterfly valve
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Model | LSWP
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Seat Leakage Class | VI
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Air to fail | Valve Open
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Travel | 90ᵒ
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Supply Pressure | 4 KSC
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | AFR | Savo
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | P Shut | 1 KSC
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | Control valve |  |  | Model | SB-10
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Make | Sr.No.
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Type | Rotary doble acting
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Model | Year of Mfg.
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Tubing | SS-304
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Size | Cv
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Hand wheel | YES
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Material Disc/Body | Characteristic
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | On-off | Positioner
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Seat Replacement type | rubber
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Type of Valve | Butterfly valve
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Seat Leakage Class | VI
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Air to fail | Valve Open
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Travel | 90ᵒ
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Supply Pressure | 4 KSC
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | AFR | Savo
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | P Shut | 1 KSC
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | Control valve |  |  | Model | SB-10
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Make | Pneucon
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Sr.No. | Type
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Model | Year of Mfg.
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Tubing | SS-304
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Size | Cv
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Hand wheel | YES
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Material Disc/Body | Characteristic
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | On-off | Positioner
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Seat Replacement type | rubber
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Type of Valve | Butterfly valve
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Seat Leakage Class | VI
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Air to fail | Valve Open
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Travel | 90ᵒ
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Supply Pressure | 4 KSC
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | AFR | Savo
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | P Shut | 1 KSC
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | Control valve |  |  | Model | SB-10
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Make | BRAY/VAAS
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Sr.No. | 150637-001-003
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Type | Cylender
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Model | 950
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Year of Mfg. | 2014
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Tubing | SS-304
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Size | 350 MM
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Cv | 3250
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Hand wheel | YES
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Characteristic | On- Off
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Seat Replacement type | Type of Valve
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | KnifeEdge | Model
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Seat Leakage Class | VI
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Air to fail | Valve Close
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Travel | 350 mm
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Supply Pressure | 4 KSC
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | AFR | Savo
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | P Shut | 1 KSC
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Model | SB-10
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Crystlizer Level transmitter | Siemens/7ML52212BA11
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Control valve |  |  | Pug mill level transmitter | Siemens/7ML52212BA11
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Make | BRAY/VAAS
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Sr.No. | 150637-002-003
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Type | cylender
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Model | 950
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Year of Mfg. | 2014
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Tubing | SS-304
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Size | 350 MM
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Cv | 3250
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Hand wheel | YES
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Characteristic | On- Off
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Seat Replacement type | Type of Valve
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Knife Edge | Model
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Seat Leakage Class | VI
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Air to fail | Valve Close
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Travel | 350 mm
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Supply Pressure | 4 KSC
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | AFR | Savo
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | P Shut | 1 KSC
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Model | SB-10
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Crystlizer Level transmitter | Siemens/7ML52212BA11
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Control valve |  |  | Pug mill level transmitter | Siemens/7ML52212BA11
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Make | BRAY/VAAS
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Sr.No. | 150637-003-003
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Type | Cylender
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Model | 950
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Year of Mfg. | 2014
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Tubing | SS-304
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Size | 350 MM
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Cv | 3250
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Hand wheel | YES
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Characteristic | On- Off
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Seat Replacement type | Type of Valve
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Knife Edge | Model
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Seat Leakage Class | VI
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Air to fail | Valve Close
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Travel | 350 mm
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Supply Pressure | 4 KSC
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | AFR | Savo
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | P Shut | 1 KSC
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Model | SB-10
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Crystlizer Level transmitter | Siemens/7ML52212BA11
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | Control valve |  |  | Pug mill level transmitter | Siemens/7ML52212BA11
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Manufacturer – | Rosemount
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Serial No. | 6205889
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Working Temperature | (-29 to 60˚)
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Model | 8705TSA030C1W0B3
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Range | NA
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | working pressure | 285 PSI
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Nominal Dia ( MM) | 80 MM
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Calibration Range | NA
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Accuracy | 0.0015
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Material Body | Sensor Material
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | 316 S1 | Linearity
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Liner | PTFE
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Output | 4-20 mA
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Repeatability | ±0.1%
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Display Version | E- Series
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Power Supply | 90-220 VAC
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Comunication | HART
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Display unit | 2 line LCD
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Cable length | Head-Mount
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | Flow Meter |  |  | Protection | IP 67
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Manufacturer – | Rosemount
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Serial No. | 6205889
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Working Temperature | (-29 to 60˚)
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Model | 8705TSA015C1W0B3
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Range | NA
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | working pressure | 285 PSI
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Nominal Dia ( MM) | 40 MM
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Calibration Range | NA
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Accuracy | 0.0015
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Material Body | Sensor Material
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | 316 S1 | Repeatability
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Liner | PTFE
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Output | 4-20 mA
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Comunication | HART
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Display Version | Power Supply
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | 90-220 VAC | Protection
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Display unit | 2 line LCD
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | Flow Meter |  |  | Cable length | Head-Mount
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Manufacturer – | Rosemount
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Serial No. | 6205900
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Working Temperature | (-29 to 60˚)
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Model | 8705TSA030C1W0B3
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Range | NA
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | working pressure | 285 PSI
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Nominal Dia ( MM) | 80 MM
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Calibration Range | NA
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Accuracy | 0.0015
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Material Body | Sensor Material
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | 316 S1 | Repeatability
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Liner | PTFE
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Output | 4-20 mA
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Comunication | HART
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Display Version | E- Series
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Power Supply | 90-220 VAC
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Protection | IP 67
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Display unit | 2 line LCD
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | Flow Meter |  |  | Cable length | Head-Mount
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Manufacturer – | Rosemount
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Serial No. | 6205892
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Working Temperature | (-29 to 60˚)
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Model | 8705TSA040C1W0B3
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Range | NA
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | working pressure | 285 PSI
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Nominal Dia ( MM) | 100 MM
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Calibration Range | NA
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Accuracy | 0.0015
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Material Body | Sensor Material
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | 316 S1 | Repeatability
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Liner | PTFE
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Output | 4-20 mA
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Comunication | HART
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Display Version | E- Series
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Power Supply | 90-220 VAC
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Protection | IP 67
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Display unit | 2 line LCD
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | flow meter |  |  | Cable length | Head-Mount
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Manufacturer – | Rosemount
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Serial No. | 6205901
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Working Temperature | (-29 to 60˚)
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Model | 8705TSA030C1W0B3
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Range | NA
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | working pressure | 285 PSI
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Nominal Dia ( MM) | 80 MM
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Calibration Range | NA
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Accuracy | 0.0015
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Material Body | Sensor Material
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | 316 S1 | Repeatability
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Liner | PTFE
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Output | 4-20 mA
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Comunication | HART
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Display Version | E- Series
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Power Supply | 90-220 VAC
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Protection | IP 67
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Display unit | 2 line LCD
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | Flow Meter |  |  | Cable length | Head-Mount
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Manufacturer – | Endress + Hauser
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Serial No. | 72001520000
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Working Temperature | (-29 to 60˚)
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Model | 10P80-EL0A1AA0B4AA
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Range | NA
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | working pressure | 285 PSI
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Nominal Dia ( MM) | 80 MM
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Calibration Range | NA
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Accuracy | 0.0015
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Material Body | Sensor Material
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | 316 S1 | Repeatability
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Liner | PTFE
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Output | 4-20 mA
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Comunication | HART
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Display Version | E- Series
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Power Supply | 90-220 VAC
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Protection | IP 67
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Display unit | 2 line LCD
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | Flow Meter |  |  | Cable length | Head-Mount
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Manufacturer – | Rosemount
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Serial No. | 13140877
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Working Temperature | (-29 to 60˚)
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Model | 8705TSA020C1W0B3
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Range | NA
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | working pressure | 285 PSI
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Nominal Dia ( MM) | 50 MM
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Calibration Range | NA
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Accuracy | 0.0015
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Material Body | Sensor Material
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | 316 S1 | Repeatability
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Liner | PTFE
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Output | 4-20 mA
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Comunication | HART
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Display Version | E- Series
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Power Supply | 90-220 VAC
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Protection | IP 67
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Display unit | 2 line LCD
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | FLOW METER |  |  | Cable length | Head-Mount
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Manufacturer – | Rosemount
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Serial No. | 13140876
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Working Temperature | (-29 to 60˚)
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Model | 8705TSA020C1W0B3
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Range | NA
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | working pressure | 285 PSI
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Nominal Dia ( MM) | 50 MM
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Calibration Range | NA
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Accuracy | 0.0015
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Material Body | Sensor Material
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | 316 S1 | Repeatability
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Liner | PTFE
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Output | 4-20 mA
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Comunication | HART
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Display Version | E- Series
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Power Supply | 90-220 VAC
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Protection | IP 67
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Display unit | 2 line LCD
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | FLOW METER |  |  | Cable length | Head-Mount
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Manufacturer – | Rosemount
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Serial No. | Working Temperature
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Model | 8705TSA020C1W0B3
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Range | NA
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | working pressure | 285 PSI
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Nominal Dia ( MM) | 50 MM
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Calibration Range | NA
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Accuracy | 0.0015
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Material Body | Sensor Material
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | 316 S1 | Repeatability
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Liner | PTFE
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Output | 4-20 mA
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Comunication | HART
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Display Version | E- Series
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Power Supply | 90-220 VAC
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Protection | IP 67
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Display unit | 2 line LCD
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | FLOW METER |  |  | Cable length | Head-Mount
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Manufacturer – | Rosemount
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Serial No. | 6205890
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Working Temperature | (-29 to 60˚)
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Model | 8705TSA040C1W0B3
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Range | NA
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | working pressure | 285 PSI
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Nominal Dia ( MM) | 100 MM
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Calibration Range | NA
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Accuracy | 0.0015
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Material Body | Sensor Material
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | 316 S1 | Repeatability
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Liner | PTFE
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Output | 4-20 mA
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Comunication | HART
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Display Version | E- Series
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Power Supply | 90-220 VAC
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Protection | IP 67
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Display unit | 2 line LCD
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | FLOW METER |  |  | Cable length | Head-Mount
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Manufacturer – | Rosemount
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Serial No. | Working Temperature
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Model | 8705TSA040C1W0B3
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Range | NA
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | working pressure | 285 PSI
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Nominal Dia ( MM) | 100 MM
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Calibration Range | NA
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Accuracy | 0.0015
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Material Body | Sensor Material
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | 316 S1 | Repeatability
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Liner | PTFE
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Output | 4-20 mA
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Comunication | HART
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Display Version | E- Series
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Power Supply | 90-220 VAC
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Protection | IP 67
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Display unit | 2 line LCD
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | FLOW METER |  |  | Cable length | Head-Mount
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Manufacturer – | Rosemount
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Serial No. | 6205904
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Working Temperature | (-29 to 60˚)
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Model | 8705TSA030C1W0B3
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Range | NA
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | working pressure | 285 PSI
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Nominal Dia ( MM) | 100 MM
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Calibration Range | NA
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Accuracy | 0.0015
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Material Body | Sensor Material
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | 316 S1 | Repeatability
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Liner | PTFE
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Output | 4-20 mA
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Comunication | HART
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Display Version | E- Series
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Power Supply | 90-220 VAC
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Protection | IP 67
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Display unit | 2 line LCD
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | FLOW METER |  |  | Cable length | Head-Mount
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Manufacturer – | ABB
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Serial No. | Working Temperature
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Model | FET3211B0A1B1C1M5
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Range | NA
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | working pressure | 285 PSI
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Nominal Dia ( MM) | 25 MM
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Calibration Range | NA
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Accuracy | 0.0015
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Material Body | Sensor Material
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | 316 S1 | Repeatability
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Liner | PTFE
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Output | 4-20 mA
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Comunication | HART
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Display Version | Power Supply
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | 90-220 VAC | Protection
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | Flow Meter |  |  | Display unit | Cable length
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Manufacturer – | ABB
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Serial No. | Working Temperature
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Model | FET3211B0A1B1C1M5
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Range | NA
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | working pressure | 285 PSI
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Nominal Dia ( MM) | 25 MM
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Calibration Range | NA
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Accuracy | 0.0015
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Material Body | Sensor Material
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | 316 S1 | Repeatability
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Liner | PTFE
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Output | 4-20 mA
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Comunication | HART
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Display Version | E- Series
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Power Supply | 90-220 VAC
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Protection | IP 67
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Display unit | 2 line LCD
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | Flow Meter |  |  | Cable length | 10 MTR
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Manufacturer – | ABB
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Serial No. | Working Temperature
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Model | FET3211B0A1B1C1M5
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Range | NA
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | working pressure | 285 PSI
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Nominal Dia ( MM) | 15 MM
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Calibration Range | NA
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Accuracy | 0.0015
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Material Body | Sensor Material
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | 316 S1 | Repeatability
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Liner | PTFE
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Output | 4-20 mA
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Comunication | HART
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Display Version | Power Supply
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | 90-220 VAC | Protection
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | Flow Meter |  |  | Display unit | Cable length
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Manufacturer – | ABB
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Serial No. | Working Temperature
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Model | FET3211B0A1B1C1M5
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Range | NA
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | working pressure | 285 PSI
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Nominal Dia ( MM) | 15 MM
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Calibration Range | NA
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Accuracy | 0.0015
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Material Body | Sensor Material
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | 316 S1 | Repeatability
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Liner | PTFE
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Output | 4-20 mA
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Comunication | HART
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Display Version | Power Supply
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | 90-220 VAC | Protection
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | Flow Meter |  |  | Display unit | Cable length
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Manufacturer – | ABB
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Serial No. | Working Temperature
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Model | FET3211B0A1B1C1M5
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Range | NA
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | working pressure | 285 PSI
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Nominal Dia ( MM) | 15 MM
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Calibration Range | NA
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Accuracy | 0.0015
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Material Body | Sensor Material
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | 316 S1 | Repeatability
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Liner | PTFE
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Output | 4-20 mA
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Comunication | HART
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Display Version | Power Supply
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | 90-220 VAC | Protection
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | Flow Meter |  |  | Display unit | Cable length
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Manufacturer – | ABB
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Serial No. | Working Temperature
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Model | FET3211B0A1B1C1M5
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Range | NA
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | working pressure | 285 PSI
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Nominal Dia ( MM) | 25 MM
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Calibration Range | NA
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Accuracy | 0.0015
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Material Body | Sensor Material
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | 316 S1 | Repeatability
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Liner | PTFE
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Output | 4-20 mA
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Comunication | HART
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Display Version | Power Supply
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | 90-220 VAC | Protection
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | Flow Meter |  |  | Display unit | Cable length
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | Manufacturer – | ABB
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | Serial No. | Working Temperature
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | Model | Range
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | 0-30 M3/HR. | working pressure
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | Nominal Dia ( MM) | Calibration Range
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | NA | Accuracy
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | Material Body | Sensor Material
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | 316 S1 | Repeatability
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | Liner | PTFE
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | Output | 4-20 mA
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | Comunication | HART
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | Display Version | Power Supply
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | 90-220 VAC | Protection
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | FLOW METER |  |  | Display unit | Cable length
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Make/Model | ABB/PM866
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Communication Module(PROFIBUS DP) | CI854A
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Communication Module (RS-232C) | CI853
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Rechargeable Battery Unit | SB822
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SG15050D64,SG15050D65
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SI151481473/480/544
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SE180100YP
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SG15071D86,DD1
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Base Plate (Ethernet) | 0000231f82f8,0000231f82fa
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Protocol | DP-V1 (PA via Linking Device)
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Protocol | MODBUS RTU master, COMLI master/ slave, Siemens 3964R master, User defined protocols
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Rated output voltage/Max. output current/Max. ambi. temperature | 3.6 V/0.05A/60°C
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Memory | 4 MB flash PROM (firmware storage), 64 MB of SDRAM.
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Master or slave | Master
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Master or slave | Master/ slave
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions | W 85.8 x H 136 x D 58.5 mm
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power Dissipation | 5.1 W typical, 8.6 W typical (incl. full supply to ModuleBus and CEXBus.
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Number of channels | 2
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Number of channels | 2
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Accolade Acon 01-45 Converter (K3/K4) | ACON-01-45
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Current Consumption | 210 mA typical (360 mA max.)
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Max units on CEX bus | 12
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Max units on CEX bus | 12
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | 1505004/1505005
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power Input Connector | Four pin, screw connector L+, L–, SA and SB.
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Transmission speed | 9.6 - 12,000 kbit/s
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Transmission speed | 75 - 19 200 b/s
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power | 24 VDC
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 13.5cm x 11.9cm x 18.6cm
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Module & cable redundancy | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Module & cable redundancy | NO
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | OR-ing Diode unit | P-OR-24-10
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Clock Frequency | 133 MHz
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Connectors | DB female (9-pin )
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Connectors | RJ-45 female (8-pin)
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | 3586
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power Supply | 24 V DC (19.2-30 V DC)
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 100 mA
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Input | 24 V DC supply-2nos.(standard)
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Built-in back-up battery | Lithium, 3.6 V
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions | W 58 x H 186 x D 135 mm
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions | W 58 x H 186 x D 135 mm
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Output | 1 N/C Relay contact,rated 5 amps @ 24VDC/230AC incase failure of the i/p power supply
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | PowerCat 6A Shielded Patch Cord | Molex power cat 6 upt patch cord lsoh IEC-60332-1 4 PR 24 AWB TIA 568-C2
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Profibus cable | Belden YJ57083, 22 AWG X 2 core
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | PSU- 1 & 2 (Cosel) | LFA240-24
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | PSPL/13-14/07307,07333
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | CONTROLLER PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Make/Model | ABB/PM866
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Communication Module(PROFIBUS DP) | CI854A
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Rechargeable Battery Unit | SB822
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SG15121204,SG151200
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SI151481533,467,555
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SG15071D84,SG15071D9D
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Base Plate (Ethernet) | 0000231f8c74,0000231f8c5c
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Protocol | DP-V1 (PA via Linking Device)
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Rated output voltage/Max. output current/Max. ambi. temperature | 3.6 V/0.05A/60°C
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Memory | 4 MB flash PROM (firmware storage), 64 MB of SDRAM.
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Master or slave | Master
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions | W 85.8 x H 136 x D 58.5 mm
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power Dissipation | 5.1 W typical, 8.6 W typical (incl. full supply to ModuleBus and CEXBus.
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Number of channels | 2
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Accolade Acon 01-45 Converter (K1,K2,K3) | ACON-01-45
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Current Consumption | 210 mA typical (360 mA max.)
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Max units on CEX bus | 12
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | 1402001/1402024/1505007
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power Input Connector | Four pin, screw connector L+, L–, SA and SB.
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Transmission speed | 9.6 - 12,000 kbit/s
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power | 24 VDC
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 13.5cm x 11.9cm x 18.6cm
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Module & cable redundancy | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | OR-ing Diode unit(Model) | P-OR-24-10
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Clock Frequency | 133 MHz
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Connectors | DB female (9-pin )
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | 3558
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power supply | 24 V DC (19.2-30 V DC)
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Input | 24 V DC supply-2nos.(standard)
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Built-in back-up battery | Lithium, 3.6 V
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions | W 58 x H 186 x D 135 mm
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Output | 1 N/C Relay contact,rated 5 amps @ 24VDC/230AC incase failure of the i/p power supply
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | PowerCat 6A Shielded Patch Cord | Molex power cat 6 upt patch cord lsoh IEC-60332-1 4 PR 24 AWB TIA 568-C2
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Profibus cable | Belden YJ57083, 22 AWG X 2 core
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | PSU- 1 & 2 (Cosel) | LFA240-24
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | PSPL/14-15/965,PSPL/14-15/959
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | CONTROLLER PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Make/Model | ABB/PM866
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Communication Module(PROFIBUS DP) | CI854A
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Communication Module (RS-232 C) | CI853
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Rechargeable Battery Unit | SB822
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SG151211E0,SG15121203
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SI151481557,SI151481454,SI151481500
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SE150100ZB
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SG15071DD3,SG15071D71
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Base Plate (Ethernet) | Protocol
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | DP-V1 (PA via Linking Device) | Protocol
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | MODBUS RTU master, COMLI master/ slave, Siemens 3964R master, User defined protocols | Rated output voltage/Max. output current/Max. ambi. temperature
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | 3.6 V/0.05A/60°C | Relative humidity
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Memory | 4 MB flash PROM (firmware storage), 64 MB of SDRAM.
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Master or Slave | Master
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Master or slave | Master/ slave
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions | W 85.8 x H 136 x D 58.5 mm
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power Dissipation | 5.1 W typical, 8.6 W typical (incl. full supply to ModuleBus and CEXBus.
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Number of channels | 2
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Number of channels | 2
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Accolade Acon 01-45 Converter (K1/K2) | ACON-01-45
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Current Consumption | 210 mA typical (360 mA max.)
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Max units on CEX bus | 12
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Max units on CEX bus | 12
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | 1505009,
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power Input Connector | Four pin, screw connector L+, L–, SA and SB.
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Transmission speed | 9.6 - 12,000 kbit/s
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Transmission speed | 75 - 19 200 b/s
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power | 24 VDC
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 13.5cm x 11.9cm x 18.6cm
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Module & cable redundancy | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Module & cable redundancy | NO
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | OR-ing Diode unit | P-OR-24-10
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Clock Frequency | 133 MHz
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Connectors | DB female (9-pin )
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Connectors | RJ-45 female (8-pin)
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | 3580
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power Supply | 24 V DC (19.2-30 V DC)
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | 24 V Current consumption | typ 190 mA
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 100 mA
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Input | 24 V DC supply-2nos.(standard)
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Built-in Back-up Battery | Lithium, 3.6 V
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions | W 58 x H 186 x D 135 mm
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions | W 58 x H 186 x D 135 mm
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Output | 1 N/C Relay contact,rated 5 amps @ 24VDC/230AC incase failure of the i/p power supply
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | CISCO Switch 1 & 2 | SF300-24, 24-port 10/100 manged switch
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Profibus Cable | Belden YJ57083, 22 AWG X 2 core
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | PSU- 1 & 2 (Cosel) | LFA240-24
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | PowerCat 6A Shielded Patch Cord | Molex power cat 6 upt patch cord lsoh IEC-60332-1 4 PR 24 AWB TIA 568-C2
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | PSU- 3 & 4 (Cosel) | PLA600F-24-W
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | CONTROLLER PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Make/Model | ABB/PM866
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Communication Module(PROFIBUS DP) | CI854A
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Communication Module (RS-232 C) | CI853
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Rechargeable Battery Unit | SB822
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SG15111DAB,SG15111DAF
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SI151481535,SI151481526
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SE150100YE,SE150100YV
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | SG15071D7A,SG15071DB1
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Base Plate (Ethernet) | 0000231189b0,0000231189b8
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Protocol | DP-V1 (PA via Linking Device)
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Protocol | MODBUS RTU master, COMLI master/ slave, Siemens 3964R master, User defined protocols
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Rated output voltage/Max. output current/Max. ambi. temperature | 3.6 V/0.05A/60°C
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Memory | 4 MB flash PROM (firmware storage), 64 MB of SDRAM.
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Master or slave | Master
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Master or slave | Master/ slave
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions | W 85.8 x H 136 x D 58.5 mm
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power Dissipation | 5.1 W typical, 8.6 W typical (incl. full supply to ModuleBus and CEXBus.
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Number of channels | 2
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Number of channels | 2
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Accolade Acon 01-45 Converter (K1,K2,K3,K4) | ACON-01-45
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Current Consumption | 210 mA typical (360 mA max.)
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Max units on CEX bus | 12
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Max units on CEX bus | 12
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | 1207033/1505014/1505006/1505015
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power Input Connector | Four pin, screw connector L+, L–, SA and SB.
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Transmission speed | 9.6 - 12,000 kbit/s
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Transmission speed | 75 - 19 200 b/s
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power | 24 VDC
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 13.5cm x 11.9cm x 18.6cm
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Module & cable redundancy | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Module & cable redundancy | NO
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | OR-ing Diode unit | P-OR-24-10,P-OR-24-70
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Clock Frequency | 133 MHz
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Connectors | DB female (9-pin )
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Connectors | RJ-45 female (8-pin)
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | 3585139
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Power supply | 24 V DC (19.2-30 V DC)
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 100 mA
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Input | 24 V DC supply-2nos.(standard)
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Built-in back-up battery | Lithium, 3.6 V
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions | W 58 x H 186 x D 135 mm
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Dimensions | W 58 x H 186 x D 135 mm
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Output | 1 N/C Relay contact,rated 5 amps @ 24VDC/230AC incase failure of the i/p power supply
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | CISCO Switch 05 &06 | SF300-24, 24-port 10/100 manged switch
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Profibus cable | Belden YJ57083, 22 AWG X 2 core
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | PSU- 1 & 2 (Cosel), PSU- 3 & 4 (Cosel) | LFA240-24,PBA1500F-24
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | PowerCat 6A Shielded Patch Cord | Molex power cat 6 upt patch cord lsoh IEC-60332-1 4 PR 24 AWB TIA 568-C2
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | Serial No. | PSPL/13-14/07332,PSPL/13-14/07312 & 2453135TR,2453135TR
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | CONTROLLER PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AI Module | AI810
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AO module | AO810V2
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | PSU-3 & PSU-4 Model(cosel) | PBA1500F-24
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14460386(P),SI14480755(R)
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N2AI810-1,2,3,4,5,6
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N2AO810-1,2,3,4
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Sr. No. | PSPL/14-15/917, PSPL/14-15/914
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 2nd Row Serial No. | SI14480735(P),SI14480760(R)
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N3AI810-1,2,3,4,5,6
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N3AO810-1,2,3,4
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input Voltage | AC85 - 264V 1Φ or DC120 - 370V
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 3rd Row Serial No. | SI14460387(P),SI14480781(R)
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N4AI810-1,2,3,4,5,6,7
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N4AO810-1,2,3,
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output Voltage/Current | 24V 65A ACIN 100V,24V 70 (105) A ACIN 200V
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8/unipolar single ended/0 to 20 mA,0 to 10 V
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8/unipolar single ended/0 to 20 mA, 4 to 20 mA
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Adjustable Output Voltage Range | 16.50 - 26.40V
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Resolution/input impedance | 12bit/290komh(voltage input)/230-275k omh(current input)
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Resolution/current limiting | 14bit/short circuit proof current limited output
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Over Current Protection | Works over 105% of rated current or 101% of peak current and recovers automatically
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/-5%/+15%/max 0.1%
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/-15%/+15%/max 0.1% at 0-500 ohms(current)
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Overvoltage Protection | Vo+4.8 - 9.6V
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input filter(rise time 0-90%)/update cycle time | 140ms/08ms
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Rise time/update cycle time | 0.35ms(PL=500 omhs)/<=2ms
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (WxHxD) | 178x61x268mm
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meters
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OR-ING DIODE UNIT (Paramount) | P-0R-24-70
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Max input voltage(non destructive) | 30V d.c
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Max input voltage(non destructive) | typ 100 mA
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Sr. No. | 184
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/40mA/0mA
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | Max 70mA/0mA/245mA
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input | 220V DC supply -2nos (standard), 48V DC supply -2nos (standard)
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 1.5W
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.3 W
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input & Output power supply | 1 green LED for each Power Supply and 1 green LED for output
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | output | 1N/C Relay Contact Rated 5Amps @ 24VDC/230VAC incase of failure of any one the input power supply.
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AI Module | AI810
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AO module | AO810V2
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AI RTD module | AI830A
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14480734(P),SI14480388(R)
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N5AI810-1,2,3,4,5,6 ,7
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N5AO810-1,2,3
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | Temperature, Storage
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 2nd Row Serial No. | SI14480759(P),SI14480725(R)
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N6AI810-1,2,3,4,5
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | C1N6AI830-1,2,3,4,5 | Relative humidity
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 3rd Row Serial No. | SI14480728(P),SI14480744(R)
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N7AI810-1,2,3,4,5
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | C1N7AI830-1,2,3,4,5 | Emitted noise
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 4th Row Serial No. | SI14480669(P),SI14480758(R)
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N8AI810-1,2,3,4,5
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8/unipolar single ended/0 to 20 mA,0 to 10 V
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal specification | 8/0 to 20 mA, 4 to 20 Ma
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8ch/3-wire RTD:Pt100,Cu10,Ni100 and resistive potentiometer
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Resolution/input impedance | 12bit/290komh(voltage input)/230-275k omh(current input)
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Resolution/current limiting | 14bit/short circuit proof current limited output
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Temperature changes
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/-5%/+15%/max 0.1%
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/-15%/+15%/max 0.1% at 0-500 ohms(current)
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/error dependent of the field cable resistance
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input filter(rise time 0-90%)/update cycle time | 140ms/08ms
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Rise time/update cycle time | 0.35ms(PL=500 omhs)/<=2ms
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Rise time/update cycle time | 0.35ms(PL=500 omhs)/150+90*(number of active ch.)ms
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meters
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meters
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Max input voltage(non destructive) | 30V d.c
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Max input voltage(non destructive) | typ 100 mA
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | CMRR,50H,60HZ | >120dB(at 10 omhs load)
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/40mA/0mA
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | Max 70mA/0mA/245mA
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | Max 70mA/50mA/0mA
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 1.5W
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.3 W
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 1.6 W
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DI Module | DI818
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | PSU-5 & PSU-6(COSEL) | PLA600F-24-W
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14480736(P),SI14480761(R)
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N9DI818-1,2,3,4,5,6 ,7,8,9,10
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | O/P VOLTAGE[V] | 24V
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/current sinking/24 V d.c.
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | O/C CURRENT[A] | 25A
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"0" | mins 30 to 05 volts
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OUTPUT VOLTAGE ADJUSTMENT RANGE | 21.60 to 26.40 V
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"1" | 11 to 30 volts
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OVERCURRENT PROTECTION | Works over 105% of rating and recovers automatically
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input impedance | 5.6 k omhs
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OVERVOLTAGE PROTECTION[V] | 27.60 to 33.60
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation | Groupwise isolated from ground,group of 16 channels
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Power Doide Unit(model) | P-OR-24-40
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Filter timers (digital selectable) | 2,4,8,16 ms
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input | 24 Vdc supply-2nos(standard)
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output Current/Voltage | 40Amps/24VDC
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input & Output power supply | 1 green LED for each Power Supply and 1 green LED for output
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/25mA
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Shavison SMPS(Model)/Sr. NO | G31-250-24/2K16/30
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 3.1 W
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input Voltage/Current | 230VAC,2.50A,50HZ
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output Voltage/Current | 24V/10A
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DI Module | DI818
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14460375(P),SI14480650(R)
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N10DI818-1,2,3,4,5,6 ,7,8,9,10
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/current sinking/24 V d.c.
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"0" | mins 30 to 05 volts
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"1" | 11 to 30 volts
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input impedance | 5.6 k omhs
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground,group of 16 channels
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | filter timers (digital selectable) | 2,4,8,16 ms
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/25mA
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 3.1 W
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DI Module | DI818
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14460483(P),SI14460742(R)
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N11DI818-1,2,3,4,5,6 ,7,8,9,10
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/current sinking/24 V d.c.
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"0" | mins 30 to 05 volts
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"1" | 11 to 30 volts
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input impedance | 5.6 k omhs
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground,group of 16 channels
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | filter timers (digital selectable) | 2,4,8,16 ms
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/25mA
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 3.1 W
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DO Module | DO818
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14480733(P),SI14480757(R)
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N12DO818-1,2,3,4,5,6 ,7,8,9,10
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/Current sourcing, current limiting/24 V d.c. (12 - 32 V d.c.), 0.5 A
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output load | < 0.32 Ω
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/40 mA
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.8 W
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DO Module | DO818
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14480656(P),SI14460416(R)
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C1N13DO818-1,2,3,4,5,6 ,7,8,9,10
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/Current sourcing, current limiting/24 V d.c. (12 - 32 V d.c.), 0.5 A
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output load | < 0.32 Ω
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/40 mA
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.8 W
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AI Module | AI810
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AO module | AO810V2
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI1450119586(P),SI14460399(R)
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N2AI810-1,2,3,4,5,6
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N2AO810-1,2,3,4
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 2nd Row Serial No. | SI14460353(P),SI14460359(R)
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N3AI810-1,2,3,4,5,6
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N3AO810-1,2,3,4
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 3rd Row Serial No. | SI14480655(P),SI14521857(R)
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N4AI810-1,2,3,4,5,6,7
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N4AO810-1,2,3
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8/unipolar single ended/0 to 20 mA,0 to 10 V
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8/unipolar single ended/0 to 20 mA, 4 to 20 mA
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Resolution/input impedance | 12bit/290komh(voltage input)/230-275k omh(current input)
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Resolution/current limiting | 14bit/short circuit proof current limited output
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/-5%/+15%/max 0.1%
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/-15%/+15%/max 0.1% at 0-500 ohms(current)
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input filter(rise time 0-90%)/update cycle time | 140ms/08ms
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Rise time/update cycle time | 0.35ms(PL=500 omhs)/<=2ms
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meters
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Max input voltage(non destructive) | 30V d.c
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Max input voltage(non destructive) | typ 100 mA
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/40mA/0mA
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | Max 70mA/0mA/245mA
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 1.5W
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.3 W
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AI Module | AI810
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AO module | AO810V2
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AI RTD module | AI830A
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14460423(P),SI14460355(R)
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N5AI810-1,2,3,4,5,6 ,7
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N5AO810-1,2,3
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | Temperature, Storage
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 2nd Row Serial No. | SI14460469(P),SI14480765(R)
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N6AI810-1,2,3,4,5
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | C2N6AI830-1,2,3,4,5 | Relative humidity
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 3rd Row Serial No. | SI14460389(P),SI14480738(R)
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N7AI810-1,2,3,4,5
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | C2N7AI830-1,2,3,4,5 | Emitted noise
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 4th Row Serial No. | SI14460462(P),SI14460457(R)
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N8AI810-1,2,3,4,5
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8/unipolar single ended/0 to 20 mA,0 to 10 V
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal specification | 8/0 to 20 mA, 4 to 20 Ma
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8ch/3-wire RTD:Pt100,Cu10,Ni100 and resistive potentiometer
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Resolution/input impedance | 12bit/290komh(voltage input)/230-275k omh(current input)
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Resolution/current limiting | 14bit/short circuit proof current limited output
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Temperature changes
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/-5%/+15%/max 0.1%
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/-15%/+15%/max 0.1% at 0-500 ohms(current)
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/error dependent of the field cable resistance
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input filter(rise time 0-90%)/update cycle time | 140ms/08ms
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Rise time/update cycle time | 0.35ms(PL=500 omhs)/<=2ms
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Rise time/update cycle time | 0.35ms(PL=500 omhs)/150+90*(number of active ch.)ms
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meters
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meters
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Max input voltage(non destructive) | 30V d.c
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Max input voltage(non destructive) | typ 100 mA
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | CMRR,50H,60HZ | >120dB(at 10 omhs load)
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/40mA/0mA
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | Max 70mA/0mA/245mA
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | Max 70mA/50mA/0mA
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 1.5W
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.3 W
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 1.6 W
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DI Module | DI818
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | PSU-5 & PSU-6(COSEL) | PLA600F-24-W
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14480795(P),SI14460422(R)
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N9DI818-1,2,3,4,5,6 ,7,8,9,10
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | O/P VOLTAGE[V] | 24V
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/current sinking/24 V d.c.
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | O/P CURRENT[A] | 25A
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"0" | mins 30 to 05 volts
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OUTPUT VOLTAGE ADJUSTMENT RANGE | 21.60 to 26.40 V
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"1" | 11 to 30 volts
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OVERCURRENT PROTECTION | Works over 105% of rating and recovers automatically
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input impedance | 5.6 k omhs
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OVERVOLTAGE PROTECTION[V] | 27.60 to 33.60
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground,group of 16 channels
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Power Doide Unit(model)/Sr. no. | P-OR-24-40/1040
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | filter timers (digital selectable) | 2,4,8,16 ms
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input | 24 Vdc supply-2nos(standard)
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output Current/Voltage | 40Amps/24VDC
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input & Output power supply | 1 green LED for each Power Supply and 1 green LED for output
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/25mA
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 3.1 W
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DI Module | DI818
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14460376(P),SI14480724(R)
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N10DI818-1,2,3,4,5,6 ,7,8,9,10
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/current sinking/24 V d.c.
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"0" | mins 30 to 05 volts
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"1" | 11 to 30 volts
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input impedance | 5.6 k omhs
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground,group of 16 channels
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | filter timers (digital selectable) | 2,4,8,16 ms
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/25mA
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 3.1 W
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DO Module | D0818
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14460390(P),SI14460852(R)
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N11DO818-1,2,3,4,5,6 ,7,8,9,10
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/Current sourcing, current limiting/24 V d.c. (12 - 32 V d.c.), 0.5 A
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output load | < 0.32 Ω
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/40 mA
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.8 W
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DO Module | DO818
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14460403(P),SI14460450(R)
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N12DO818-1,2,3,4,5,6 ,7,8,9,10
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/Current sourcing, current limiting/24 V d.c. (12 - 32 V d.c.), 0.5 A
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output load | < 0.32 Ω
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/40 mA
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Dimensions (LxWxH) | 96mm x 54mm x 119mm
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.8 W
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Product Weight | 0.2 kg
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DO Module | DO818
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Shavison SMPS(Model) | G31-250-24
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14460432(P),SI14522203(R)
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N13D0818-1,2,3,4,5,6
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Sr. No | 2K16/31
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/Current sourcing, current limiting/24 V d.c. (12 - 32 V d.c.), 0.5 A
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input Voltage/Current | 230VAC
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output load | < 0.32 Ω
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input Current | 10A
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Friquency | 50HZ
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output Voltage | 24V
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output Current | 10A
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/40 mA
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.8 W
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AI Module | AI810
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AI module | AI830A
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AO module | AO810V2
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14522186(P),SI14480749(R)
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C3N2AI810-1,2,3,4,5
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C3N2AI830-1,2,3
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C3N2AO810-01,2
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 2nd Row Serial No. | SI14460379(P),SI14460468(R)
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C3N3AI810-1,2,3,4
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C3N3AI830-1,2,3,
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C3N3AO810-01,2,3
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 3rd Row Serial No. | SI14460396(P),SI14460360(R)
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C3N4AI810-1,2,3,4,5
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C3N4AI830-1,2,3,4
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8/unipolar single ended/0 to 20 mA,0 to 10 V
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8ch/3-wire RTD:Pt100,Cu10,Ni100 and resistive potentiometer
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8/unipolar single ended/0 to 20 mA, 4 to 20 mA
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Resolution/input impedance | 12bit/290komh(voltage input)/230-275k omh(current input)
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Resolution/current limiting
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 14bit/short circuit proof current limited output | Temperature changes
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/-5%/+15%/max 0.1%
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/error dependent of the field cable resistance
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/-15%/+15%/max 0.1% at 0-500 ohms(current)
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input filter(rise time 0-90%)/update cycle time | 140ms/08ms
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Rise time/update cycle time | 0.35ms(PL=500 omhs)/150+90*(number of active ch.)ms
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Rise time/update cycle time | 0.35ms(PL=500 omhs)/<=2ms
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meters
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meters
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Max input voltage(non destructive) | 30V d.c
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | CMRR,50H,60HZ | >120dB(at 10 omhs load)
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Max input voltage(non destructive) | typ 100 mA
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/40mA/0mA
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | Max 70mA/50mA/0mA
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | Max 70mA/0mA/245mA
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 1.5W
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 1.6 W
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.3 W
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DI Module | DI818
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | PSU-5 & PSU-6(COSEL) | PLA600F-24-W
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14522193(P),SI14522207(R)
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C3N5DI818-1,2,3,4,5,6 ,7,8,9
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Sr. No. | PS-PL-13-14/07327, PS-PL-13-14/07310
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/current sinking/24 V d.c.
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | O/P VOLTAGE[V] | 24V
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"0" | mins 30 to 05 volts
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | O/P CURRENT[A] | 10A
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"1" | 11 to 30 volts
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OUTPUT VOLTAGE ADJUSTMENT RANGE | 21.60 to 26.40 V
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input impedance | 5.6 k omhs
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OVERCURRENT PROTECTION | Works over 105% of rating and recovers automatically
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground,group of 16 channels
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OVERVOLTAGE PROTECTION[V] | 27.60 to 33.60
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | filter timers (digital selectable) | 2,4,8,16 ms
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Power Doide Unit(model)/Sr. no. | P-OR-24-40/8110
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input | 24 Vdc supply-2nos(standard)
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output Current/Voltage | 40Amps/24VDC
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/25mA
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input & Output power supply | 1 green LED for each Power Supply and 1 green LED for output
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 3.1 W
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DO Module | DO818
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14522180(P),SI14460381(R)
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C2N9DO818-1,2,3,4,5,6 ,7
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/Current sourcing, current limiting/24 V d.c. (12 - 32 V d.c.), 0.5 A
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output load | < 0.32 Ω
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/40 mA
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.8 W
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AI Module | AI810
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AI module | AI830A
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | AO module | AO810V2
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14522205(P),SI14522190(R)
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N2AI810-1,2,3,4,5
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N2AI830-1,2,3
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N2AO810-1,2
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 2nd Row Serial No. | SI14480737(P),SI14460460(R)
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N3AI810-1,2,3,4,5
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N3AI830-1,2,3
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N3AO810-1,2
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Relative humidity | 5 to 95 %, non-condensing
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 3rd Row Serial No. | SI14480716(P),SI14480743(R)
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N4AI810-1,2,3,4,5
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N4AI830-1,2,3
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N4AO810-1,2
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Emitted noise | < 55 dB (A)
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 4thRow Serial No. | SI14480654(P),SI14460433(R)
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N5AI810-1,2,3,4
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N5AI830-1,2,3,4
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N5AO810-1,2
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8/unipolar single ended/0 to 20 mA,0 to 10 V
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8ch/3-wire RTD:Pt100,Cu10,Ni100 and resistive potentiometer
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 8/unipolar single ended/0 to 20 mA, 4 to 20 mA
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Resolution/input impedance | 12bit/290komh(voltage input)/230-275k omh(current input)
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Resolution/current limiting
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 14bit/short circuit proof current limited output | Temperature changes
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/-5%/+15%/max 0.1%
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/error dependent of the field cable resistance
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/under range/over range/error | Groupwise isolated from ground/-15%/+15%/max 0.1% at 0-500 ohms(current)
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input filter(rise time 0-90%)/update cycle time | 140ms/08ms
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Rise time/update cycle time | 0.35ms(PL=500 omhs)/150+90*(number of active ch.)ms
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Rise time/update cycle time | 0.35ms(PL=500 omhs)/<=2ms
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meters
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meters
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Max input voltage(non destructive) | 30V d.c
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | CMRR,50H,60HZ | >120dB(at 10 omhs load)
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Max input voltage(non destructive) | typ 100 mA
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/40mA/0mA
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | Max 70mA/50mA/0mA
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | Max 70mA/0mA/245mA
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 1.5W
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 1.6 W
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.3 W
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DI Module | DI818
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | PSU-5 & PSU-6(COSEL) | PLA600F-24-W
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14460451(P),SI14460456(R)
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N6DI818-1,2,3,4,5,6,7,8,9,10
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Sr. No. | PS-PL-13-14/07327, PS-PL-13-14/07310
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/current sinking/24 V d.c.
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 3.1 W
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | O/P VOLTAGE[V] | 24V
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"0" | mins 30 to 05 volts
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | O/P CURRENT[A] | 25A
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"1" | 11 to 30 volts
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OUTPUT VOLTAGE ADJUSTMENT RANGE | 21.60 to 26.40 V
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input impedance | 5.6 k omhs
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OVERCURRENT PROTECTION | Works over 105% of rating and recovers automatically
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground,group of 16 channels
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | OVERVOLTAGE PROTECTION[V] | 27.60 to 33.60
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | filter timers (digital selectable) | 2,4,8,16 ms
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Power Doide Unit(model)/Sr. no. | P-OR-24-40/1770
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input | 24 Vdc supply-2nos(standard)
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output Current/Voltage | 40Amps/24VDC
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/25mA
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Input & Output power supply | 1 green LED for each Power Supply and 1 green LED for output
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DI Module | DI818
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14522188(P),SI14521976(R)
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N7DI818-1,2,3,4,5,6,7,8,9
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/current sinking/24 V d.c.
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"0" | mins 30 to 05 volts
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input voltage range,"1" | 11 to 30 volts
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | input impedance | 5.6 k omhs
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground,group of 16 channels
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | filter timers (digital selectable) | 2,4,8,16 ms
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/25mA
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DO Module | DO818
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14522194(P),SI14501222(R)
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N8DO818-1,2,3,4,5,6,7,8,9,10,11
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/Current sourcing, current limiting/24 V d.c. (12 - 32 V d.c.), 0.5 A
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output load | < 0.32 Ω
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/40 mA
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.8 W
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Make/Model | ABB/CI840A
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | DO Module | DO818
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Operating | 5 to +55 °C
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 1st Row Serial No. | SI14522179(P),SI14521648(R)
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Serial No. | C4N9DO818-1,2,3,4,5,6,7,8,9,10,11
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature, Storage | (-25 to +70 °C)
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Communication protocol | PROFIBUS DP-IV
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Channels/signal type/signal specification | 32 ch/Current sourcing, current limiting/24 V d.c. (12 - 32 V d.c.), 0.5 A
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Master or slave | SLAVE
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Output load | < 0.32 Ω
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Line Redundancy | YES
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Isolation/ | Groupwise isolated from ground
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Pollution degree | Degree 2 according to IEC/EN 61131-2
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Hot Swap | Yes
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | maximum field cable length | 600 meter
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Altitude | 2000 m according to IEC/EN 61131-2
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Used together with HI controller | Yes
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | current limiting | Sensor power can be current limited by MTU
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Environmental conditions | Industrial
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | 24 V current consumption | typ 190 mA
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Current consuption +5V modulbus/+24V module bus/+24V external | 70mA/0mA/40 mA
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Corrosion protection | G3 compliant to ISA 71.04
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | power disipation | 2.8 W
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Electrical Safety | EN 50178, IEC 61131-2, UL 61010-1, UL 61010-2-201
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | rated insulation voltage/Dielectric test voltage | 50V/500V a.c.
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | Protection class | IP20 according to EN 60529, IEC 529
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | CLUSTER MODULE PRIMERY & REDUNDANT |  |  | ISA Secure certified | YES
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Make/Model | Siemens/SIMATIC S7-300
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Number of Inputs | 28 (24 Digital, 4 Analogue)
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | AI MODULE MAKE/ MODEL | SIEMENS/331-1KF02-0AB0/8 CH./12 Bit
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | DI MODULE/MAKE/ MODEL | SIEMENS/321-15L00-0A0/32 CH./12 Bit/24 V DC
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Temperature, Operating | 5 to +55 °C
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Interface | RS-485
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Dimensions | 120 x 125 x 130 mm
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | AO MODULE MAKE/ MODEL | SIEMENS/332-5HF00-0AB0/8 CH./12 Bit
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | DO MODULE MAKE/ MODEL | SIEMENS/322-1BL00-0AA0/32 CH./12 Bit/24 V DC
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Temperature, Storage | (-25 to +70 °C)
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Supply Voltage | 24 VDC
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Programming Language Used | CFC, FBD, Graph, HiGraph, Ladder Logic, SCL, STL
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | AO MODULE MAKE/ MODEL | SIEMENS/332-5HD01-0AB/4 CH./12 Bit
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Number of Digital Inputs/output card | 24,16
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Communication Port Type | RS485
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Number of Communication Ports | 1
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Number of Analogue Input/ Outputs | 05,02
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | BRS PLC PANEL |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL |  |  | Make/Model | WinPAC/WP-8147
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL |  |  | AI MODULE | 7017
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL |  |  | CPU/System Memory | PXA270 or compatible, 32-bit, 520 MHz/128 MB SDRAM
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL |  |  | DO MODULE | 7042 D
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL |  |  | Software | Embedded ISaGRAF Ver.3 SoftLogic (IEC 61131-3)
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL |  |  | DI MODULE | 7041 D
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL |  |  | Master or slave | Modbus RTU/TCP (Master, Slave)
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL |  |  | PROTECTION CHANNEL CARD | 8 AI X 4 DO
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL |  |  | Communication Interfaces | 2 x 10/100BASE-T Ethernet Ports,2 x Serial Ports (RS-232/485),1 x USB Port
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL |  |  | PROTECTION CHANNEL CARD | 4 AI X 8 DO
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL |  |  | Storage | 96 MB Flash, 4 GB microSD card (up to 32 GB)
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | SPRAY ENGINEERING PANEL |  |  | PROTECTION CHANNEL CARD | 6 AI X 6 DO
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | ALLEN BRADLLY CONTROLLER |  |  | Make/Model | ALLEN-BRADLEY
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | ALLEN BRADLLY CONTROLLER |  |  | POWER SUPPLY MAKE/MODEL | ALLEN BRADLLEY/1769-PA4
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | ALLEN BRADLLY CONTROLLER |  |  | Serial No. | L36ERM
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | ALLEN BRADLLY CONTROLLER |  |  | POWER SUPPLY MAKE/MODEL | ALLEN BRADLLEY/1606-XL5960EE
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | ALLEN BRADLLY CONTROLLER |  |  | DI MODULE/MODEL | ALLEN-BRADLEY/1769-1832
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | ALLEN BRADLLY CONTROLLER |  |  | 8-PORT ETHERNET SWITCH MAKE/MODEL | ALLEN BRADLLEY/stratuix-2000
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | ALLEN BRADLLY CONTROLLER |  |  | DO MODULE/MODEL | ALLEN-BRADLEY/1769-1F16C
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | ALLEN BRADLLY CONTROLLER |  |  | PLC Make/ Model | ALLEN BRADLLEY/Micrologix1401
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | ALLEN BRADLLY CONTROLLER |  |  | AO MODULE/MODEL | ALLEN-BRADLEY/1769-0F8C
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | ALLEN BRADLLY CONTROLLER |  |  | 8 chanel relay board | Shavison
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | Make/Model | ABB/PM 583
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | Programming Memory | 1MB
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | AI MODULE MAKE/ MODEL | ABB/AI523-1,2,3
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | ISOLATOR CONVERTER MAKE/MODEL | PEPPERL+FUCHS/KFD2-STC4-1
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | Temperature, Operating | 5 to +55 °C
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | Interface | RS232 / RS485 configurable, Programing,
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | Programming Language Used | FBD/LD/SFC
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | AO MODULE MAKE/ MODEL | ABB/AO523-1,2,3
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | ETHERNET MEDIA CONVERTOR MAKE/ MODEL | Santeleqip/SC09FENMSC2301
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | Temperature, Storage | (-25 to +70 °C)
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | Supply Voltage | 24 VDC
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | Number of Inputs | 320DI, 240DO/DC Local, max. 10 expansion modules
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | DO MODULE MAKE/ MODEL | ABB/DC523-1,2
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | Power Supply/MAKE | MEAN WELL/NES-350-24
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | Communication Port Type | RS485
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | RELAY BOARD | CONNECTWELL 8-CHANNEL
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | ABB CONTROLLER |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | Controller Make/Model | Siemens/SIMATIC S7-1200
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | CPU | CPU 1215C
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | AI MODULE MAKE/ MODEL | Siemens/SM1234
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | Temperature, Operating | 5 to +55 °C
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | Interface | 2 × PROFINET (Ethernet),
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | HMI Make/Model | Siemens/SIPLUS HMI TP700 Comfort GEA
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | AO MODULE MAKE/ MODEL | Siemens/SM1234
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | Temperature, Storage | (-25 to +70 °C)
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | Supply Voltage | 24 V DC
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | Power Supply/MAKE | Phoenix contact/TRIO-PS-2G/1AC/24DC/10
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | DO MODULE MAKE/ MODEL | Siemens/SM1222
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | Communication Port Type | 2 × USB 2.0, 1 × SD Card slot
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | AI MODULE MAKE/ MODEL | Siemens/SM1231 GEA LV
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | DI MODULE MAKE/ MODEL | Siemens/SM1221DC
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Decanter-1 PLC Panel |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | Controller Make/Model | Siemens/SIMATIC S7-1200
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | CPU | CPU 1215C
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | AI MODULE MAKE/ MODEL | Siemens/SM1234
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | Temperature, Operating | 5 to +55 °C
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | Interface | 2 × PROFINET (Ethernet),
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | HMI Make/Model | Siemens/SIPLUS HMI TP700 Comfort GEA
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | AO MODULE MAKE/ MODEL | Siemens/SM1234
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | Temperature, Storage | (-25 to +70 °C)
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | Supply Voltage | 24 V DC
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | Power Supply/MAKE | Phoenix contact/TRIO-PS-2G/1AC/24DC/10
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | DO MODULE MAKE/ MODEL | Siemens/SM1222
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | Vibration | 10 < f < 50 Hz: 0.0375 mm amplitude, 50 < f < 150 Hz: 0.5 g acceleration, 5 < f < 500 Hz: 0.2 g acceleration
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | Communication Port Type | 2 × USB 2.0, 1 × SD Card slot
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | AI MODULE MAKE/ MODEL | Siemens/SM1231 GEA LV
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | DI MODULE MAKE/ MODEL | Siemens/SM1221DC
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | PLC Panel |  |  | Temperature changes | 3 °C/minutes according to IEC/EN 61131-2
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | CPU Make | H.P.
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | I/P Address | 172.16.4.21
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | Model | HPE ProLiant DL20 Gen11
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | I/P Address | 172.17.4.21
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | Sr. No. | SGH434JTN5
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | Windows edition/Version | Windows Server 2022 standard /21H2
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | System Type | 64-bit Operating System,x64-based processor
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | Monitor Make/Model | H.P./HP Elite Display E231
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | Processor | Intel®Xeon® E E-2434 3.42Ghz 3.30GHz
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | Sr. No | 3CM42816HB
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | Storage | 2TB
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | Key Board Make | H.P.
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | RAM | 32 GB
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | Server-1 |  |  | Mouse Make | H.P.
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | CPU Make | H.P.
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | I/P Address | 172.16.4.22
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | Model | HPE ProLiant DL20 Gen11
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | I/P Address | 172.17.4.22
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | Sr. No. | Windows edition/Version
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | System Type | 64-bit Operating System,x64-based processor
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | Monitor Make/Model | H.P./HP Elite Display E231
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | Processor | Intel®Xeon® E E-2434 3.42Ghz 3.30GHz
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | Sr. No | 3CM42816HB
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | Storage | 2 TB
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | Key Board Make | H.P.
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | RAM | 32 GB
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | SERVER-2 |  |  | Mouse Make | H.P.
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | CPU Make | H.P.
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | I/P Address | 172.16.4.23
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | Model | HPE ProLiant DL20 Gen11
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | I/P Address | 172.17.4.23
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | Sr. No. | SGH424JSXV
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | Windows edition/Version | Windows Server 2022 standard /21H2
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | System Type | 64-bit Operating System,x64-based processor
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | Monitor Make/Model | H.P./HP Elite Display E231
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | Processor | Intel®Xeon® E E-2434 3.42Ghz 3.30GHz
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | Sr. No | 3CM42816HB
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | Storage | 2 TB
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | Key Board Make | H.P.
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | RAM | 32 GB
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | HISTORY SERVER |  |  | Mouse Make | H.P.
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | CPU Make | Hewlett-Packard Company
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | I/P Address | 172.16.4.71
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | Model | HP Z2 TWR Base Unit G9
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | I/P Address | 172.17.4.71
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | Sr. No. | 4CE337D2VM
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | Windows edition/Version | Windows 10 IoT Enterprise LSTC/21H2
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | System Type | 64-bit Operating System,x64-based processor
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | Monitor Make/Model | H.P./HP Elite Display E231
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | Processor | 13TH Gen Intel®core™i7-13700K 3.40GHz
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | Sr. No | 3CM42816H1
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | Storage | 1TB
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | Key Board Make | H.P.
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | RAM | 16 GB(15.7 usable)
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | ENGINEERING WORKSTATION |  |  | Mouse Make | H.P.
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | CPU Make | Hewlett-Packard Company
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | I/P Address | 172.16.4.81
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | Model | HP Z2 TWR Base Unit G9
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | I/P Address | 172.17.4.81
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | Sr. No. | 4CE338CBC0
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | Windows edition/Version | Windows 10 IoT Enterprise LSTC/21H2
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | System Type | 64-bit Operating System,x64-based processor
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | Monitor Make/Model | H.P./HP Elite Display E231
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | Processor | 13TH Gen Intel®core™i7-13700K 3.40GHz
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | Sr. No | 3CM42816GQ
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | Storage | 1TB
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | Key Board Make | H.P.
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | RAM | 16 GB(15.7 usable)
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OPERATOR WORKSTATION OS-1 |  |  | Mouse Make | H.P.
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | CPU Make | Hewlett-Packard Company
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | I/P Address | 172.16.4.82
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | Model | HP Z2 TWR Base Unit G9
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | I/P Address | 172.17.4.82
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | Sr. No. | 4CE338CB6N
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | Windows edition/Version | Windows 10 IoT Enterprise LSTC/21H2
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | System Type | 64-bit Operating System,x64-based processor
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | Monitor Make/Model | H.P./HP Elite Display E231
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | Processor | 13TH Gen Intel®core™i7-13700K 3.40GHz
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | Sr. No | 3CM42816H4
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | Storage | 1TB
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | Key Board Make | H.P.
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | RAM | 16 GB(15.7 usable)
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OPERATOR WORKSTATION OS-02 |  |  | Mouse Make | H.P.
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | CPU Make | Hewlett-Packard Company
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | I/P Address | 172.16.4.83
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | Model | HP Z2 TWR Base Unit G9
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | I/P Address | 172.17.4.83
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | Sr. No. | 4CE338CN86
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | Windows edition/Version | Windows 10 IoT Enterprise LSTC/21H2
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | System Type | 64-bit Operating System,x64-based processor
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | Monitor Make/Model | H.P./HP Elite Display E231
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | Processor | 13TH Gen Intel®core™i7-13700K 3.40GHz
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | Sr. No | 3CM42816H8
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | Storage | 1TB
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | Key Board Make | H.P.
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | RAM | 16 GB(15.7 usable)
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OPERATOR WORKSTATION OS-03 |  |  | Mouse Make | H.P.
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | CPU Make | Hewlett-Packard Company
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | I/P Address | 172.16.4.84
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | Model | HP Z2 TWR Base Unit G9
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | I/P Address | 172.17.4.84
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | Sr. No. | 4CE351D024
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | Windows edition/Version | Windows 10 IoT Enterprise LSTC/21H2
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | System Type | 64-bit Operating System,x64-based processor
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | Monitor Make/Model | H.P./HP Elite Display E231
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | Processor | 13TH Gen Intel®core™i7-13700K 3.40GHz
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | Sr. No | 3CM42816GX
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | Storage | 1TB
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | Key Board Make | H.P.
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | RAM | 16 GB(15.7 usable)
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OPERATOR WORKSTATION OS-04 |  |  | Mouse Make | H.P.
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | CPU Make | Hewlett-Packard Company
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | I/P Address | 172.16.4.85
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | Model | HP Z2 TWR Base Unit G9
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | I/P Address | 172.17.4.85
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | Sr. No. | 4CE351D022
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | Windows edition/Version | Windows 10 IoT Enterprise LSTC/21H2
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | System Type | 64-bit Operating System,x64-based processor
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | Monitor Make/Model | H.P./HP Elite Display E231
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | Processor | 13TH Gen Intel®core™i7-13700K 3.40GHz
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | Sr. No | 3CM42816H0
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | Storage | 1TB
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | Key Board Make | H.P.
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | RAM | 16 GB(15.7 usable)
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OPERATOR WORKSTATION OS-05 |  |  | Mouse Make | H.P.
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | CPU Make | Hewlett-Packard Company
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | I/P Address | 172.16.4.86
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | Model | HP Z2 TWR Base Unit G9
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | I/P Address | 172.17.4.86
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | Sr. No. | 4CE351D00J
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | Windows edition/Version | Windows 10 IoT Enterprise LSTC/21H2
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | System Type | 64-bit Operating System,x64-based processor
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | Monitor Make/Model | H.P./HP Elite Display E231
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | Processor | 13TH Gen Intel®core™i7-13700K 3.40GHz
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | Sr. No | 3CM42816GY
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | Storage | 1TB
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | Key Board Make | H.P.
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | RAM | 16 GB(15.7 usable)
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OPERATOR WORKSTATION OS-06 |  |  | Mouse Make | H.P.
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | CPU Make | Hewlett-Packard Company
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | I/P Address | 172.16.4.87
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | Model | HP Z2 TWR Base Unit G9
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | I/P Address | 172.17.4.87
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | Sr. No. | 4CE351BMZT
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | Windows edition/Version | Windows 10 IoT Enterprise LSTC/21H2
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | System Type | 64-bit Operating System,x64-based processor
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | Monitor Make/Model | H.P./HP Elite Display E231
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | Processor | 13TH Gen Intel®core™i7-13700K 3.40GHz
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | Sr. No | 3CM42816H2
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | Storage | 1TB
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | Key Board Make | H.P.
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | RAM | 16 GB(15.7 usable)
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OPERATOR WORKSTATION OS-07 |  |  | Mouse Make | H.P.
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | CPU Make | Hewlett-Packard Company
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | I/P Address | 172.16.4.88
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | Model | HP Z2 TWR Base Unit G9
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | I/P Address | 172.17.4.88
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | Sr. No. | 4CE337D2ZR
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | Windows edition/Version | Windows 10 IoT Enterprise LSTC/21H2
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | System Type | 64-bit Operating System,x64-based processor
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | Monitor Make/Model | H.P./HP Elite Display E231
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | Processor | 13TH Gen Intel®core™i7-13700K 3.40GHz
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | Sr. No | 3CM42816J4
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | Storage | 1TB
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | Key Board Make | H.P.
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | RAM | 16 GB(15.7 usable)
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OPERATOR WORKSTATION OS-08 |  |  | Mouse Make | H.P.
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OS-SPARE |  |  | CPU Make | Hewlett-Packard Company
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OS-SPARE |  |  | I/P Address | 172.16.4.149
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OS-SPARE |  |  | Model | HP Z2 TWR Base Unit G9
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OS-SPARE |  |  | I/P Address | 172.17.4.149
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OS-SPARE |  |  | Sr. No. | 4CE337D2HB
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OS-SPARE |  |  | Windows edition/Version | Windows 10 IoT Enterprise LSTC/21H2
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OS-SPARE |  |  | System Type | 64-bit Operating System,x64-based processor
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OS-SPARE |  |  | Processor | 13TH Gen Intel®core™i7-13700K 3.40GHz
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OS-SPARE |  |  | Storage | 1TB
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OS-SPARE |  |  | RAM | 16 GB(15.7 usable)
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | CPU Make | DELL
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | I/P Address | 192.168.1.2
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | Model | OPTIPLEX3020
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | Windows edition/Version | Windows 7 Professional
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | Sr. No. | Monitor Make
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | System Type | 64-bit Operating System
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | Model | MODELO
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | Processor | Intel® Core™ i3 3240
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | Sr. No | CN-0638CF-74261
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | Storage | 500 GB
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | Key Board Make | HP
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | RAM | 4 GB
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | ENGINEERING CUM OPERATOR SYSTEM |  |  | Mouse Make | HP
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | CPU Make | H.P.
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | I/P Address | 192.168.1.101
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | Model | HP PRO 3500 SERIES MT
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | Windows edition/Version | Windows 7 Professional
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | Sr. No. | CZC4112HHK
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | Monitor Make | HANNS.G
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | System Type | 64-bit Operating System
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | Model | HX193DPB
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | Processor | Intel® Core™ i3 3240 CPU @ 3.40 GHz Processors
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | Sr. No | 0702050115CM2,0702050115CM2
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | Storage | 500 GB
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | Key Board Make | HP
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | RAM | 4GB
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | CLIENT-1 SYSTEM |  |  | Mouse Make | HP
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | CPU Make | H.P.
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | I/P Address | 192.168.1.102
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | Model | HP PRO 3500 SERIES MT
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | Windows edition/Version | Windows 7 Professional
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | Sr. No. | CZC4112HWM
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | Monitor Make | HANNS.G
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | System Type | 64-bit Operating System
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | Model | HX193DPB
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | Processor | Intel® Core™ i3 3240 CPU @ 3.40 GHz Processors
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | Sr. No | 0702050115CM2
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | Storage | 500 GB
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | Key Board Make | HP
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | RAM | 4GB
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | CLIENT-2 SYSTEM |  |  | Mouse Make | HP
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | CPU Make | IBM
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | I/P Address | 192.168.200.1
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | Model | 158434
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | Windows edition/Version | Windows 7 Professional
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | Sr. No. | PLA2FTFXM6
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | Monitor Make | DELL
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | System Type | 32-bit Operating System
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | Model | E1912HC
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | Processor | Intel® Core™ i3 3240 CPU @ 3.40 GHz Processors
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | Storage | 500 GB
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | Key Board Make | H.P.
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | RAM | 4GB
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OPERATOR SYSTEM |  |  | Mouse Make | H.P.
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | Make | GST
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | MANUAL CALL POINT (MCP)-Make | GST
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | Model | GST200N-1
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | Model | DI-9204E
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | Sr. No. | 10105118
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | LOOP POWER STROBE HOOTER | GST
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | Power Rating | 120W
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | HEAT \ PHOTOELECT DETECTOR -Make | GST
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | Input rating | 100-240VAC,50-60Hz,1.5A
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | Model | DI-9101E
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | Battery Supply | 24VDC,2.82 A
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | INTELLIGENT PHOTO ELECTRIC SMOKE DETECTOR-Make | GST
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | INTELLIGENT FIRE ALARAM CONTROL PANEL |  |  | Model | (I-9102)
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | Make | GST
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | MANUAL CALL POINT (MCP)-Make | GST
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | Model | GST200N-1
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | Model | DI-9204E
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | Sr. No. | 10105118
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | LOOP POWER STROBE HOOTER | GST
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | Power Rating | 120W
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | HEAT \ PHOTOELECT DETECTOR -Make | GST
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | Input rating | 100-240VAC,50-60Hz,1.5A
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | Model | DI-9101E
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | Battery Supply | 24VDC,2.82 A
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | INTELLIGENT PHOTO ELECTRIC SMOKE DETECTOR-Make | GST
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | FIRE ALARAM CONTROL PANEL |  |  | Model | (I-9102)
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | Make | GST
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | MANUAL CALL POINT (MCP)-Make | GST
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | Model | GST200N-1
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | Model | DI-9204E
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | Sr. No. | 10105118
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | LOOP POWER STROBE HOOTER | GST
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | Power Rating | 120W
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | HEAT \ PHOTOELECT DETECTOR -Make | GST
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | Input rating | 100-240VAC,50-60Hz,1.5A
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | Model | DI-9101E
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | Battery Supply | 24VDC,2.82 A
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | INTELLIGENT PHOTO ELECTRIC SMOKE DETECTOR-Make | GST
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | FIRE ALARAM CONTROL PANEL |  |  | Model | (I-9102)
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Make | Revo
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Sr.No. | B15D2106
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Type | Rotary single acting
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Model | RD700600500000
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Year of Manufacture | 2014
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Tubing | SS-304
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Size | 50 MM
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Cv | 68
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Hand wheel | No
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Material Disc/Body | GG25SS1.4581
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Characteristic | Throttling
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Positioner | ABB
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Seat Replacement type | EPDM
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Type of Valve | Butterfly valve
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Model | RD1101
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Seat Leakage Class | VI
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Air to fail | Valve Open
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Sr.No. | 122122
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Travel | 90ᵒ
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Supply Pressure | 4 KSC
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | AFR | Janetics
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | P Shut | 1 KSC
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Model | FRC 1361 (1/4")
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Conductivity Tx. | ISCT-1072
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Control valve |  |  | Make | I & S
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Manufacturer – | Rose mount
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Serial No. | 6205899
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Working Temperature | (-29 to 60˚)
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Model | 8705TSA030C1W0B3
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Range | NA
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | working pressure | 285 PSI
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Nominal Dia ( MM) | 80 MM
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Calibration Range | NA
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Accuracy | 0.0015
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Material Body | Sensor Material
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | 316 S1 | Repeatability
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Liner | PTFE
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Output | 4-20 mA
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Comunication | HART
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Display Version | Power Supply
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | 90-220 VAC | Protection
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Display unit | Cable length
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Flow meter |  |  | Melt conc. Brix Trans. | SMAR/BR-14160
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Make | Continental
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Sr.No. | 13104
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Type | Single Acting
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Model | 3102
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Year of Manufacture | 2022
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Tubing | SS
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Size | 150 MM
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Cv | Hand wheel
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Material Disc/Body | SS-316 / WCB
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Characteristic | Throttling
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Positioner | YTC
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Seat Replacement type | PTFE
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Type of Valve | Butterfly
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Model | EP-1000RSN
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Seat Leakage Class | Air to fail
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | open | Sr.No.
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Travel | 90 DEG
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Supply Pressure | 2.5 KSC
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Control valve |  |  | P Shut | 4 KSC
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Manufacturer – | Krohne Marshal
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Serial No. | J164080098
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Working Temperature | 120 DEEGRI
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Model | IFC100
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Range | working pressure
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Nominal Dia ( MM) | 50 MM
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Calibration Range | 0-10 M3/Hr.
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Material Body | Sensor Material
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Liner | PTFE
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Output | 4 -20mA
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Display Version | Power Supply
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | 220VAC | Comunication
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Display unit | 2 line LCD
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Cable length | 5 Mtr.
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Flow Meter |  |  | Protection | Earthing
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Manufacturer – | Adept
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Serial No. | 1004974
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Working Temperature | 120 DEEGRI
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Model | 6410
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Range | 0-150 M3/Hr.
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | working pressure | 10 KG/CM2
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Nominal Dia ( MM) | 150MM
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Calibration Range | 0-150 M3/Hr.
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Material Body | Sensor Material
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | SS316 | Linearity
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Liner | PTFE
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Output | 4 -20mA
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Display Version | Power Supply
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | 24 VDC | Comunication
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Display unit | 2 line LCD
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Cable length | 5 Mtr.
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Flow Meter |  |  | Protection | Earthing
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Manufacturer – | Adept
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Serial No. | 230808234
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Working Temperature | 120 DEEGRI
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Model | 6415
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Range | 0-30 M3/Hr.
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | working pressure | 10 KG/CM2
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Nominal Dia ( MM) | 50MM
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Calibration Range | .1-30 M3/Hr.
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Material Body | Sensor Material
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | SS316 | Linearity
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Liner | PTFE
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Output | 4 -20mA
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Display Version | Power Supply
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | 220VAC | Comunication
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Display unit | 2 line LCD
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Cable length | 5 Mtr.
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Flow Meter |  |  | Protection | Earthing
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Make | Continental
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Sr. No. | 19127
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Type | Rotary single acting
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Model | 232/SA -100+M
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Year of Mfg. | 2014
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Tubing | SS-304
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Size | 100 MM
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Cv | 175
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Hand wheel | YES
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Material Disc/Body | SS-316 / A216GR WCB
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Characteristic | THROTTLING
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Positioner | Seimens
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Seat Replacement type | PTFE
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Type of Valve | Butterfly valve
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Model | Sipart PS2
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Seat Leakage Class | VI
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Air to fail | Valve Close
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Sr. No. | N1H1057494184
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Travel | 90ᵒ
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Supply Pressure | 4 KSC
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | AFR | Savo
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Air pr. Min /Max | 105 psi( 7 kg/cm2)
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | P Shut | 1 KSC
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Model | SB-10
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Drain Header Pr. Trans. | Yokogawa/EJA530E-JAS40N-012EL
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Control valve |  |  | Liqour Feed I/L Flow Meter | Rosemount/8732EMT1A1M4

## MAINTENANCE SCHEDULE
sheet id | sheet name | EQUIPMENT TAG NAME/APPLICATION | Sr.No. | Name of Equipment | Maintenance / Inspection Activities | Daily | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years | 3 - Years | 4 - Years | Remarks
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 1 | Stop & Emergency Valve | Blue contact between Valve & Seat | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 1 | Stop & Emergency Valve | Thrust Bearing
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 1 | Stop & Emergency Valve | Gaskets, O−Rings & Seals
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 2 | Throttle Valves | Bearings | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 2 | Throttle Valves | Pivot Pins & Lock Pins
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 2 | Throttle Valves | Lift measurement & Valve freeness
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 3 | Turbine Casing | Casing to Pedestal alignment | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 3 | Turbine Casing | Casing fasteners bolts elongation check & retightening)
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 3 | Turbine Casing | Casing joint line (Compound replacement)
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 3 | Turbine Casing | Full assembly (External)
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 4 | Relay with Governor | Worm wheel | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 4 | Relay with Governor | Bearing,springs, Sliping clutch.
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 4 | Relay with Governor | Gaskets, O−Rings & Seals
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 5 | Over Load Valve | Spindles | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 5 | Over Load Valve | Guide box
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 5 | Over Load Valve | Gaskets, O−Rings & Seals
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 6 | Nozzle & Diaphragms | Nozzles (1st stage) | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 6 | Nozzle & Diaphragms | Steam labyrinth packing (HP & LP)
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 6 | Nozzle & Diaphragms | Steam labyrinth packing holders (HP & LP)
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 6 | Nozzle & Diaphragms | Oil seal labyrinth packing
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 7 | Rotor | Bearings | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 7 | Rotor | Rotor Shaft
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 7 | Rotor | Thrust Bearing Pads
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 7 | Rotor | HP & LP blades
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 8 | Overspeed Trip | Full assembly (Internal) | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 8 | Overspeed Trip | Springs
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 9 | Exhaust Steam Relief Valve | Springs | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 9 | Exhaust Steam Relief Valve | Valve seat
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 10 | Gear Box | Alignment between Gear box & Drive Equipment | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 10 | Gear Box | Alignment between Turbine & Gear box
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 10 | Gear Box | Bearings Casing Fastener
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 10 | Gear Box | Gear & Gear wheel
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 10 | Gear Box | Pinion
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 10 | Gear Box | SSS Clutch ,Oil Seals
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 10 | Gear Box | Gaskets, O−Rings & Seals
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 11 | Coupling (HS &LS) | Transmission Unit / Elements | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 11 | Coupling (HS &LS) | Shear pins
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 11 | Coupling (HS &LS) | Coupling bolt tightness check
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 12 | Main oil tank | Inspection & Cleaning | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 12 | Main oil tank | Tank's rust preventive coating
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 12 | Main oil tank | Suction strainers & Foot valves
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 13 | Filter | Filter element | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 13 | Filter | Filter Assembly
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 13 | Filter | Gaskets, O−Rings & Seals
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 14 | Alternator - | Rotor Shaft | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 14 | Alternator - | Full assembly
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 14 | Alternator - | Shaft balancing
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 14 | Alternator - | Bearings
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 15 | All Duties Valve | Full assembly | [5 empty] | Yes
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | 15 | All Duties Valve | Valve and seat contact
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 1 | Stop & Emergency Valve | Blue contact between Valve & Seat | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 1 | Stop & Emergency Valve | Thrust Bearing
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 1 | Stop & Emergency Valve | Gaskets, O−Rings & Seals
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 2 | Throttle Valves | Bearings | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 2 | Throttle Valves | Pivot Pins & Lock Pins
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 2 | Throttle Valves | Lift measurement & Valve freeness
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 3 | Turbine Casing | Casing to Pedestal alignment | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 3 | Turbine Casing | Casing fasteners bolts elongation check & retightening)
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 3 | Turbine Casing | Casing joint line (Compound replacement)
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 3 | Turbine Casing | Full assembly (External)
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 4 | Relay with Governor | Worm wheel | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 4 | Relay with Governor | Bearing,springs, Sliping clutch.
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 4 | Relay with Governor | Gaskets, O−Rings & Seals
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 5 | Over Load Valve | Spindles | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 5 | Over Load Valve | Guide box
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 5 | Over Load Valve | Gaskets, O−Rings & Seals
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 6 | Nozzle & Diaphragms | Nozzles (1st stage) | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 6 | Nozzle & Diaphragms | Steam labyrinth packing (HP & LP)
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 6 | Nozzle & Diaphragms | Steam labyrinth packing holders (HP & LP)
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 6 | Nozzle & Diaphragms | Oil seal labyrinth packing
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 7 | Rotor | Bearings | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 7 | Rotor | Rotor Shaft
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 7 | Rotor | Thrust Bearing Pads
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 7 | Rotor | HP & LP blades
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 8 | Overspeed Trip | Full assembly (Internal) | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 8 | Overspeed Trip | Springs
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 9 | Exhaust Steam Relief Valve | Springs | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 9 | Exhaust Steam Relief Valve | Valve seat
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 10 | Gear Box | Alignment between Gear box & Drive Equipment | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 10 | Gear Box | Alignment between Turbine & Gear box
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 10 | Gear Box | Bearings Casing Fastener
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 10 | Gear Box | Gear & Gear wheel
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 10 | Gear Box | Pinion
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 10 | Gear Box | SSS Clutch ,Oil Seals
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 10 | Gear Box | Gaskets, O−Rings & Seals
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 11 | Coupling(HS &LS) | Transmission Unit / Elements | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 11 | Coupling(HS &LS) | Shear pins
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 11 | Coupling(HS &LS) | Coupling bolt tightness check
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 12 | Main oil tank | Inspection & Cleaning | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 12 | Main oil tank | Tank's rust preventive coating
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 12 | Main oil tank | Suction strainers & Foot valves
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 13 | Filter | Filter element | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 13 | Filter | Filter Assembly
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 13 | Filter | Gaskets, O−Rings & Seals
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 14 | Alternator - | Rotor Shaft | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 14 | Alternator - | Full assembly
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 14 | Alternator - | Shaft balancing
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 14 | Alternator - | Bearings
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 15 | All Duties Valve | Full assembly | [5 empty] | Yes
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | 15 | All Duties Valve | Valve and seat contact
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 1 | Stop & Emergency Valve | Blue contact between Valve & Seat | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 1 | Stop & Emergency Valve | Thrust Bearing
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 1 | Stop & Emergency Valve | Gaskets, O−Rings & Seals
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 2 | Throttle Valves | Bearings | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 2 | Throttle Valves | Pivot Pins & Lock Pins
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 2 | Throttle Valves | Lift measurement & Valve freeness
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 3 | Turbine Casing | Casing to Pedestal alignment | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 3 | Turbine Casing | Casing fasteners bolts elongation check & retightening)
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 3 | Turbine Casing | Casing joint line (Compound replacement)
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 3 | Turbine Casing | Full assembly (External)
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 4 | Relay with Governor | Worm wheel | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 4 | Relay with Governor | Bearing,springs, Sliping clutch.
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 4 | Relay with Governor | Gaskets, O−Rings & Seals
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 5 | Over Load Valve | Spindles | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 5 | Over Load Valve | Guide box
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 5 | Over Load Valve | Gaskets, O−Rings & Seals
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 6 | Nozzle & Diaphragms | Nozzles (1st stage) | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 6 | Nozzle & Diaphragms | Steam labyrinth packing (HP & LP)
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 6 | Nozzle & Diaphragms | Steam labyrinth packing holders (HP & LP)
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 6 | Nozzle & Diaphragms | Oil seal labyrinth packing
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 7 | Rotor | Bearings | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 7 | Rotor | Rotor Shaft
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 7 | Rotor | Thrust Bearing Pads
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 7 | Rotor | HP & LP blades
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 8 | Overspeed Trip | Full assembly (Internal) | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 8 | Overspeed Trip | Springs
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 9 | Exhaust Steam Relief Valve | Springs | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 9 | Exhaust Steam Relief Valve | Valve seat
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 10 | Gear Box | Alignment between Gear box & Drive Equipment | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 10 | Gear Box | Alignment between Turbine & Gear box
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 10 | Gear Box | Bearings Casing Fastener
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 10 | Gear Box | Gear & Gear wheel
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 10 | Gear Box | Pinion
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 10 | Gear Box | SSS Clutch ,Oil Seals
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 10 | Gear Box | Gaskets, O−Rings & Seals
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 11 | Coupling (HS &LS) | Transmission Unit / Elements | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 11 | Coupling (HS &LS) | Shear pins
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 11 | Coupling (HS &LS) | Coupling bolt tightness check
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 12 | Main oil tank | Inspection & Cleaning | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 12 | Main oil tank | Tank's rust preventive coating
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 12 | Main oil tank | Suction strainers & Foot valves
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 13 | Filter | Filter element | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 13 | Filter | Filter Assembly
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 13 | Filter | Gaskets, O−Rings & Seals
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 14 | All Duties Valve | Full assembly | [5 empty] | Yes
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | 14 | All Duties Valve | Valve and seat contact
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 1 | Actuator | Unscrew the actuator from bracket
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 1 | Actuator | Check the actuator kit & adjustable spring.
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 1 | Actuator | Proper lubricant & assembling all parts.
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 2 | Body | Check physical condition. | [5 empty] | Yes
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 2 | Body | Clean body surface for scaling and foreign particles.
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 3 | Seat | Replace if any requirement
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 4 | Plug | Clean body surface for scaling and foreign particles.
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 7 | A.F.R | Clean its air filter & internal parts.
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | 9 | Monitoring Instruments | Check & clean physical condition.
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 1 | Actuator | Unscrew the actuator from bracket
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 1 | Actuator | Check the actuator kit & adjustable spring.
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 1 | Actuator | Proper lubricant & assembling all parts.
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 2 | Body | Check physical condition. | [5 empty] | Yes
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 2 | Body | Clean body surface for scaling and foreign particles.
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 3 | Seat | Replace if any requirement
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 4 | Plug | Clean body surface for scaling and foreign particles.
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 7 | A.F.R | Clean its air filter & internal parts.
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | 9 | Monitoring Instruments | Check & clean physical condition.
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 1 | Actuator | Unscrew the actuator from bracket
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 1 | Actuator | Check the actuator kit & adjustable spring.
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 1 | Actuator | Proper lubricant & assembling all parts.
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 2 | Body | Check physical condition. | [5 empty] | Yes
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 2 | Body | Clean body surface for scaling and foreign particles.
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 3 | Seat | Replace if any requirement
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 4 | Plug | Clean body surface for scaling and foreign particles.
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 7 | A.F.R | Clean its air filter & internal parts.
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 8 | Electronic equipment | Veryfied calibration status.
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | 10 | Monitoring Instruments | Check & clean physical condition.
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 1 | Actuator | Unscrew the actuator from bracket
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 1 | Actuator | Check the actuator kit & adjustable spring.
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 1 | Actuator | Proper lubricant & assembling all parts.
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 2 | Body | Check physical condition. | [5 empty] | Yes
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 2 | Body | Clean body surface for scaling and foreign particles.
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 3 | Seat | Replace if any requirement
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 4 | Plug | Check leakage & Scaling condition.
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 4 | Plug | Clean body surface for scaling and foreign particles.
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 7 | A.F.R | Clean its air filter & internal parts.
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | 9 | Monitoring Instruments | Check & clean physical condition.
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 1 | Actuator | Unscrew the actuator from bracket
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 1 | Actuator | Check the actuator kit & adjustable spring.
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 1 | Actuator | Proper lubricant & assembling all parts.
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 2 | Body | Check physical condition. | [5 empty] | Yes
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 2 | Body | Clean body surface for scaling and foreign particles.
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 3 | Seat | Replace if any requirement
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 4 | Plug | Check leakage & Scaling condition.
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 4 | Plug | Clean body surface for scaling and foreign particles.
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 7 | A.F.R | Clean its air filter & internal parts.
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | 9 | Monitoring Instruments | Check & clean physical condition.
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 1 | Proxi | Remove all air accessories. | [5 empty] | Yes
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 1 | Proxi | Unscrew the actuator from bracket
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 1 | Proxi | Check the proxi & adjustable point.
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 1 | Proxi | Proper clean & assembling all parts.
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 2 | Acrylic Seet | Check cut and damage sign. | [5 empty] | Yes
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 2 | Acrylic Seet | Replace if any requirement
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 3 | PLC | Clean with Check power supply | [5 empty] | Yes
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 3 | PLC | Check running status.
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 4 | Isolater | Check power output supply. | [5 empty] | Yes
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 4 | Isolater | Clean its conector ,fuse internal parts.
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 5 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 5 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 5 | Electronic equipment | Veryfied calibration status.
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | 7 | Monitoring Instruments | Check & clean physical condition.
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 1 | Proxi | Remove all air accessories. | [5 empty] | Yes
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 1 | Proxi | Unscrew the actuator from bracket
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 1 | Proxi | Check the proxi & adjustable point.
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 1 | Proxi | Proper clean & assembling all parts.
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 2 | Acrelic Seat | Check cut and damage sign. | [5 empty] | Yes
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 2 | Acrelic Seat | Replace if any requirement
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 3 | PLC | Clean with Check power supply | [5 empty] | Yes
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 3 | PLC | Check running status.
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 4 | Isolater | Check power output supply. | [5 empty] | Yes
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 4 | Isolater | Clean its conector ,fuse internal parts.
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 5 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 5 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 5 | Electronic equipment | Veryfied calibration status.
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | 7 | Monitoring Instruments | Check & clean physical condition.
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 1 | Proxi | Remove all air accessories. | [5 empty] | Yes
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 1 | Proxi | Unscrew the actuator from bracket
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 1 | Proxi | Check the proxi & adjustable point.
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 1 | Proxi | Proper clean & assembling all parts.
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 2 | Acrelic Seat | Check cut and damage sign. | [5 empty] | Yes
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 2 | Acrelic Seat | Replace if any requirement
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 3 | PLC | Clean with Check power supply | [5 empty] | Yes
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 3 | PLC | Check running status.
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 4 | Isolater | Check power output supply. | [5 empty] | Yes
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 4 | Isolater | Clean its conector ,fuse internal parts.
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 5 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 5 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 5 | Electronic equipment | Veryfied calibration status.
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | 7 | Monitoring Instruments | Check & clean physical condition.
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 1 | Proxi | Remove all air accessories. | [5 empty] | Yes
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 1 | Proxi | Unscrew the actuator from bracket
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 1 | Proxi | Check the proxi & adjustable point.
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 1 | Proxi | Proper clean & assembling all parts.
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 2 | Acrelic Seat | Check cut and damage sign. | [5 empty] | Yes
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 2 | Acrelic Seat | Replace if any requirement
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 3 | PLC | Clean with Check power supply | [5 empty] | Yes
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 3 | PLC | Check running status.
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 4 | Isolater | Check power output supply. | [5 empty] | Yes
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 4 | Isolater | Clean its conector ,fuse internal parts.
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 5 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 5 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 5 | Electronic equipment | Veryfied calibration status.
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | 7 | Monitoring Instruments | Check & clean physical condition.
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 1 | Proxi | Remove all air accessories. | [5 empty] | Yes
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 1 | Proxi | Unscrew the actuator from bracket
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 1 | Proxi | Check the proxi & adjustable point.
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 1 | Proxi | Proper clean & assembling all parts.
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 2 | Acrelic Seat | Check cut and damage sign. | [5 empty] | Yes
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 2 | Acrelic Seat | Replace if any requirement
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 3 | PLC | Clean with Check power supply | [5 empty] | Yes
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 3 | PLC | Check running status.
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 4 | Isolater | Check power output supply. | [5 empty] | Yes
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 4 | Isolater | Clean its conector ,fuse internal parts.
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 5 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 5 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 5 | Electronic equipment | Veryfied calibration status.
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | 7 | Monitoring Instruments | Check & clean physical condition.
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 1 | Vibration Tx. | Remove all air accessories. | [5 empty] | Yes
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 1 | Vibration Tx. | Unscrew the actuator from bracket
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 1 | Vibration Tx. | Check the proxi & adjustable point.
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 1 | Vibration Tx. | Proper clean & assembling all parts.
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 2 | Pressure Tx. | Check cut and damage sign. | [5 empty] | Yes
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 2 | Pressure Tx. | Replace if any requirement
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 3 | RTD | Check damage rtd wire | [5 empty] | Yes
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 3 | RTD | Check resistance power
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 4 | Indicator | Check power supply. | [5 empty] | Yes
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 4 | Indicator | Clean its conector ,fuse internal parts.
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 5 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 5 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 5 | Electronic equipment | Veryfied calibration status.
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | 7 | Monitoring Instruments | Check & clean physical condition.
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | 1 | Transmitter Body | Check physical condition. | [5 empty] | Yes
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | 1 | Transmitter Body | Clean body surface for scaling and foreign particles.
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | 2 | Pressure Tx | Veryfied calibration status. | [5 empty] | Yes
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | 2 | Pressure Tx | Replace if any requirement
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | 3 | RTD | Check damage rtd wire | [5 empty] | Yes
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | 3 | RTD | Check resistance power
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | 4 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | 4 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | 4 | Electronic equipment | Veryfied calibration status.
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | 5 | Calibration | Calibration done after install at position. (0-100%)
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | 6 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
d16b06a34dbb | Transmitter :: ZIL/SUG./01/TX.-01 | ZIL/SUG./01/TX.-01 | 6 | Monitoring Instruments | Check & clean physical condition.
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | 1 | Transmitter Body | Check physical condition. | [5 empty] | Yes
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | 1 | Transmitter Body | Clean body surface for scaling and foreign particles.
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | 2 | RTD | Check damage rtd wire | [5 empty] | Yes
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | 2 | RTD | Check resistance power
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | 3 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | 3 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | 3 | Electronic equipment | Veryfied calibration status.
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | 4 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
325da979b950 | Transmitter :: ZIL/SUG./02/TX.-2 | ZIL/SUG./02/TX.-2 | 4 | Monitoring Instruments | Check & clean physical condition.
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | 1 | Transmitter Body | Check physical condition. | [5 empty] | Yes
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | 1 | Transmitter Body | Clean body surface for scaling and foreign particles.
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | 2 | RTD | Check damage rtd wire | [5 empty] | Yes
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | 2 | RTD | Check resistance power
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | 3 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | 3 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | 3 | Electronic equipment | Veryfied calibration status.
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | 4 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
5e92fe30c410 | Transmitter :: ZIL/SUG./03/TX.-03 | ZIL/SUG./03/TX.-03 | 4 | Monitoring Instruments | Check & clean physical condition.
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | 1 | Transmitter Body | Check physical condition. | [5 empty] | Yes
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | 1 | Transmitter Body | Clean body surface for scaling and foreign particles.
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | 2 | Diaphragm Seal | Check Diaphrgm seal | [5 empty] | Yes
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | 2 | Diaphragm Seal | Check cleaning
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | 3 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | 3 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | 3 | Electronic equipment | Veryfied calibration status.
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | 4 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
1492ad800d11 | Transmitter :: ZIL/SUG./04/TX.-04 | ZIL/SUG./04/TX.-04 | 4 | Monitoring Instruments | Check & clean physical condition.
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | 1 | Transmitter Body | Check physical condition. | [5 empty] | Yes
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | 1 | Transmitter Body | Clean body surface for scaling and foreign particles.
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | 2 | Routine Maintenance | Inspect electrode weekly/monthly |  | Yes
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | 2 | Routine Maintenance | Clean deposits from electrode.
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | 3 | Ph electrode | Check physical condition. | [5 empty] | Yes
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | 3 | Ph electrode | Use fresh certified buffer solutions
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | 3 | Ph electrode | Clean electrode before calibration
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | 4 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | 4 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | 4 | Electronic equipment | Veryfied calibration status.
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | 5 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
f79fd145caa8 | Transmitter :: ZIL/SUG./05/TX.-05 | ZIL/SUG./05/TX.-05 | 5 | Monitoring Instruments | Check & clean physical condition.
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | 1 | Transmitter Body | Check physical condition. | [5 empty] | Yes
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | 1 | Transmitter Body | Clean body surface for scaling and foreign particles.
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | 2 | Routine Maintenance | Inspect electrode weekly/monthly |  | Yes
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | 2 | Routine Maintenance | Clean deposits from electrode.
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | 3 | Ph electrode | Check physical condition. | [5 empty] | Yes
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | 3 | Ph electrode | Use fresh certified buffer solutions
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | 3 | Ph electrode | Clean electrode before calibration
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | 4 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | 4 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | 4 | Electronic equipment | Veryfied calibration status.
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | 5 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
ae232e634443 | Transmitter :: ZIL/SUG./06/TX.-06 | ZIL/SUG./06/TX.-06 | 5 | Monitoring Instruments | Check & clean physical condition.
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 1 | Visual Inspection | Sensor body free from cracks, dents, or corrosion | [5 empty] | Yes
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 1 | Visual Inspection | Cable gland and connector secure
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 1 | Visual Inspection | Check cable damage, cuts, or insulation deterioration
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 1 | Visual Inspection | Sensor identification visible
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 2 | Cable & Wiring Check | Cable properly clamped to prevent movement |  | Yes
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 2 | Cable & Wiring Check | No moisture ingress in junction box or connector
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 3 | Preventive Maintenance | Check mounting stud for corrosion. | [5 empty] | Yes
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 3 | Preventive Maintenance | Verify trend readings against historical values
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 3 | Preventive Maintenance | Inspect cable supports and conduit
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 4 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 4 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 4 | Electronic equipment | Veryfied calibration status.
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 5 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
73362d5a8684 | Transmitter :: ZIL/SUG./07/TX.-07 | ZIL/SUG./07/TX.-07 | 5 | Monitoring Instruments | Check & clean physical condition.
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 1 | Visual Inspection | Sensor body free from cracks, dents, or corrosion | [5 empty] | Yes
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 1 | Visual Inspection | Cable gland and connector secure
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 1 | Visual Inspection | Check cable damage, cuts, or insulation deterioration
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 1 | Visual Inspection | Sensor identification visible
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 2 | Cable & Wiring Check | Cable properly clamped to prevent movement |  | Yes
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 2 | Cable & Wiring Check | No moisture ingress in junction box or connector
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 3 | Preventive Maintenance | Check mounting stud for corrosion. | [5 empty] | Yes
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 3 | Preventive Maintenance | Verify trend readings against historical values
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 3 | Preventive Maintenance | Inspect cable supports and conduit
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 4 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 4 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 4 | Electronic equipment | Veryfied calibration status.
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 5 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
6eb025f934c5 | Transmitter :: ZIL/SUG./08/TX.-08 | ZIL/SUG./08/TX.-08 | 5 | Monitoring Instruments | Check & clean physical condition.
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 1 | Actuator | Unscrew the actuator from bracket
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 3 | Seat | Replace if any requirement
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 7 | A.F.R | Clean its air filter & internal parts.
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 8 | Electronic equipment | Veryfied calibration status.
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 9 | Calibration | Calibration done after install at position. (0-100%)
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 1 | Actuator | Unscrew the actuator from bracket
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 3 | Seat | Replace if any requirement
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 7 | A.F.R | Clean its air filter & internal parts.
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 8 | Electronic equipment | Veryfied calibration status.
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 9 | Calibration | Calibration done after install at position. (0-100%)
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 1 | Actuator | Unscrew the actuator from bracket
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 3 | Seat | Replace if any requirement
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 7 | A.F.R | Clean its air filter & internal parts.
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 8 | Electronic equipment | Veryfied calibration status.
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 9 | Calibration | Calibration done after install at position. (0-100%)
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 1 | Actuator | Unscrew the actuator from bracket
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 3 | Seat | Replace if any requirement
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 7 | A.F.R | Clean its air filter & internal parts.
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 8 | Calibration | Calibration done after install at position. (0-100%)
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | 9 | Monitoring Instruments | Check & clean physical condition.
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 1 | Actuator | Unscrew the actuator from bracket
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 3 | Seat | Replace if any requirement
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 4 | Plug | Check leakage & Scaling condition.
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 7 | A.F.R | Clean its air filter & internal parts.
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 8 | Electronic equipment | Veryfied calibration status.
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 9 | Calibration | Calibration done after install at position. (0-100%)
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 1 | Actuator | Unscrew the actuator from bracket
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 3 | Seat | Replace if any requirement
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 4 | Plug | Check leakage & Scaling condition.
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 7 | A.F.R | Clean its air filter & internal parts.
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 8 | Electronic equipment | Veryfied calibration status.
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 9 | Calibration | Calibration done after install at position. (0-100%)
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 1 | Actuator | Unscrew the actuator from bracket
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 1 | Actuator | Proper lubricant & assembling all parts.
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 2 | Body | Clean body surface for scaling and foreign particles.
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 3 | Seat | Replace if any requirement
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 4 | Plug | Check leakage & Scaling condition.
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 7 | A.F.R | Clean its air filter & internal parts.
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 8 | Calibration | Calibration done after install at position. (0-100%)
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | 9 | Monitoring Instruments | Check & clean physical condition.
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 1 | Actuator | Unscrew the actuator from bracket
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 1 | Actuator | Check the actuator kit & adjustable spring.
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 1 | Actuator | Proper lubricant & assembling all parts.
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 2 | Body | Check physical condition. | [5 empty] | Yes
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 2 | Body | Clean body surface for scaling and foreign particles.
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 3 | Seat | Replace if any requirement
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 4 | Plug | Check leakage & Scaling condition.
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 4 | Plug | Clean body surface for scaling and foreign particles.
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 7 | A.F.R | Clean its air filter & internal parts.
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 8 | Calibration | Calibration done after install at position. (0-100%)
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | 9 | Monitoring Instruments | Check & clean physical condition.
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 1 | Actuator | Unscrew the actuator from bracket
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 3 | Seat | Replace if any requirement
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 4 | Plug | Check leakage & Scaling condition.
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 7 | A.F.R | Clean its air filter & internal parts.
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 8 | Calibration | Calibration done after install at position. (0-100%)
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | 9 | Monitoring Instruments | Check & clean physical condition.
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 1 | Actuator | Unscrew the actuator from bracket
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 3 | Seat | Replace if any requirement
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 7 | A.F.R | Clean its air filter & internal parts.
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 8 | Electronic equipment | Veryfied calibration status.
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 1 | Actuator | Unscrew the actuator from bracket
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 3 | Seat | Replace if any requirement
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 7 | A.F.R | Clean its air filter & internal parts.
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 8 | Electronic equipment | Veryfied calibration status.
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 1 | Actuator | Unscrew the actuator from bracket
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 3 | Seat | Replace if any requirement
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 7 | A.F.R | Clean its air filter & internal parts.
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 8 | Electronic equipment | Veryfied calibration status.
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 1 | Actuator | Unscrew the actuator from bracket
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 3 | Seat | Replace if any requirement
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 7 | A.F.R | Clean its air filter & internal parts.
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 8 | Electronic equipment | Veryfied calibration status.
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 1 | Actuator | Unscrew the actuator from bracket
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 3 | Seat | Replace if any requirement
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 4 | Plug | Check leakage & Scaling condition.
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 7 | A.F.R | Clean its air filter & internal parts.
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 8 | Electronic equipment | Veryfied calibration status.
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 1 | Electrode | Unscrew the Cylinder from body
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 1 | Electrode | Check the cylinder kit & Neck bush.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 1 | Electrode | Proper lubricant & assembling all parts.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 2 | Actuator | Unscrew the actuator from bracket
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 2 | Actuator | Check the actuator kit & adjustable spring.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 2 | Actuator | Proper lubricant & assembling all parts.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 3 | Body | Check physical condition. | [5 empty] | Yes
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 3 | Body | Clean body surface for scaling and foreign particles.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 4 | Seat | Replace if any requirement
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 5 | Plug | Check leakage & Scaling condition.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 5 | Plug | Clean body surface for scaling and foreign particles.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 8 | Brick Transmitter | Check & Calibrated
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 9 | A.F.R | Clean its air filter & internal parts.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 8 | Electronic equipment | Veryfied calibration status.
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | 11 | Monitoring Instruments | Check & clean physical condition.
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 1 | Electrode | Unscrew the Cylinder from body
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 1 | Electrode | Check the cylinder kit & Neck bush.
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 1 | Electrode | Proper lubricant & assembling all parts.
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 2 | Actuator | Unscrew the actuator from bracket
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 2 | Actuator | Check the actuator kit & adjustable spring.
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 2 | Actuator | Proper lubricant & assembling all parts.
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 3 | Body | Check physical condition. | [5 empty] | Yes
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 3 | Body | Clean body surface for scaling and foreign particles.
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 4 | Seat | Replace if any requirement
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 5 | Plug | Check leakage & Scaling condition.
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 5 | Plug | Clean body surface for scaling and foreign particles.
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 8 | Brick Transmitter | Check & Calibrated
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 9 | A.F.R | Clean its air filter & internal parts.
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | 11 | Monitoring Instruments | Check & clean physical condition.
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 1 | Electrode | Unscrew the Cylinder from body
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 1 | Electrode | Check the cylinder kit & Neck bush.
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 1 | Electrode | Proper lubricant & assembling all parts.
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 2 | Actuator | Unscrew the actuator from bracket
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 2 | Actuator | Check the actuator kit & adjustable spring.
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 2 | Actuator | Proper lubricant & assembling all parts.
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 3 | Body | Check physical condition. | [5 empty] | Yes
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 3 | Body | Clean body surface for scaling and foreign particles.
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 4 | Seat | Replace if any requirement
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 5 | Plug | Check leakage & Scaling condition.
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 5 | Plug | Clean body surface for scaling and foreign particles.
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 8 | Brick Transmitter | Check & Calibrated
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 9 | A.F.R | Clean its air filter & internal parts.
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | 11 | Monitoring Instruments | Check & clean physical condition.
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 1 | Electrode | Unscrew the Cylinder from body
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 1 | Electrode | Check the cylinder kit & Neck bush.
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 1 | Electrode | Proper lubricant & assembling all parts.
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 2 | Actuator | Unscrew the actuator from bracket
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 2 | Actuator | Check the actuator kit & adjustable spring.
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 2 | Actuator | Proper lubricant & assembling all parts.
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 3 | Body | Check physical condition. | [5 empty] | Yes
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 3 | Body | Clean body surface for scaling and foreign particles.
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 4 | Seat | Replace if any requirement
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 5 | Plug | Check leakage & Scaling condition.
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 5 | Plug | Clean body surface for scaling and foreign particles.
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 8 | Brick Transmitter | Check & Calibrated
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 9 | A.F.R | Clean its air filter & internal parts.
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | 11 | Monitoring Instruments | Check & clean physical condition.
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 1 | Electrode | Unscrew the Cylinder from body
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 1 | Electrode | Check the cylinder kit & Neck bush.
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 1 | Electrode | Proper lubricant & assembling all parts.
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 2 | Actuator | Unscrew the actuator from bracket
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 2 | Actuator | Check the actuator kit & adjustable spring.
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 2 | Actuator | Proper lubricant & assembling all parts.
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 3 | Body | Check physical condition. | [5 empty] | Yes
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 3 | Body | Clean body surface for scaling and foreign particles.
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 4 | Seat | Replace if any requirement
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 5 | Plug | Check leakage & Scaling condition.
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 5 | Plug | Clean body surface for scaling and foreign particles.
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 8 | Brick Transmitter | Check & Calibrated
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 9 | A.F.R | Clean its air filter & internal parts.
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | 11 | Monitoring Instruments | Check & clean physical condition.
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 1 | Electrode | Unscrew the Cylinder from body
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 1 | Electrode | Check the cylinder kit & Neck bush.
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 1 | Electrode | Proper lubricant & assembling all parts.
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 2 | Actuator | Unscrew the actuator from bracket
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 2 | Actuator | Check the actuator kit & adjustable spring.
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 2 | Actuator | Proper lubricant & assembling all parts.
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 3 | Body | Check physical condition. | [5 empty] | Yes
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 3 | Body | Clean body surface for scaling and foreign particles.
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 4 | Seat | Replace if any requirement
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 5 | Plug | Check leakage & Scaling condition.
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 5 | Plug | Clean body surface for scaling and foreign particles.
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 8 | Brick Transmitter | Check & Calibrated
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 9 | A.F.R | Clean its air filter & internal parts.
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | 11 | Monitoring Instruments | Check & clean physical condition.
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 1 | Electrode | Unscrew the Cylinder from body
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 1 | Electrode | Check the cylinder kit & Neck bush.
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 1 | Electrode | Proper lubricant & assembling all parts.
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 2 | Actuator | Unscrew the actuator from bracket
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 2 | Actuator | Check the actuator kit & adjustable spring.
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 2 | Actuator | Proper lubricant & assembling all parts.
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 3 | Body | Check physical condition. | [5 empty] | Yes
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 3 | Body | Clean body surface for scaling and foreign particles.
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 4 | Seat | Replace if any requirement
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 5 | Plug | Check leakage & Scaling condition.
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 5 | Plug | Clean body surface for scaling and foreign particles.
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 8 | Brick Transmitter | Check & Calibrated
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 9 | A.F.R | Clean its air filter & internal parts.
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | 11 | Monitoring Instruments | Check & clean physical condition.
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 1 | Electrode | Unscrew the Cylinder from body
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 1 | Electrode | Check the cylinder kit & Neck bush.
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 1 | Electrode | Proper lubricant & assembling all parts.
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 2 | Actuator | Unscrew the actuator from bracket
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 2 | Actuator | Check the actuator kit & adjustable spring.
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 2 | Actuator | Proper lubricant & assembling all parts.
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 3 | Body | Check physical condition. | [5 empty] | Yes
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 3 | Body | Clean body surface for scaling and foreign particles.
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 4 | Seat | Replace if any requirement
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 5 | Plug | Check leakage & Scaling condition.
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 5 | Plug | Clean body surface for scaling and foreign particles.
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 8 | Brick Transmitter | Check & Calibrated
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 9 | A.F.R | Clean its air filter & internal parts.
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | 11 | Monitoring Instruments | Check & clean physical condition.
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 1 | Electrode | Unscrew the Cylinder from body
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 1 | Electrode | Check the cylinder kit & Neck bush.
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 1 | Electrode | Proper lubricant & assembling all parts.
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 2 | Actuator | Unscrew the actuator from bracket
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 2 | Actuator | Check the actuator kit & adjustable spring.
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 2 | Actuator | Proper lubricant & assembling all parts.
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 3 | Body | Check physical condition. | [5 empty] | Yes
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 3 | Body | Clean body surface for scaling and foreign particles.
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 4 | Seat | Replace if any requirement
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 5 | Plug | Check leakage & Scaling condition.
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 5 | Plug | Clean body surface for scaling and foreign particles.
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 8 | Brick Transmitter | Check & Calibrated
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 9 | A.F.R | Clean its air filter & internal parts.
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | 11 | Monitoring Instruments | Check & clean physical condition.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 1 | Electrode | Unscrew the Cylinder from body
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 1 | Electrode | Check the cylinder kit & Neck bush.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 1 | Electrode | Proper lubricant & assembling all parts.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 2 | Actuator | Unscrew the actuator from bracket
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 2 | Actuator | Check the actuator kit & adjustable spring.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 2 | Actuator | Proper lubricant & assembling all parts.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 3 | Body | Check physical condition. | [5 empty] | Yes
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 3 | Body | Clean body surface for scaling and foreign particles.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 4 | Seat | Replace if any requirement
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 5 | Plug | Check leakage & Scaling condition.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 5 | Plug | Clean body surface for scaling and foreign particles.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 8 | Brick Transmitter | Check & Calibrated
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 9 | A.F.R | Clean its air filter & internal parts.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 10 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 10 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 10 | Electronic equipment | Veryfied calibration status.
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | 12 | Monitoring Instruments | Check & clean physical condition.
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 1 | Electrode | Unscrew the Cylinder from body
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 1 | Electrode | Check the cylinder kit & Neck bush.
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 1 | Electrode | Proper lubricant & assembling all parts.
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 2 | Actuator | Unscrew the actuator from bracket
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 2 | Actuator | Check the actuator kit & adjustable spring.
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 2 | Actuator | Proper lubricant & assembling all parts.
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 3 | Body | Check physical condition. | [5 empty] | Yes
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 3 | Body | Clean body surface for scaling and foreign particles.
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 4 | Seat | Replace if any requirement
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 5 | Plug | Check leakage & Scaling condition.
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 5 | Plug | Clean body surface for scaling and foreign particles.
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 8 | Brick Transmitter | Check & Calibrated
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 9 | A.F.R | Clean its air filter & internal parts.
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | 11 | Monitoring Instruments | Check & clean physical condition.
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 1 | Electrode | Unscrew the Cylinder from body
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 1 | Electrode | Check the cylinder kit & Neck bush.
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 1 | Electrode | Proper lubricant & assembling all parts.
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 2 | Actuator | Unscrew the actuator from bracket
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 2 | Actuator | Check the actuator kit & adjustable spring.
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 2 | Actuator | Proper lubricant & assembling all parts.
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 3 | Body | Check physical condition. | [5 empty] | Yes
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 3 | Body | Clean body surface for scaling and foreign particles.
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 4 | Seat | Replace if any requirement
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 5 | Plug | Check leakage & Scaling condition.
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 5 | Plug | Clean body surface for scaling and foreign particles.
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 8 | Brick Transmitter | Check & Calibrated
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 9 | A.F.R | Clean its air filter & internal parts.
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | 11 | Monitoring Instruments | Check & clean physical condition.
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 1 | Electrode | Unscrew the Cylinder from body
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 1 | Electrode | Check the cylinder kit & Neck bush.
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 1 | Electrode | Proper lubricant & assembling all parts.
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 2 | Actuator | Unscrew the actuator from bracket
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 2 | Actuator | Check the actuator kit & adjustable spring.
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 2 | Actuator | Proper lubricant & assembling all parts.
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 3 | Body | Check physical condition. | [5 empty] | Yes
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 3 | Body | Clean body surface for scaling and foreign particles.
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 4 | Seat | Replace if any requirement
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 5 | Plug | Check leakage & Scaling condition.
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 5 | Plug | Clean body surface for scaling and foreign particles.
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 8 | Brick Transmitter | Check & Calibrated
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 9 | A.F.R | Clean its air filter & internal parts.
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | 11 | Monitoring Instruments | Check & clean physical condition.
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 1 | Electrode | Unscrew the Cylinder from body
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 1 | Electrode | Check the cylinder kit & Neck bush.
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 1 | Electrode | Proper lubricant & assembling all parts.
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 2 | Actuator | Unscrew the actuator from bracket
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 2 | Actuator | Check the actuator kit & adjustable spring.
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 2 | Actuator | Proper lubricant & assembling all parts.
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 3 | Body | Check physical condition. | [5 empty] | Yes
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 3 | Body | Clean body surface for scaling and foreign particles.
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 4 | Seat | Replace if any requirement
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 5 | Plug | Check leakage & Scaling condition.
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 5 | Plug | Clean body surface for scaling and foreign particles.
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 8 | Brick Transmitter | Check & Calibrated
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 9 | A.F.R | Clean its air filter & internal parts.
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | 11 | Monitoring Instruments | Check & clean physical condition.
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 1 | Electrode | Unscrew the Cylinder from body
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 1 | Electrode | Check the cylinder kit & Neck bush.
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 1 | Electrode | Proper lubricant & assembling all parts.
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 2 | Actuator | Unscrew the actuator from bracket
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 2 | Actuator | Check the actuator kit & adjustable spring.
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 2 | Actuator | Proper lubricant & assembling all parts.
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 3 | Body | Check physical condition. | [5 empty] | Yes
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 3 | Body | Clean body surface for scaling and foreign particles.
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 4 | Seat | Replace if any requirement
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 5 | Plug | Check leakage & Scaling condition.
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 5 | Plug | Clean body surface for scaling and foreign particles.
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 8 | Brick Transmitter | Check & Calibrated
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 9 | A.F.R | Clean its air filter & internal parts.
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | 11 | Monitoring Instruments | Check & clean physical condition.
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 1 | Electrode | Unscrew the Cylinder from body
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 1 | Electrode | Check the cylinder kit & Neck bush.
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 1 | Electrode | Proper lubricant & assembling all parts.
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 2 | Actuator | Unscrew the actuator from bracket
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 2 | Actuator | Check the actuator kit & adjustable spring.
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 2 | Actuator | Proper lubricant & assembling all parts.
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 3 | Body | Check physical condition. | [5 empty] | Yes
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 3 | Body | Clean body surface for scaling and foreign particles.
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 4 | Seat | Replace if any requirement
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 5 | Plug | Check leakage & Scaling condition.
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 5 | Plug | Clean body surface for scaling and foreign particles.
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 8 | Brick Transmitter | Check & Calibrated
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 9 | A.F.R | Clean its air filter & internal parts.
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | 11 | Monitoring Instruments | Check & clean physical condition.
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 1 | Electrode | Unscrew the Cylinder from body
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 1 | Electrode | Check the cylinder kit & Neck bush.
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 1 | Electrode | Proper lubricant & assembling all parts.
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 2 | Actuator | Unscrew the actuator from bracket
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 2 | Actuator | Check the actuator kit & adjustable spring.
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 2 | Actuator | Proper lubricant & assembling all parts.
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 3 | Body | Check physical condition. | [5 empty] | Yes
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 3 | Body | Clean body surface for scaling and foreign particles.
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 4 | Seat | Replace if any requirement
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 5 | Plug | Check leakage & Scaling condition.
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 5 | Plug | Clean body surface for scaling and foreign particles.
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 8 | Brick Transmitter | Check & Calibrated
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 9 | A.F.R | Clean its air filter & internal parts.
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | 11 | Monitoring Instruments | Check & clean physical condition.
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 1 | Electrode | Unscrew the Cylinder from body
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 1 | Electrode | Check the cylinder kit & Neck bush.
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 1 | Electrode | Proper lubricant & assembling all parts.
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 2 | Actuator | Unscrew the actuator from bracket
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 2 | Actuator | Check the actuator kit & adjustable spring.
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 2 | Actuator | Proper lubricant & assembling all parts.
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 3 | Body | Check physical condition. | [5 empty] | Yes
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 3 | Body | Clean body surface for scaling and foreign particles.
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 4 | Seat | Replace if any requirement
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 5 | Plug | Check leakage & Scaling condition.
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 5 | Plug | Clean body surface for scaling and foreign particles.
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 8 | Brick Transmitter | Check & Calibrated
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 9 | A.F.R | Clean its air filter & internal parts.
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | 11 | Monitoring Instruments | Check & clean physical condition.
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 1 | Electrode | Unscrew the Cylinder from body
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 1 | Electrode | Check the cylinder kit & Neck bush.
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 1 | Electrode | Proper lubricant & assembling all parts.
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 2 | Actuator | Unscrew the actuator from bracket
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 2 | Actuator | Check the actuator kit & adjustable spring.
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 2 | Actuator | Proper lubricant & assembling all parts.
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 3 | Body | Check physical condition. | [5 empty] | Yes
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 3 | Body | Clean body surface for scaling and foreign particles.
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 4 | Seat | Replace if any requirement
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 5 | Plug | Check leakage & Scaling condition.
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 5 | Plug | Clean body surface for scaling and foreign particles.
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 8 | Brick Transmitter | Check & Calibrated
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 9 | A.F.R | Clean its air filter & internal parts.
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | 11 | Monitoring Instruments | Check & clean physical condition.
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 1 | Electrode | Unscrew the Cylinder from body
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 1 | Electrode | Check the cylinder kit & Neck bush.
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 1 | Electrode | Proper lubricant & assembling all parts.
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 2 | Actuator | Unscrew the actuator from bracket
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 2 | Actuator | Check the actuator kit & adjustable spring.
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 2 | Actuator | Proper lubricant & assembling all parts.
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 3 | Body | Check physical condition. | [5 empty] | Yes
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 3 | Body | Clean body surface for scaling and foreign particles.
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 4 | Seat | Replace if any requirement
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 5 | Plug | Check leakage & Scaling condition.
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 5 | Plug | Clean body surface for scaling and foreign particles.
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 8 | Brick Transmitter | Check & Calibrated
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 9 | A.F.R | Clean its air filter & internal parts.
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | 11 | Monitoring Instruments | Check & clean physical condition.
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 1 | Actuator | Unscrew the actuator from bracket
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 1 | Actuator | Check the actuator kit & adjustable spring.
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 1 | Actuator | Proper lubricant & assembling all parts.
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 2 | Body | Check physical condition. | [5 empty] | Yes
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 2 | Body | Clean body surface for scaling and foreign particles.
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 3 | Seat | Replace if any requirement
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 4 | Plug | Check leakage & Scaling condition.
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 4 | Plug | Clean body surface for scaling and foreign particles.
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 7 | A.F.R | Clean its air filter & internal parts.
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | 9 | Monitoring Instruments | Check & clean physical condition.
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 1 | Actuator | Unscrew the actuator from bracket
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 1 | Actuator | Check the actuator kit & adjustable spring.
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 1 | Actuator | Proper lubricant & assembling all parts.
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 2 | Body | Check physical condition. | [5 empty] | Yes
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 2 | Body | Clean body surface for scaling and foreign particles.
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 3 | Seat | Replace if any requirement
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 4 | Plug | Check leakage & Scaling condition.
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 4 | Plug | Clean body surface for scaling and foreign particles.
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 7 | A.F.R | Clean its air filter & internal parts.
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 8 | Electronic equipment | Veryfied calibration status.
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | 9 | Monitoring Instruments | Check & clean physical condition.
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 1 | Actuator | Unscrew the actuator from bracket
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 1 | Actuator | Check the actuator kit & adjustable spring.
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 1 | Actuator | Proper lubricant & assembling all parts.
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 2 | Body | Check physical condition. | [5 empty] | Yes
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 2 | Body | Clean body surface for scaling and foreign particles.
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 3 | Seat | Replace if any requirement
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 4 | Plug | Check leakage & Scaling condition.
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 4 | Plug | Clean body surface for scaling and foreign particles.
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 7 | A.F.R | Clean its air filter & internal parts.
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | 9 | Monitoring Instruments | Check & clean physical condition.
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 1 | Actuator | Unscrew the actuator from bracket
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 1 | Actuator | Check the actuator kit & adjustable spring.
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 1 | Actuator | Proper lubricant & assembling all parts.
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 2 | Body | Check physical condition. | [5 empty] | Yes
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 2 | Body | Clean body surface for scaling and foreign particles.
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 3 | Seat | Replace if any requirement
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 4 | Plug | Check leakage & Scaling condition.
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 4 | Plug | Clean body surface for scaling and foreign particles.
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 7 | A.F.R | Clean its air filter & internal parts.
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 8 | Electronic equipment | Veryfied calibration status.
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 9 | Calibration | Calibration done after install at position. (0-100%)
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | 10 | Monitoring Instruments | Check & clean physical condition.
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 1 | Actuator | Unscrew the actuator from bracket
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 3 | Seat | Replace if any requirement
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 4 | Plug | Check leakage & Scaling condition.
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 7 | A.F.R | Clean its air filter & internal parts.
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | 9 | Monitoring Instruments | Check & clean physical condition.
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 1 | Actuator | Unscrew the actuator from bracket
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 3 | Seat | Replace if any requirement
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 4 | Plug | Check leakage & Scaling condition.
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 7 | A.F.R | Clean its air filter & internal parts.
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 8 | Electronic equipment | Veryfied calibration status.
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 1 | Actuator | Unscrew the actuator from bracket
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 1 | Actuator | Check the actuator kit & adjustable spring.
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 1 | Actuator | Proper lubricant & assembling all parts.
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 2 | Body | Check physical condition. | [5 empty] | Yes
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 2 | Body | Clean body surface for scaling and foreign particles.
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 3 | Seat | Replace if any requirement
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 4 | Plug | Check leakage & Scaling condition.
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 4 | Plug | Clean body surface for scaling and foreign particles.
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 7 | A.F.R | Clean its air filter & internal parts.
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 8 | Electronic equipment | Veryfied calibration status.
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
af99b8d37f38 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080A | ZIL/SUG./080A | 10 | Monitoring Instruments | Check & clean physical condition.
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 1 | Actuator | Unscrew the actuator from bracket
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 1 | Actuator | Check the actuator kit & adjustable spring.
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 1 | Actuator | Proper lubricant & assembling all parts.
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 2 | Body | Check physical condition. | [5 empty] | Yes
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 2 | Body | Clean body surface for scaling and foreign particles.
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 3 | Seat | Replace if any requirement
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 4 | Plug | Check leakage & Scaling condition.
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 4 | Plug | Clean body surface for scaling and foreign particles.
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 7 | A.F.R | Clean its air filter & internal parts.
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 8 | Electronic equipment | Veryfied calibration status.
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
95694f79439e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080B | ZIL/SUG./080B | 10 | Monitoring Instruments | Check & clean physical condition.
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 1 | Actuator | Unscrew the actuator from bracket
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 3 | Seat | Replace if any requirement
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 7 | A.F.R | Clean its air filter & internal parts.
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 8 | Electronic equipment | Veryfied calibration status.
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 1 | Actuator | Unscrew the actuator from bracket
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 3 | Seat | Replace if any requirement
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 7 | A.F.R | Clean its air filter & internal parts.
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 8 | Electronic equipment | Veryfied calibration status.
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 1 | Actuator | Unscrew the actuator from bracket
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 3 | Seat | Replace if any requirement
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 7 | A.F.R | Clean its air filter & internal parts.
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 8 | Electronic equipment | Veryfied calibration status.
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 1 | Actuator | Unscrew the actuator from bracket
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 3 | Seat | Replace if any requirement
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 7 | A.F.R | Clean its air filter & internal parts.
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 8 | Electronic equipment | Veryfied calibration status.
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 1 | Actuator | Unscrew the actuator from bracket
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 3 | Seat | Replace if any requirement
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 7 | A.F.R | Clean its air filter & internal parts.
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 8 | Electronic equipment | Veryfied calibration status.
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 8 | Electronic equipment | Veryfied calibration status.
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 1 | Actuator | Unscrew the actuator from bracket
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 3 | Seat | Replace if any requirement
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 7 | A.F.R | Clean its air filter & internal parts.
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 8 | Electronic equipment | Veryfied calibration status.
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 1 | Actuator | Unscrew the actuator from bracket
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 1 | Actuator | Check the actuator kit & adjustable spring.
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 1 | Actuator | Proper lubricant & assembling all parts.
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 2 | Body | Check physical condition. | [5 empty] | Yes
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 2 | Body | Clean body surface for scaling and foreign particles.
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 3 | Seat | Replace if any requirement
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 4 | Plug | Clean body surface for scaling and foreign particles.
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 7 | A.F.R | Clean its air filter & internal parts.
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 8 | Electronic equipment | Veryfied calibration status.
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | 10 | Monitoring Instruments | Check & clean physical condition.
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 1 | Actuator | Unscrew the actuator from bracket
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 1 | Actuator | Check the actuator kit & adjustable spring.
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 1 | Actuator | Proper lubricant & assembling all parts.
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 2 | Body | Check physical condition. | [5 empty] | Yes
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 2 | Body | Clean body surface for scaling and foreign particles.
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 3 | Seat | Replace if any requirement
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 4 | Plug | Clean body surface for scaling and foreign particles.
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 7 | A.F.R | Clean its air filter & internal parts.
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 8 | Electronic equipment | Veryfied calibration status.
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | 10 | Monitoring Instruments | Check & clean physical condition.
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 1 | Actuator | Unscrew the actuator from bracket
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 3 | Seat | Replace if any requirement
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 7 | A.F.R | Clean its air filter & internal parts.
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 8 | Electronic equipment | Veryfied calibration status.
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 1 | Actuator | Unscrew the actuator from bracket
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 3 | Seat | Replace if any requirement
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 7 | A.F.R | Clean its air filter & internal parts.
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 8 | Electronic equipment | Veryfied calibration status.
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 1 | Actuator | Unscrew the actuator from bracket
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 3 | Seat | Replace if any requirement
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 7 | A.F.R | Clean its air filter & internal parts.
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 8 | Electronic equipment | Veryfied calibration status.
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 1 | Actuator | Unscrew the actuator from bracket
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 1 | Actuator | Check the actuator kit & adjustable spring.
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 1 | Actuator | Proper lubricant & assembling all parts.
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 2 | Body | Check physical condition. | [5 empty] | Yes
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 2 | Body | Clean body surface for scaling and foreign particles.
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 3 | Seat | Replace if any requirement
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 4 | Plug | Clean body surface for scaling and foreign particles.
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 7 | A.F.R | Clean its air filter & internal parts.
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | 9 | Monitoring Instruments | Check & clean physical condition.
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 1 | Actuator | Unscrew the actuator from bracket
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 1 | Actuator | Check the actuator kit & adjustable spring.
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 1 | Actuator | Proper lubricant & assembling all parts.
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 2 | Body | Check physical condition. | [5 empty] | Yes
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 2 | Body | Clean body surface for scaling and foreign particles.
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 3 | Seat | Replace if any requirement
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 4 | Plug | Clean body surface for scaling and foreign particles.
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 7 | A.F.R | Clean its air filter & internal parts.
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | 9 | Monitoring Instruments | Check & clean physical condition.
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 1 | Actuator | Unscrew the actuator from bracket
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 1 | Actuator | Check the actuator kit & adjustable spring.
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 1 | Actuator | Proper lubricant & assembling all parts.
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 2 | Body | Check physical condition. | [5 empty] | Yes
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 2 | Body | Clean body surface for scaling and foreign particles.
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 3 | Seat | Replace if any requirement
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 4 | Plug | Clean body surface for scaling and foreign particles.
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 7 | A.F.R | Clean its air filter & internal parts.
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | 9 | Monitoring Instruments | Check & clean physical condition.
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 1 | Actuator | Unscrew the actuator from bracket
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 3 | Seat | Replace if any requirement
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 7 | A.F.R | Clean its air filter & internal parts.
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 8 | Electronic equipment | Veryfied calibration status.
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 1 | Actuator | Unscrew the actuator from bracket
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 3 | Seat | Replace if any requirement
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 7 | A.F.R | Clean its air filter & internal parts.
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 8 | Electronic equipment | Veryfied calibration status.
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 1 | Actuator | Unscrew the actuator from bracket
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 3 | Seat | Replace if any requirement
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 7 | A.F.R | Clean its air filter & internal parts.
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 8 | Electronic equipment | Veryfied calibration status.
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 1 | Actuator | Unscrew the actuator from bracket
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 3 | Seat | Replace if any requirement
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 7 | A.F.R | Clean its air filter & internal parts.
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 8 | Electronic equipment | Veryfied calibration status.
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 1 | Actuator | Unscrew the actuator from bracket
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 3 | Seat | Replace if any requirement
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 7 | A.F.R | Clean its air filter & internal parts.
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 8 | Electronic equipment | Veryfied calibration status.
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 1 | Actuator | Unscrew the actuator from bracket
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 3 | Seat | Replace if any requirement
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 7 | A.F.R | Clean its air filter & internal parts.
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | 9 | Monitoring Instruments | Check & clean physical condition.
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 1 | Actuator | Unscrew the actuator from bracket
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 3 | Seat | Replace if any requirement
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 7 | A.F.R | Clean its air filter & internal parts.
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | 9 | Monitoring Instruments | Check & clean physical condition.
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 1 | Actuator | Unscrew the actuator from bracket
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 1 | Actuator | Proper lubricant & assembling all parts.
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 2 | Body | Clean body surface for scaling and foreign particles.
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 3 | Seat | Replace if any requirement
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 7 | A.F.R | Clean its air filter & internal parts.
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | 9 | Monitoring Instruments | Check & clean physical condition.
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 1 | Actuator | Unscrew the actuator from bracket
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 3 | Seat | Replace if any requirement
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 7 | A.F.R | Clean its air filter & internal parts.
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 8 | Electronic equipment | Veryfied calibration status.
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | 10 | Monitoring Instruments | Check & clean physical condition.
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 1 | Actuator | Unscrew the actuator from bracket
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 1 | Actuator | Check the actuator kit & adjustable spring.
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 1 | Actuator | Proper lubricant & assembling all parts.
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 2 | Body | Check physical condition. | [5 empty] | Yes
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 2 | Body | Clean body surface for scaling and foreign particles.
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 3 | Seat | Replace if any requirement
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 4 | Plug | Clean body surface for scaling and foreign particles.
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 7 | A.F.R | Clean its air filter & internal parts.
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 8 | Electronic equipment | Veryfied calibration status.
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | 10 | Monitoring Instruments | Check & clean physical condition.
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 1 | Actuator | Unscrew the actuator from bracket
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 3 | Seat | Replace if any requirement
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 7 | A.F.R | Clean its air filter & internal parts.
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 8 | Electronic equipment | Veryfied calibration status.
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | 9 | Monitoring Instruments | Check & clean physical condition.
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 1 | Actuator | Unscrew the actuator from bracket
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 1 | Actuator | Proper lubricant & assembling all parts.
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 2 | Body | Clean body surface for scaling and foreign particles.
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 3 | Seat | Replace if any requirement
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 7 | A.F.R | Clean its air filter & internal parts.
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 8 | Electronic equipment | Veryfied calibration status.
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | 9 | Monitoring Instruments | Check & clean physical condition.
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 1 | Actuator | Unscrew the actuator from bracket
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 1 | Actuator | Proper lubricant & assembling all parts.
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 2 | Body | Clean body surface for scaling and foreign particles.
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 3 | Seat | Replace if any requirement
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 7 | A.F.R | Clean its air filter & internal parts.
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 8 | Electronic equipment | Veryfied calibration status.
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | 10 | Monitoring Instruments | Check & clean physical condition.
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 1 | Actuator | Unscrew the actuator from bracket
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 1 | Actuator | Proper lubricant & assembling all parts.
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 2 | Body | Clean body surface for scaling and foreign particles.
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 3 | Seat | Replace if any requirement
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 7 | A.F.R | Clean its air filter & internal parts.
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 8 | Electronic equipment | Veryfied calibration status.
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | 10 | Monitoring Instruments | Check & clean physical condition.
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 1 | Actuator | Unscrew the actuator from bracket
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 1 | Actuator | Proper lubricant & assembling all parts.
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 2 | Body | Clean body surface for scaling and foreign particles.
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 3 | Seat | Replace if any requirement
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 7 | A.F.R | Clean its air filter & internal parts.
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 8 | Electronic equipment | Veryfied calibration status.
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | 10 | Monitoring Instruments | Check & clean physical condition.
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 1 | Actuator | Unscrew the actuator from bracket
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 1 | Actuator | Check the actuator kit & adjustable spring.
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 1 | Actuator | Proper lubricant & assembling all parts.
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 2 | Body | Check physical condition. | [5 empty] | Yes
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 2 | Body | Clean body surface for scaling and foreign particles.
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 3 | Seat | Replace if any requirement
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 4 | Plug | Clean body surface for scaling and foreign particles.
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 7 | A.F.R | Clean its air filter & internal parts.
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 8 | Electronic equipment | Veryfied calibration status.
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | 9 | Monitoring Instruments | Check & clean physical condition.
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 1 | Sensor | Sensor cleaning & check its shape . | [5 empty] | Yes
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 1 | Sensor | Check its continuity end the conector.
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 2 | Power supply Card | check Its eatrhing voltage.
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 3 | Microprocessor Unit | Check its output signal
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 5 | Liner | Check its scaling. | [5 empty] | Yes
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 5 | Liner | Check its any deformation parts.
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 6 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 6 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 6 | Electronic equipment | Veryfied calibration status.
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | 8 | Monitoring Instruments | Check & clean physical condition.
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 1 | Sensor | Check its continuity end the conector.
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 2 | Power supply Card | check Its eatrhing voltage.
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 3 | Microprocessor Unit | Check its output signal
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 5 | Liner | Check its any deformation parts.
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 6 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 6 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 6 | Electronic equipment | Veryfied calibration status.
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | 8 | Monitoring Instruments | Check & clean physical condition.
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | 1 | Sensor | Check its continuity end the conector.
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | 2 | Power supply Card | check Its eatrhing voltage.
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | 3 | Microprocessor Unit | Check its output signal
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | 5 | Liner | Check its scaling. | [5 empty] | Yes
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | 5 | Liner | Check its any deformation parts.
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | 7 | Monitoring Instruments | Check & clean physical condition.
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | 1 | Sensor | Check its continuity end the conector.
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | 2 | Power supply Card | check Its eatrhing voltage.
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | 3 | Microprocessor Unit | Check its output signal
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | 5 | Liner | Check its scaling. | [5 empty] | Yes
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | 5 | Liner | Check its any deformation parts.
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | 7 | Monitoring Instruments | Check & clean physical condition.
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | 1 | Sensor | Check its continuity end the conector.
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | 2 | Power supply Card | check Its eatrhing voltage.
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | 3 | Microprocessor Unit | Check its output signal
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | 5 | Liner | Check its scaling. | [5 empty] | Yes
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | 5 | Liner | Check its any deformation parts.
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | 7 | Monitoring Instruments | Check & clean physical condition.
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | 1 | Sensor | Check its continuity end the conector.
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | 2 | Power supply Card | check Its eatrhing voltage.
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | 3 | Microprocessor Unit | Check its output signal
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | 5 | Liner | Check its scaling. | [5 empty] | Yes
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | 5 | Liner | Check its any deformation parts.
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | 7 | Monitoring Instruments | Check & clean physical condition.
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | 1 | Sensor | Check its continuity end the conector.
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | 2 | Power supply Card | check Its eatrhing voltage.
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | 3 | Microprocessor Unit | Check its output signal
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | 5 | Liner | Check its scaling. | [5 empty] | Yes
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | 5 | Liner | Check its any deformation parts.
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | 7 | Monitoring Instruments | Check & clean physical condition.
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | 1 | Sensor | Check its continuity end the conector.
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | 2 | Power supply Card | check Its eatrhing voltage.
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | 3 | Microprocessor Unit | Check its output signal
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | 5 | Liner | Check its scaling. | [5 empty] | Yes
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | 5 | Liner | Check its any deformation parts.
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | 7 | Monitoring Instruments | Check & clean physical condition.
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | 1 | Sensor | Check its continuity end the conector.
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | 2 | Power supply Card | check Its eatrhing voltage.
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | 3 | Microprocessor Unit | Check its output signal
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | 5 | Liner | Check its scaling. | [5 empty] | Yes
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | 5 | Liner | Check its any deformation parts.
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | 7 | Monitoring Instruments | Check & clean physical condition.
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 1 | Sensor | Check its continuity end the conector.
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 2 | Power supply Card | check Its eatrhing voltage.
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 3 | Microprocessor Unit | Check its output signal
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 5 | Liner | Check its any deformation parts.
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 6 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 6 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 6 | Electronic equipment | Veryfied calibration status.
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | 8 | Monitoring Instruments | Check & clean physical condition.
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 1 | Sensor | Check its continuity end the conector.
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 2 | Power supply Card | check Its eatrhing voltage.
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 3 | Microprocessor Unit | Check its output signal
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 5 | Liner | Check its scaling. | [5 empty] | Yes
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 5 | Liner | Check its any deformation parts.
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 6 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 6 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 6 | Electronic equipment | Veryfied calibration status.
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | 8 | Monitoring Instruments | Check & clean physical condition.
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | 1 | Sensor | Check its continuity end the conector.
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | 2 | Power supply Card | check Its eatrhing voltage.
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | 3 | Microprocessor Unit | Check its output signal
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | 5 | Liner | Check its any deformation parts.
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | 7 | Monitoring Instruments | Check & clean physical condition.
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | 1 | Sensor | Check its continuity end the conector.
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | 2 | Power supply Card | check Its eatrhing voltage.
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | 3 | Microprocessor Unit | Check its output signal
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | 5 | Liner | Check its scaling. | [5 empty] | Yes
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | 5 | Liner | Check its any deformation parts.
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | 7 | Monitoring Instruments | Check & clean physical condition.
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | 1 | Sensor | Check its continuity end the conector.
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | 2 | Power supply Card | check Its eatrhing voltage.
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | 3 | Microprocessor Unit | Check its output signal
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | 5 | Liner | Check its scaling. | [5 empty] | Yes
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | 5 | Liner | Check its any deformation parts.
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | 7 | Monitoring Instruments | Check & clean physical condition.
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 1 | Sensor | Check its continuity end the conector.
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 2 | Power supply Card | check Its eatrhing voltage.
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 3 | Microprocessor Unit | Check its output signal
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 5 | Liner | Check its any deformation parts.
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 6 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 6 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 6 | Electronic equipment | Veryfied calibration status.
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | 8 | Monitoring Instruments | Check & clean physical condition.
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | 1 | Sensor | Check its continuity end the conector.
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | 2 | Power supply Card | check Its eatrhing voltage.
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | 3 | Microprocessor Unit | Check its output signal
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | 5 | Liner | Check its any deformation parts.
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | 7 | Monitoring Instruments | Check & clean physical condition.
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 1 | Sensor | Check its continuity end the conector.
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 2 | Power supply Card | check Its eatrhing voltage.
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 3 | Microprocessor Unit | Check its output signal
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 5 | Liner | Check its any deformation parts.
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 6 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 6 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 6 | Electronic equipment | Veryfied calibration status.
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | 8 | Monitoring Instruments | Check & clean physical condition.
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | 1 | Sensor | Check its continuity end the conector.
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | 2 | Power supply Card | check Its eatrhing voltage.
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | 3 | Microprocessor Unit | Check its output signal
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | 5 | Liner | Check its scaling. | [5 empty] | Yes
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | 5 | Liner | Check its any deformation parts.
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | 7 | Monitoring Instruments | Check & clean physical condition.
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | 1 | Sensor | Check its continuity end the conector.
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | 2 | Power supply Card | check Its eatrhing voltage.
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | 3 | Microprocessor Unit | Check its output signal
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | 5 | Liner | Check its scaling. | [5 empty] | Yes
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | 5 | Liner | Check its any deformation parts.
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | 7 | Monitoring Instruments | Check & clean physical condition.
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | 1 | Sensor | Check its continuity end the conector.
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | 2 | Power supply Card | check Its eatrhing voltage.
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | 3 | Microprocessor Unit | Check its output signal
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | 5 | Liner | Check its scaling. | [5 empty] | Yes
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | 5 | Liner | Check its any deformation parts.
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | 7 | Monitoring Instruments | Check & clean physical condition.
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | 1 | Sensor | Check its continuity end the conector.
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | 2 | Power supply Card | check Its eatrhing voltage.
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | 3 | Microprocessor Unit | Check its output signal
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | 5 | Liner | Check its scaling. | [5 empty] | Yes
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | 5 | Liner | Check its any deformation parts.
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | 7 | Monitoring Instruments | Check & clean physical condition.
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | 1 | Sensor | Check its continuity end the conector.
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | 2 | Power supply Card | check Its eatrhing voltage.
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | 3 | Microprocessor Unit | Check its output signal
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | 5 | Liner | Check its scaling. | [5 empty] | Yes
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | 5 | Liner | Check its any deformation parts.
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | 7 | Monitoring Instruments | Check & clean physical condition.
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | 1 | Sensor | Check its continuity end the conector.
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | 2 | Power supply Card | check Its eatrhing voltage.
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | 3 | Microprocessor Unit | Check its output signal
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | 5 | Liner | Check its scaling. | [5 empty] | Yes
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | 5 | Liner | Check its any deformation parts.
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | 7 | Monitoring Instruments | Check & clean physical condition.
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | 1 | Sensor | Check its continuity end the conector.
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | 2 | Power supply Card | check Its eatrhing voltage.
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | 3 | Microprocessor Unit | Check its output signal
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | 5 | Liner | Check its any deformation parts.
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | 7 | Monitoring Instruments | Check & clean physical condition.
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | 1 | Sensor | Check its continuity end the conector.
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | 2 | Power supply Card | check Its eatrhing voltage.
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | 3 | Microprocessor Unit | Check its output signal
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | 5 | Liner | Check its any deformation parts.
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | 7 | Monitoring Instruments | Check & clean physical condition.
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | 1 | Sensor | Check its continuity end the conector.
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | 2 | Power supply Card | check Its eatrhing voltage.
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | 3 | Microprocessor Unit | Check its output signal
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | 5 | Liner | Check its scaling. | [5 empty] | Yes
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | 5 | Liner | Check its any deformation parts.
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | 7 | Monitoring Instruments | Check & clean physical condition.
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | 1 | Sensor | Check its continuity end the conector.
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | 2 | Power supply Card | check Its eatrhing voltage.
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | 3 | Microprocessor Unit | Check its output signal
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | 5 | Liner | Check its any deformation parts.
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | 7 | Monitoring Instruments | Check & clean physical condition.
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | 1 | Sensor | Check its continuity end the conector.
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | 2 | Power supply Card | check Its eatrhing voltage.
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | 3 | Microprocessor Unit | Check its output signal
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | 5 | Liner | Check its any deformation parts.
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | 7 | Monitoring Instruments | Check & clean physical condition.
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | 1 | Sensor | Check its continuity end the conector.
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | 2 | Power supply Card | check Its eatrhing voltage.
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | 3 | Microprocessor Unit | Check its output signal
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | 5 | Liner | Check its any deformation parts.
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | 7 | Monitoring Instruments | Check & clean physical condition.
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | 1 | Sensor | Check its continuity end the conector.
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | 2 | Power supply Card | check Its eatrhing voltage.
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | 3 | Microprocessor Unit | Check its output signal
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | 5 | Liner | Check its scaling. | [5 empty] | Yes
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | 5 | Liner | Check its any deformation parts.
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | 7 | Monitoring Instruments | Check & clean physical condition.
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 1 | Cylinder | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 1 | Cylinder | Unscrew the cylinder from sutter ,bagcamp & bucket
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 1 | Cylinder | Check the cylinder kit & air flow valve
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 1 | Cylinder | Proper lubricant & assembling all parts.
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 2 | Bearing | Check physical condition. | [5 empty] | Yes
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 2 | Bearing | Clean body surface for scaling and foreign particles.
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 3 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 3 | Solenoide Valve | Replace if any requirement
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 4 | Suttar Assembly | Check Bearing condition.
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 4 | Suttar Assembly | Clean body surface for scaling and foreign particles.
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 5 | A.F.R | Check filter Element ,spring ,kit proper cleaning.
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 6 | Loadcell | Check resitance | [5 empty] | Yes
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 6 | Loadcell | Check output supply.
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 6 | Loadcell | Check ground with supply.
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 7 | Calibration | Zero calibration | [5 empty] | Yes
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 7 | Calibration | Calibration done after install at position. (0-100%)
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 8 | Electronic equipment | Veryfied calibration status.
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | 9 | Monitoring Instruments | Check & clean physical condition.
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 1 | Cylinder | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 1 | Cylinder | Unscrew the cylinder from sutter ,bagcamp & bucket
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 1 | Cylinder | Check the cylinder kit & air flow valve
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 1 | Cylinder | Proper lubricant & assembling all parts.
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 2 | Bearing | Check physical condition. | [5 empty] | Yes
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 2 | Bearing | Clean body surface for scaling and foreign particles.
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 3 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 3 | Solenoide Valve | Replace if any requirement
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 4 | Suttar Assembly | Check Bearing condition.
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 4 | Suttar Assembly | Clean body surface for scaling and foreign particles.
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 5 | A.F.R | Check filter Element ,spring ,kit proper cleaning.
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 6 | Loadcell | Check resitance | [5 empty] | Yes
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 6 | Loadcell | Check output supply.
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 6 | Loadcell | Check ground with supply.
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 7 | Calibration | Zero calibration | [5 empty] | Yes
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 7 | Calibration | Calibration done after install at position. (0-100%)
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 8 | Electronic equipment | Veryfied calibration status.
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | 9 | Monitoring Instruments | Check & clean physical condition.
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 1 | Cylinder | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 1 | Cylinder | Unscrew the cylinder from sutter ,bagcamp & bucket
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 1 | Cylinder | Check the cylinder kit & air flow valve
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 1 | Cylinder | Proper lubricant & assembling all parts.
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 2 | Bearing | Check physical condition. | [5 empty] | Yes
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 2 | Bearing | Clean body surface for scaling and foreign particles.
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 3 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 3 | Solenoide Valve | Replace if any requirement
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 4 | Suttar Assembly | Check Bearing condition.
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 4 | Suttar Assembly | Clean body surface for scaling and foreign particles.
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 5 | A.F.R | Check filter lement ,spring ,kit proper cleaning.
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 6 | Loadcell | Check resitance | [5 empty] | Yes
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 6 | Loadcell | Check output supply.
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 6 | Loadcell | Check ground with supply.
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 7 | Calibration | Zero calibration | [5 empty] | Yes
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 7 | Calibration | Calibration done after install at position. (0-100%)
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 8 | Electronic equipment | Veryfied calibration status.
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | 9 | Monitoring Instruments | Check & clean physical condition.
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 1 | Cylinder | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 1 | Cylinder | Unscrew the cylinder from sutter ,bagcamp & bucket
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 1 | Cylinder | Check the cylinder kit & air flow valve
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 1 | Cylinder | Proper lubricant & assembling all parts.
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 2 | Bearing | Check physical condition. | [5 empty] | Yes
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 2 | Bearing | Clean body surface for scaling and foreign particles.
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 3 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 3 | Solenoide Valve | Replace if any requirement
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 4 | Suttar Assembly | Check Bearing condition.
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 4 | Suttar Assembly | Clean body surface for scaling and foreign particles.
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 5 | A.F.R | Check filter lement ,spring ,kit proper cleaning.
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 6 | Loadcell | Check resitance | [5 empty] | Yes
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 6 | Loadcell | Check output supply.
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 6 | Loadcell | Check ground with supply.
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 7 | Calibration | Zero calibration | [5 empty] | Yes
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 7 | Calibration | Calibration done after install at position. (0-100%)
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 8 | Electronic equipment | Veryfied calibration status.
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | 9 | Monitoring Instruments | Check & clean physical condition.
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 1 | Cylinder | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 1 | Cylinder | Unscrew the cylinder from sutter ,bagcamp & bucket
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 1 | Cylinder | Check the cylinder kit & air flow valve
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 1 | Cylinder | Proper lubricant & assembling all parts.
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 2 | Bearing | Check physical condition. | [5 empty] | Yes
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 2 | Bearing | Clean body surface for scaling and foreign particles.
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 3 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 3 | Solenoide Valve | Replace if any requirement
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 4 | Suttar Assembly | Check Bearing condition.
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 4 | Suttar Assembly | Clean body surface for scaling and foreign particles.
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 5 | A.F.R | Check filter lement ,spring ,kit proper cleaning.
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 6 | Loadcell | Check resitance | [5 empty] | Yes
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 6 | Loadcell | Check output supply.
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 6 | Loadcell | Check ground with supply.
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 7 | Calibration | Zero calibration | [5 empty] | Yes
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 7 | Calibration | Calibration done after install at position. (0-100%)
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 8 | Electronic equipment | Veryfied calibration status.
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | 9 | Monitoring Instruments | Check & clean physical condition.
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 1 | Controller | Check physical condition. | [5 empty] | Yes
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 1 | Controller | Clean internal & Extranal Part warm-up
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 2 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 2 | Solenoide Valve | Repair & Replace if any requirement
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 3 | Isolater | Check physical condition.
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 3 | Isolater | Clean internal & Extranal Part warm-up
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 4 | A.F.R | Check filter Element ,spring ,kit proper cleaning.
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 5 | Calibration | Zero calibration | [5 empty] | Yes
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 5 | Calibration | Calibration done after install at position. (0-100%)
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 6 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 6 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 6 | Electronic equipment | Veryfied calibration status.
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | 7 | Monitoring Instruments | Check & clean physical condition.
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | 1 | Controller | Check physical condition. | [5 empty] | Yes
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | 1 | Controller | Clean internal & Extranal Part warm-up
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | 2 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | 2 | Solenoide Valve | Repair & Replace if any requirement
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | 3 | Isolater | Check physical condition.
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | 3 | Isolater | Clean internal & Extranal Part warm-up
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | 4 | A.F.R | Check filter Element ,spring ,kit proper cleaning.
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | 5 | Calibration | Zero calibration | [5 empty] | Yes
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | 5 | Calibration | Calibration done after install at position. (0-100%)
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | 6 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | 6 | Monitoring Instruments | Check & clean physical condition.
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | 1 | Controller | Check physical condition. | [5 empty] | Yes
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | 1 | Controller | Clean internal & Extranal Part warm-up
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | 2 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | 2 | Solenoide Valve | Repair & Replace if any requirement
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | 3 | Isolater | Check physical condition.
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | 3 | Isolater | Clean internal & Extranal Part warm-up
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | 4 | A.F.R | Check filter Element ,spring ,kit proper cleaning.
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | 5 | Calibration | Zero calibration | [5 empty] | Yes
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | 5 | Calibration | Calibration done after install at position. (0-100%)
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | 8 | Monitoring Instruments | Check & clean physical condition.
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | 1 | Controller | Check physical condition. | [5 empty] | Yes
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | 1 | Controller | Clean internal & Extranal Part warm-up
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | 2 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | 2 | Solenoide Valve | Repair & Replace if any requirement
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | 3 | Isolater | Check physical condition.
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | 3 | Isolater | Clean internal & Extranal Part warm-up
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | 4 | A.F.R | Check filter Element ,spring ,kit proper cleaning.
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | 5 | Calibration | Zero calibration | [5 empty] | Yes
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | 5 | Calibration | Calibration done after install at position. (0-100%)
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | 8 | Monitoring Instruments | Check & clean physical condition.
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | 1 | Controller | Check physical condition. | [5 empty] | Yes
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | 1 | Controller | Clean internal & Extranal Part warm-up
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | 2 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | 2 | Solenoide Valve | Repair & Replace if any requirement
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | 3 | Isolater | Check physical condition.
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | 3 | Isolater | Clean internal & Extranal Part warm-up
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | 4 | A.F.R | Check filter Element ,spring ,kit proper cleaning.
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | 5 | Calibration | Zero calibration | [5 empty] | Yes
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | 5 | Calibration | Calibration done after install at position. (0-100%)
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | 8 | Monitoring Instruments | Check & clean physical condition.
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 1 | Controller | Check physical condition. | [5 empty] | Yes
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 1 | Controller | Clean internal & Extranal Part warm-up
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 2 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 2 | Solenoide Valve | Repair & Replace if any requirement
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 3 | Isolater | Check physical condition.
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 3 | Isolater | Clean internal & Extranal Part warm-up
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 4 | A.F.R | Check filter Element ,spring ,kit proper cleaning.
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 5 | Calibration | Zero calibration | [5 empty] | Yes
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 5 | Calibration | Calibration done after install at position. (0-100%)
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 6 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 6 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 6 | Electronic equipment | Veryfied calibration status.
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | 7 | Monitoring Instruments | Check & clean physical condition.
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 1 | Controller | Check physical condition. | [5 empty] | Yes
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 1 | Controller | Clean internal & Extranal Part warm-up
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 2 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 2 | Solenoide Valve | Repair & Replace if any requirement
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 3 | Isolater | Check physical condition.
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 3 | Isolater | Clean internal & Extranal Part warm-up
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 4 | A.F.R | Check filter Element ,spring ,kit proper cleaning.
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 5 | Calibration | Zero calibration | [5 empty] | Yes
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 5 | Calibration | Calibration done after install at position. (0-100%)
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 6 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 6 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 6 | Electronic equipment | Veryfied calibration status.
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | 7 | Monitoring Instruments | Check & clean physical condition.
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | 1 | Controller | Check physical condition. | [5 empty] | Yes
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | 1 | Controller | Clean internal & Extranal Part warm-up
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | 2 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | 3 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | 3 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | 3 | Electronic equipment | Veryfied calibration status.
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | 4 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
4db646afc3ed | CENTRIFUGAL B & C :: ZIL/SUG./001/RAW-CFM-01 | ZIL/SUG./001/RAW-CFM-01 | 4 | Monitoring Instruments | Check & clean physical condition.
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | 1 | Controller | Check physical condition. | [5 empty] | Yes
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | 1 | Controller | Clean internal & Extranal Part warm-up
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | 2 | Calibration | Calibration done after install at position. | [5 empty] | Yes
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | 3 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | 3 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | 3 | Electronic equipment | Veryfied calibration status.
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | 4 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
32e46fdd6380 | CENTRIFUGAL B & C :: ZIL/SUG./001/REF-CFM- 01 | ZIL/SUG./001/REF-CFM- 01 | 4 | Monitoring Instruments | Check & clean physical condition.
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 1 | Solenoide Valve | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 1 | Solenoide Valve | Check Solenoid valve seal kit.
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 1 | Solenoide Valve | Replace if any requirement
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 1 | Solenoide Valve | Proper lubricant & assembling all parts.
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 2 | Press. Switch | Check physical condition. | [5 empty] | Yes
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 2 | Press. Switch | Clean body with calibration check
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 3 | Press. Tx. | Check physical condition.
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 3 | Press. Tx. | Clean body with calibration check
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 4 | Press. Gauge | Check physical condition.
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 4 | Press. Gauge | Clean body with calibration check
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 5 | Temp.Sensor | Check physical condition.
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 5 | Temp.Sensor | Clean body with calibration check
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 6 | Flow Switch | Check physical condition. | [5 empty] | Yes
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 6 | Flow Switch | Check diaphgram
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 6 | Flow Switch | Check output supply.
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 7 | AFR | Check filter Element ,spring ,kit proper cleaning.
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | 8 | Monitoring Instruments | Check & clean physical condition.
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 1 | Solenoide Valve | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 1 | Solenoide Valve | Check Solenoid valve seal kit.
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 1 | Solenoide Valve | Replace if any requirement
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 1 | Solenoide Valve | Proper lubricant & assembling all parts.
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 2 | Press. Switch | Check physical condition. | [5 empty] | Yes
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 2 | Press. Switch | Clean body with calibration check
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 3 | Press. Tx. | Check physical condition.
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 3 | Press. Tx. | Clean body with calibration check
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 4 | Press. Gauge | Check physical condition.
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 4 | Press. Gauge | Clean body with calibration check
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 5 | Temp.Sensor | Check physical condition.
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 5 | Temp.Sensor | Clean body with calibration check
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 6 | Flow Switch | Check physical condition. | [5 empty] | Yes
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 6 | Flow Switch | Check diaphgram
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 6 | Flow Switch | Check output supply.
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 7 | AFR | Check filter Element ,spring ,kit proper cleaning.
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | 8 | Monitoring Instruments | Check & clean physical condition.
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 1 | Solenoide Valve | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 1 | Solenoide Valve | Check Solenoid valve seal kit.
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 1 | Solenoide Valve | Replace if any requirement
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 1 | Solenoide Valve | Proper lubricant & assembling all parts.
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 2 | Press. Switch | Check physical condition. | [5 empty] | Yes
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 2 | Press. Switch | Clean body with calibration check
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 3 | Press. Tx. | Check physical condition.
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 3 | Press. Tx. | Clean body with calibration check
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 4 | Press. Gauge | Check physical condition.
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 4 | Press. Gauge | Clean body with calibration check
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 5 | Temp.Sensor | Check physical condition.
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 5 | Temp.Sensor | Clean body with calibration check
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 6 | Flow Switch | Check physical condition. | [5 empty] | Yes
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 6 | Flow Switch | Check diaphgram
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 6 | Flow Switch | Check output supply.
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 7 | AFR | Check filter Element ,spring ,kit proper cleaning.
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | 8 | Monitoring Instruments | Check & clean physical condition.
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 1 | Solenoide Valve | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 1 | Solenoide Valve | Check Solenoid valve seal kit.
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 1 | Solenoide Valve | Replace if any requirement
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 1 | Solenoide Valve | Proper lubricant & assembling all parts.
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 2 | Press. Switch | Check physical condition. | [5 empty] | Yes
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 2 | Press. Switch | Clean body with calibration check
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 3 | Press. Tx. | Check physical condition.
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 3 | Press. Tx. | Clean body with calibration check
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 4 | Press. Gauge | Check physical condition.
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 4 | Press. Gauge | Clean body with calibration check
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 5 | Temp.Sensor | Check physical condition.
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 5 | Temp.Sensor | Clean body with calibration check
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 6 | Flow Switch | Check physical condition. | [5 empty] | Yes
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 6 | Flow Switch | Check diaphgram
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 6 | Flow Switch | Check output supply.
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 7 | AFR | Check filter Element ,spring ,kit proper cleaning.
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | 8 | Monitoring Instruments | Check & clean physical condition.
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 1 | Solenoide Valve | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 1 | Solenoide Valve | Check Solenoid valve seal kit.
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 1 | Solenoide Valve | Replace if any requirement
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 1 | Solenoide Valve | Proper lubricant & assembling all parts.
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 2 | Controller | Check physical condition. | [5 empty] | Yes
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 2 | Controller | Clean body with calibration check
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 3 | After Filter | Check physical condition.
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 3 | After Filter | Clean body with calibration check
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 4 | Gauge | Check physical condition.
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 4 | Gauge | Clean body with calibration check
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 5 | Drain filter | Check physical condition.
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 5 | Drain filter | Clean with check
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 6 | Carben Ball | Check physical condition.
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 6 | Carben Ball | Clean & drye after filling
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 7 | Alumina Ball | Check physical condition.
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 7 | Alumina Ball | Clean & drye after filling
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 8 | 3 Way Valve | Check physical condition. | [5 empty] | Yes
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 8 | 3 Way Valve | Check diaphgram
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 8 | 3 Way Valve | Check valve passing.
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | 9 | Monitoring Instruments | Check & clean physical condition.
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 1 | Solenoide Valve | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 1 | Solenoide Valve | Check Solenoid valve seal kit.
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 1 | Solenoide Valve | Replace if any requirement
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 1 | Solenoide Valve | Proper lubricant & assembling all parts.
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 2 | Controller | Check physical condition. | [5 empty] | Yes
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 2 | Controller | Clean body with calibration check
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 3 | Filter | Check physical condition.
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 3 | Filter | Clean body with calibration check
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 4 | Gauge | Check physical condition.
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 4 | Gauge | Clean body with calibration check
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 5 | Drain filter | Check physical condition.
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 5 | Drain filter | Clean with check
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 6 | Carben Ball | Check physical condition.
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 6 | Carben Ball | Clean & drye after filling
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 7 | Alumina Ball | Check physical condition.
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 7 | Alumina Ball | Clean & drye after filling
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 8 | 3 Way Valve | Check physical condition. | [5 empty] | Yes
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 8 | 3 Way Valve | Check diaphgram
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 8 | 3 Way Valve | Check valve passing.
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | 9 | Monitoring Instruments | Check & clean physical condition.
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 1 | Auto Feed Panel | Inspection of all Instrument.
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 2 | Actuator | Unscrew the actuator from bracket
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 2 | Actuator | Check the actuator kit & adjustable spring.
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 2 | Actuator | Proper lubricant & assembling all parts.
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 3 | Body | Check physical condition. | [5 empty] | Yes
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 3 | Body | Clean body surface for scaling and foreign particles.
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 4 | Seat | Replace if any requirement
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 5 | Plug | Clean body surface for scaling and foreign particles.
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 6 | Positioner | Check Relay ,cam,spring & kit.
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 6 | Positioner | Check with loop calibrator.
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 7 | A.F.R | Clean its air filter & internal parts.
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 8 | Electronic Equipment | Verfied Calibration Status.
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 9 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 9 | Electrode | Check Air opration
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 9 | Electrode | Check Seal kit & neck bush.
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 10 | Solenoid Valve | Check Air opration
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | 12 | Monitoring Instruments | Check & clean physical condition.
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 1 | Auto Feed Panel | Inspection of all Instrument.
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 2 | Actuator | Unscrew the actuator from bracket
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 2 | Actuator | Check the actuator kit & adjustable spring.
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 2 | Actuator | Proper lubricant & assembling all parts.
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 3 | Body | Check physical condition. | [5 empty] | Yes
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 3 | Body | Clean body surface for scaling and foreign particles.
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 4 | Seat | Replace if any requirement
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 5 | Plug | Clean body surface for scaling and foreign particles.
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 6 | Positioner | Check Relay ,cam,spring & kit.
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 6 | Positioner | Check with loop calibrator.
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 7 | A.F.R | Clean its air filter & internal parts.
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 8 | Electrode | Check Air opration
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 8 | Electrode | Check Seal kit & neck bush.
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 9 | Electronic Equipment | Verfied Calibration Status.
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 10 | Solenoid Valve | Check Air opration
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | 12 | Monitoring Instruments | Check & clean physical condition.
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 1 | Auto Feed Panel | Inspection of all Instrument.
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 2 | Actuator | Unscrew the actuator from bracket
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 2 | Actuator | Check the actuator kit & adjustable spring.
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 2 | Actuator | Proper lubricant & assembling all parts.
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 3 | Body | Check physical condition. | [5 empty] | Yes
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 3 | Body | Clean body surface for scaling and foreign particles.
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 4 | Seat | Replace if any requirement
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 5 | Plug | Clean body surface for scaling and foreign particles.
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 6 | Positioner | Check Relay ,cam,spring & kit.
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 6 | Positioner | Check with loop calibrator.
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 7 | A.F.R | Clean its air filter & internal parts.
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 8 | Electrode | Check Air opration
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 8 | Electrode | Check Seal kit & neck bush.
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 9 | Electronic Equipment | Verfied Calibration Status.
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 10 | Solenoid Valve | Check Air opration
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | 12 | Monitoring Instruments | Check & clean physical condition.
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 1 | Auto Feed Panel | Inspection of all Instrument.
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 2 | Actuator | Unscrew the actuator from bracket
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 2 | Actuator | Check the actuator kit & adjustable spring.
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 2 | Actuator | Proper lubricant & assembling all parts.
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 3 | Body | Check physical condition. | [5 empty] | Yes
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 3 | Body | Clean body surface for scaling and foreign particles.
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 4 | Seat | Replace if any requirement
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 5 | Plug | Clean body surface for scaling and foreign particles.
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 6 | Positioner | Check Relay ,cam,spring & kit.
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 6 | Positioner | Check with loop calibrator.
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 7 | A.F.R | Clean its air filter & internal parts.
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 8 | Electrode | Check Air opration
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 8 | Electrode | Check Seal kit & neck bush.
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 9 | Electronic Equipment | Verfied Calibration Status.
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 10 | Solenoid Valve | Check Air opration
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | 12 | Monitoring Instruments | Check & clean physical condition.
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 1 | Auto Feed Panel | Inspection of all Instrument.
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 2 | Actuator | Unscrew the actuator from bracket
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 2 | Actuator | Check the actuator kit & adjustable spring.
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 2 | Actuator | Proper lubricant & assembling all parts.
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 3 | Body | Check physical condition. | [5 empty] | Yes
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 3 | Body | Clean body surface for scaling and foreign particles.
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 4 | Seat | Replace if any requirement
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 5 | Plug | Clean body surface for scaling and foreign particles.
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 6 | Positioner | Check Relay ,cam,spring & kit.
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 6 | Positioner | Check with loop calibrator.
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 7 | A.F.R | Clean its air filter & internal parts.
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 8 | Electrode | Check Air opration
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 8 | Electrode | Check Seal kit & neck bush.
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 9 | Electronic Equipment | Verfied Calibration Status.
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 10 | Solenoid Valve | Check Air opration
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | 12 | Monitoring Instruments | Check & clean physical condition.
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 1 | Auto Feed Panel | Inspection of all Instrument.
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 2 | Actuator | Unscrew the actuator from bracket
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 2 | Actuator | Check the actuator kit & adjustable spring.
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 2 | Actuator | Proper lubricant & assembling all parts.
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 3 | Body | Check physical condition. | [5 empty] | Yes
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 3 | Body | Clean body surface for scaling and foreign particles.
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 4 | Seat | Replace if any requirement
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 5 | Plug | Clean body surface for scaling and foreign particles.
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 6 | Positioner | Check Relay ,cam,spring & kit.
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 6 | Positioner | Check with loop calibrator.
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 7 | A.F.R | Clean its air filter & internal parts.
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 8 | Electrode | Check Air opration
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 8 | Electrode | Check Seal kit & neck bush.
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 9 | Electronic Equipment | Verfied Calibration Status.
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 10 | Solenoid Valve | Check Air opration
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | 12 | Monitoring Instruments | Check & clean physical condition.
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 1 | Auto Feed Panel | Inspection of all Instrument.
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 2 | Actuator | Unscrew the actuator from bracket
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 2 | Actuator | Check the actuator kit & adjustable spring.
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 2 | Actuator | Proper lubricant & assembling all parts.
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 3 | Body | Check physical condition. | [5 empty] | Yes
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 3 | Body | Clean body surface for scaling and foreign particles.
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 4 | Seat | Replace if any requirement
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 5 | Plug | Clean body surface for scaling and foreign particles.
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 6 | Positioner | Check Relay ,cam,spring & kit.
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 6 | Positioner | Check with loop calibrator.
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 7 | A.F.R | Clean its air filter & internal parts.
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 8 | Electrode | Check Air opration
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 8 | Electrode | Check Seal kit & neck bush.
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 9 | Electronic Equipment | Verfied Calibration Status.
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 10 | Solenoid Valve | Check Air opration
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | 12 | Monitoring Instruments | Check & clean physical condition.
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 1 | Auto Feed Panel | Inspection of all Instrument.
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 2 | Actuator | Unscrew the actuator from bracket
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 2 | Actuator | Check the actuator kit & adjustable spring.
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 2 | Actuator | Proper lubricant & assembling all parts.
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 3 | Body | Check physical condition. | [5 empty] | Yes
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 3 | Body | Clean body surface for scaling and foreign particles.
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 4 | Seat | Replace if any requirement
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 5 | Plug | Clean body surface for scaling and foreign particles.
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 6 | Positioner | Check Relay ,cam,spring & kit.
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 6 | Positioner | Check with loop calibrator.
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 7 | A.F.R | Clean its air filter & internal parts.
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 8 | Electrode | Check Air opration
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 8 | Electrode | Check Seal kit & neck bush.
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 9 | Electronic Equipment | Verfied Calibration Status.
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 10 | Solenoid Valve | Check Air opration
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | 12 | Monitoring Instruments | Check & clean physical condition.
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 1 | Auto Feed Panel | Inspection of all Instrument.
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 2 | Actuator | Unscrew the actuator from bracket
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 2 | Actuator | Check the actuator kit & adjustable spring.
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 2 | Actuator | Proper lubricant & assembling all parts.
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 3 | Body | Check physical condition. | [5 empty] | Yes
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 3 | Body | Clean body surface for scaling and foreign particles.
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 4 | Seat | Replace if any requirement
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 5 | Plug | Clean body surface for scaling and foreign particles.
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 6 | Positioner | Check Relay ,cam,spring & kit.
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 6 | Positioner | Check with loop calibrator.
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 7 | A.F.R | Clean its air filter & internal parts.
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 8 | Electronic Equipment | Verfied Calibration Status.
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 9 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 9 | Electrode | Check Air opration
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 9 | Electrode | Check Seal kit & neck bush.
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 10 | Solenoid Valve | Check Air opration
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | 12 | Monitoring Instruments | Check & clean physical condition.
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 1 | Auto Feed Panel | Inspection of all Instrument.
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 2 | Actuator | Unscrew the actuator from bracket
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 2 | Actuator | Check the actuator kit & adjustable spring.
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 2 | Actuator | Proper lubricant & assembling all parts.
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 3 | Body | Check physical condition. | [5 empty] | Yes
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 3 | Body | Clean body surface for scaling and foreign particles.
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 4 | Seat | Replace if any requirement
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 5 | Plug | Clean body surface for scaling and foreign particles.
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 6 | Positioner | Check Relay ,cam,spring & kit.
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 6 | Positioner | Check with loop calibrator.
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 7 | A.F.R | Clean its air filter & internal parts.
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 8 | Electrode | Check Air opration
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 8 | Electrode | Check Seal kit & neck bush.
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 9 | Electronic Equipment | Verfied Calibration Status.
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 10 | Solenoid Valve | Check Air opration
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | 12 | Monitoring Instruments | Check & clean physical condition.
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 1 | Auto Feed Panel | Inspection of all Instrument.
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 2 | Actuator | Unscrew the actuator from bracket
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 2 | Actuator | Check the actuator kit & adjustable spring.
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 2 | Actuator | Proper lubricant & assembling all parts.
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 3 | Body | Check physical condition. | [5 empty] | Yes
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 3 | Body | Clean body surface for scaling and foreign particles.
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 4 | Seat | Replace if any requirement
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 5 | Plug | Clean body surface for scaling and foreign particles.
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 6 | Positioner | Check Relay ,cam,spring & kit.
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 6 | Positioner | Check with loop calibrator.
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 7 | A.F.R | Clean its air filter & internal parts.
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 8 | Electrode | Check Air opration
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 8 | Electrode | Check Seal kit & neck bush.
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 9 | Electronic Equipment | Verfied Calibration Status.
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 10 | Solenoid Valve | Check Air opration
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | 12 | Monitoring Instruments | Check & clean physical condition.
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 1 | Auto Feed Panel | Inspection of all Instrument.
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 2 | Actuator | Unscrew the actuator from bracket
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 2 | Actuator | Check the actuator kit & adjustable spring.
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 2 | Actuator | Proper lubricant & assembling all parts.
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 3 | Body | Check physical condition. | [5 empty] | Yes
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 3 | Body | Clean body surface for scaling and foreign particles.
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 4 | Seat | Replace if any requirement
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 5 | Plug | Clean body surface for scaling and foreign particles.
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 6 | Positioner | Check Relay ,cam,spring & kit.
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 6 | Positioner | Check with loop calibrator.
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 7 | A.F.R | Clean its air filter & internal parts.
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 8 | Electrode | Check Air opration
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 8 | Electrode | Check Seal kit & neck bush.
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 9 | Electronic Equipment | Verfied Calibration Status.
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 10 | Solenoid Valve | Check Air opration
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | 12 | Monitoring Instruments | Check & clean physical condition.
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 1 | Auto Feed Panel | Inspection of all Instrument.
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 2 | Actuator | Unscrew the actuator from bracket
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 2 | Actuator | Check the actuator kit & adjustable spring.
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 2 | Actuator | Proper lubricant & assembling all parts.
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 3 | Body | Check physical condition. | [5 empty] | Yes
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 3 | Body | Clean body surface for scaling and foreign particles.
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 4 | Seat | Replace if any requirement
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 5 | Plug | Clean body surface for scaling and foreign particles.
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 6 | Positioner | Check Relay ,cam,spring & kit.
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 6 | Positioner | Check with loop calibrator.
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 7 | A.F.R | Clean its air filter & internal parts.
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 8 | Electrode | Check Air opration
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 8 | Electrode | Check Seal kit & neck bush.
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 9 | Electronic Equipment | Verfied Calibration Status.
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 10 | Solenoid Valve | Check Air opration
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | 12 | Monitoring Instruments | Check & clean physical condition.
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 1 | Auto Feed Panel | Inspection of all Instrument.
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 2 | Actuator | Unscrew the actuator from bracket
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 2 | Actuator | Check the actuator kit & adjustable spring.
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 2 | Actuator | Proper lubricant & assembling all parts.
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 3 | Body | Check physical condition. | [5 empty] | Yes
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 3 | Body | Clean body surface for scaling and foreign particles.
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 4 | Seat | Replace if any requirement
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 5 | Plug | Clean body surface for scaling and foreign particles.
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 6 | Positioner | Check Relay ,cam,spring & kit.
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 6 | Positioner | Check with loop calibrator.
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 7 | A.F.R | Clean its air filter & internal parts.
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 8 | Electrode | Check Air opration
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 8 | Electrode | Check Seal kit & neck bush.
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 9 | Electronic Equipment | Verfied Calibration Status.
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 10 | Solenoid Valve | Check Air opration
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | 12 | Monitoring Instruments | Check & clean physical condition.
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 1 | Auto Feed Panel | Inspection of all Instrument.
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 2 | Actuator | Unscrew the actuator from bracket
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 2 | Actuator | Check the actuator kit & adjustable spring.
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 2 | Actuator | Proper lubricant & assembling all parts.
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 3 | Body | Check physical condition. | [5 empty] | Yes
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 3 | Body | Clean body surface for scaling and foreign particles.
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 4 | Seat | Replace if any requirement
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 5 | Plug | Clean body surface for scaling and foreign particles.
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 6 | Positioner | Check Relay ,cam,spring & kit.
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 6 | Positioner | Check with loop calibrator.
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 7 | A.F.R | Clean its air filter & internal parts.
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 8 | Electrode | Check Air opration
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 8 | Electrode | Check Seal kit & neck bush.
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 9 | Electronic Equipment | Verfied Calibration Status.
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 10 | Solenoid Valve | Check Air opration
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | 12 | Monitoring Instruments | Check & clean physical condition.
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 1 | Auto Feed Panel | Check physical condition internal & External | [5 empty] | Yes
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 1 | Auto Feed Panel | Remove all air accessories. Like Controller & Indicator etc.
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 1 | Auto Feed Panel | Check the Contol card & all terminals Clean it
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 1 | Auto Feed Panel | Check panel to all field loop & Body leval sensor
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 1 | Auto Feed Panel | Inspection of all Instrument.
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 1 | Auto Feed Panel | Calibration done after install at position. (0-100%)
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 2 | Actuator | Unscrew the actuator from bracket
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 2 | Actuator | Check the actuator kit & adjustable spring.
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 2 | Actuator | Proper lubricant & assembling all parts.
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 3 | Body | Check physical condition. | [5 empty] | Yes
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 3 | Body | Clean body surface for scaling and foreign particles.
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 4 | Seat | Replace if any requirement
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 5 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 5 | Plug | Clean body surface for scaling and foreign particles.
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 6 | Positioner | Check Relay ,cam,spring & kit.
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 6 | Positioner | Check with loop calibrator.
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 7 | A.F.R | Clean its air filter & internal parts.
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 8 | Electrode | Clean its air kit & internal parts. | [5 empty] | Yes
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 8 | Electrode | Check Air opration
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 8 | Electrode | Check Seal kit & neck bush.
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 9 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 9 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 9 | Electronic Equipment | Verfied Calibration Status.
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 10 | Solenoid Valve | Clean its air kit & internal parts. | [5 empty] | Yes
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 10 | Solenoid Valve | Check Air opration
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 11 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 12 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | 12 | Monitoring Instruments | Check & clean physical condition.
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 1 | Actuator | Unscrew the actuator from bracket
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 1 | Actuator | Check the actuator kit & adjustable spring.
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 1 | Actuator | Proper lubricant & assembling all parts.
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 2 | Body | Check physical condition. | [5 empty] | Yes
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 2 | Body | Clean body surface for scaling and foreign particles.
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 3 | Seat | Replace if any requirement
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 4 | Plug | Clean body surface for scaling and foreign particles.
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 5 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 5 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 5 | Electronic Equipment | Verfied Calibration Status.
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 6 | A.F.R | Check Air output supply. | [5 empty] | Yes
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 6 | A.F.R | Clean its air filter & internal parts.
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | 8 | Monitoring Instruments | Check & clean physical condition.
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 1 | Actuator | Unscrew the actuator from bracket
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 1 | Actuator | Check the actuator kit & adjustable spring.
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 1 | Actuator | Proper lubricant & assembling all parts.
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 2 | Body | Check physical condition. | [5 empty] | Yes
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 2 | Body | Clean body surface for scaling and foreign particles.
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 3 | Seat | Replace if any requirement
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 4 | Plug | Clean body surface for scaling and foreign particles.
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 5 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 5 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 5 | Electronic Equipment | Verfied Calibration Status.
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 6 | A.F.R | Check Air output supply. | [5 empty] | Yes
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 6 | A.F.R | Clean its air filter & internal parts.
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | 8 | Monitoring Instruments | Check & clean physical condition.
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 1 | Actuator | Unscrew the actuator from bracket
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 1 | Actuator | Check the actuator kit & adjustable spring.
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 1 | Actuator | Proper lubricant & assembling all parts.
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 2 | Body | Check physical condition. | [5 empty] | Yes
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 2 | Body | Clean body surface for scaling and foreign particles.
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 3 | Seat | Replace if any requirement
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 4 | Plug | Clean body surface for scaling and foreign particles.
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 5 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 5 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 5 | Electronic Equipment | Verfied Calibration Status.
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 6 | A.F.R | Check Air output supply. | [5 empty] | Yes
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 6 | A.F.R | Clean its air filter & internal parts.
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | 8 | Monitoring Instruments | Check & clean physical condition.
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 1 | Actuator | Unscrew the actuator from bracket
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 1 | Actuator | Check the actuator kit & adjustable spring.
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 1 | Actuator | Proper lubricant & assembling all parts.
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 2 | Body | Check physical condition. | [5 empty] | Yes
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 2 | Body | Clean body surface for scaling and foreign particles.
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 3 | Seat | Replace if any requirement
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 4 | Plug | Clean body surface for scaling and foreign particles.
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 5 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 5 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 5 | Electronic Equipment | Verfied Calibration Status.
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 6 | A.F.R | Check Air output supply. | [5 empty] | Yes
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 6 | A.F.R | Clean its air filter & internal parts.
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | 8 | Monitoring Instruments | Check & clean physical condition.
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 1 | Actuator | Unscrew the actuator from bracket
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 1 | Actuator | Check the actuator kit & adjustable spring.
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 1 | Actuator | Proper lubricant & assembling all parts.
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 2 | Body | Check physical condition. | [5 empty] | Yes
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 2 | Body | Clean body surface for scaling and foreign particles.
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 3 | Seat | Replace if any requirement
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 4 | Plug | Clean body surface for scaling and foreign particles.
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 5 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 5 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 5 | Electronic Equipment | Verfied Calibration Status.
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 6 | A.F.R | Check Air output supply. | [5 empty] | Yes
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 6 | A.F.R | Clean its air filter & internal parts.
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | 8 | Monitoring Instruments | Check & clean physical condition.
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 1 | Actuator | Unscrew the actuator from bracket
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 1 | Actuator | Check the actuator kit & adjustable spring.
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 1 | Actuator | Proper lubricant & assembling all parts.
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 2 | Body | Check physical condition. | [5 empty] | Yes
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 2 | Body | Clean body surface for scaling and foreign particles.
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 3 | Seat | Replace if any requirement
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 4 | Plug | Clean body surface for scaling and foreign particles.
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 5 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 5 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 5 | Electronic Equipment | Verfied Calibration Status.
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 6 | A.F.R | Check Air output supply. | [5 empty] | Yes
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 6 | A.F.R | Clean its air filter & internal parts.
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | 8 | Monitoring Instruments | Check & clean physical condition.
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 1 | Actuator | Unscrew the actuator from bracket
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 1 | Actuator | Check the actuator kit & adjustable spring.
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 1 | Actuator | Proper lubricant & assembling all parts.
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 2 | Body | Check physical condition. | [5 empty] | Yes
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 2 | Body | Clean body surface for scaling and foreign particles.
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 3 | Seat | Replace if any requirement
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 4 | Plug | Clean body surface for scaling and foreign particles.
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 5 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 5 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 5 | Electronic Equipment | Verfied Calibration Status.
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 6 | A.F.R | Check Air output supply. | [5 empty] | Yes
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 6 | A.F.R | Clean its air filter & internal parts.
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | 8 | Monitoring Instruments | Check & clean physical condition.
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 1 | Actuator | Unscrew the actuator from bracket
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 1 | Actuator | Check the actuator kit & adjustable spring.
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 1 | Actuator | Proper lubricant & assembling all parts.
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 2 | Body | Check physical condition. | [5 empty] | Yes
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 2 | Body | Clean body surface for scaling and foreign particles.
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 3 | Seat | Replace if any requirement
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 4 | Plug | Clean body surface for scaling and foreign particles.
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 6 | Positioner | Check Relay ,cam,spring & kit.
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 6 | Positioner | Check with loop calibrator.
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 7 | Electronic Equipment | Verfied Calibration Status.
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 8 | A.F.R | Clean its air filter & internal parts.
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | 10 | Monitoring Instruments | Check & clean physical condition.
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 1 | Actuator | Unscrew the actuator from bracket
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 1 | Actuator | Check the actuator kit & adjustable spring.
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 1 | Actuator | Proper lubricant & assembling all parts.
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 2 | Body | Check physical condition. | [5 empty] | Yes
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 2 | Body | Clean body surface for scaling and foreign particles.
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 3 | Seat | Replace if any requirement
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 4 | Plug | Clean body surface for scaling and foreign particles.
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 6 | Positioner | Check Relay ,cam,spring & kit.
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 6 | Positioner | Check with loop calibrator.
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 7 | Electronic Equipment | Verfied Calibration Status.
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 8 | A.F.R | Clean its air filter & internal parts.
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | 10 | Monitoring Instruments | Check & clean physical condition.
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 1 | Actuator | Unscrew the actuator from bracket
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 1 | Actuator | Check the actuator kit & adjustable spring.
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 1 | Actuator | Proper lubricant & assembling all parts.
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 2 | Body | Check physical condition. | [5 empty] | Yes
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 2 | Body | Clean body surface for scaling and foreign particles.
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 3 | Seat | Replace if any requirement
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 4 | Plug | Clean body surface for scaling and foreign particles.
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 6 | Positioner | Check Relay ,cam,spring & kit.
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 6 | Positioner | Check with loop calibrator.
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 7 | Electronic Equipment | Verfied Calibration Status.
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 8 | A.F.R | Clean its air filter & internal parts.
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | 10 | Monitoring Instruments | Check & clean physical condition.
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 1 | Actuator | Unscrew the actuator from bracket
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 1 | Actuator | Check the actuator kit & adjustable spring.
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 1 | Actuator | Proper lubricant & assembling all parts.
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 2 | Body | Check physical condition. | [5 empty] | Yes
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 2 | Body | Clean body surface for scaling and foreign particles.
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 3 | Seat | Replace if any requirement
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 4 | Plug | Clean body surface for scaling and foreign particles.
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 6 | Positioner | Check Relay ,cam,spring & kit.
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 6 | Positioner | Check with loop calibrator.
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 7 | Electronic Equipment | Verfied Calibration Status.
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 8 | A.F.R | Clean its air filter & internal parts.
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | 10 | Monitoring Instruments | Check & clean physical condition.
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 1 | Actuator | Unscrew the actuator from bracket
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 1 | Actuator | Check the actuator kit & adjustable spring.
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 1 | Actuator | Proper lubricant & assembling all parts.
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 2 | Body | Check physical condition. | [5 empty] | Yes
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 2 | Body | Clean body surface for scaling and foreign particles.
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 3 | Seat | Replace if any requirement
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 4 | Plug | Check leakage & Scaling condition.
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 4 | Plug | Clean body surface for scaling and foreign particles.
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 6 | Positioner | Check Relay ,cam,spring & kit.
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 6 | Positioner | Check with loop calibrator.
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 7 | Electronic Equipment | Verfied Calibration Status.
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 8 | A.F.R | Clean its air filter & internal parts.
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | 10 | Monitoring Instruments | Check & clean physical condition.
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 1 | Actuator | Unscrew the actuator from bracket
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 1 | Actuator | Check the actuator kit & adjustable spring.
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 1 | Actuator | Proper lubricant & assembling all parts.
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 2 | Body | Check physical condition. | [5 empty] | Yes
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 2 | Body | Clean body surface for scaling and foreign particles.
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 3 | Seat | Replace if any requirement
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 4 | Plug | Clean body surface for scaling and foreign particles.
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 6 | Positioner | Check Relay ,cam,spring & kit.
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 6 | Positioner | Check with loop calibrator.
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 7 | Electronic Equipment | Verfied Calibration Status.
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 8 | A.F.R | Clean its air filter & internal parts.
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | 10 | Monitoring Instruments | Check & clean physical condition.
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 1 | Actuator | Unscrew the actuator from bracket
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 1 | Actuator | Check the actuator kit & adjustable spring.
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 1 | Actuator | Proper lubricant & assembling all parts.
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 2 | Body | Check physical condition. | [5 empty] | Yes
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 2 | Body | Clean body surface for scaling and foreign particles.
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 3 | Seat | Replace if any requirement
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 4 | Plug | Clean body surface for scaling and foreign particles.
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 6 | Positioner | Check Relay ,cam,spring & kit.
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 6 | Positioner | Check with loop calibrator.
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 7 | Electronic Equipment | Verfied Calibration Status.
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 8 | A.F.R | Clean its air filter & internal parts.
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | 10 | Monitoring Instruments | Check & clean physical condition.
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 1 | Actuator | Unscrew the actuator from bracket
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 1 | Actuator | Check the actuator kit & adjustable spring.
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 1 | Actuator | Proper lubricant & assembling all parts.
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 2 | Body | Check physical condition. | [5 empty] | Yes
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 2 | Body | Clean body surface for scaling and foreign particles.
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 3 | Seat | Replace if any requirement
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 4 | Plug | Clean body surface for scaling and foreign particles.
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 6 | Positioner | Check Relay ,cam,spring & kit.
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 6 | Positioner | Check with loop calibrator.
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 7 | Electronic Equipment | Verfied Calibration Status.
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 8 | A.F.R | Clean its air filter & internal parts.
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | 10 | Monitoring Instruments | Check & clean physical condition.
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 1 | Actuator | Unscrew the actuator from bracket
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 1 | Actuator | Check the actuator kit & adjustable spring.
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 1 | Actuator | Proper lubricant & assembling all parts.
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 2 | Body | Check physical condition. | [5 empty] | Yes
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 2 | Body | Clean body surface for scaling and foreign particles.
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 3 | Seat | Replace if any requirement
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 4 | Plug | Clean body surface for scaling and foreign particles.
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 6 | Positioner | Check Relay ,cam,spring & kit.
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 6 | Positioner | Check with loop calibrator.
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 7 | Electronic Equipment | Verfied Calibration Status.
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 8 | A.F.R | Clean its air filter & internal parts.
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | 10 | Monitoring Instruments | Check & clean physical condition.
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 1 | Actuator | Unscrew the actuator from bracket
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 1 | Actuator | Check the actuator kit & adjustable spring.
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 1 | Actuator | Proper lubricant & assembling all parts.
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 2 | Body | Check physical condition. | [5 empty] | Yes
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 2 | Body | Clean body surface for scaling and foreign particles.
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 3 | Seat | Replace if any requirement
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 4 | Plug | Clean body surface for scaling and foreign particles.
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 6 | Positioner | Check Relay ,cam,spring & kit.
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 6 | Positioner | Check with loop calibrator.
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 7 | Electronic Equipment | Verfied Calibration Status.
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 8 | A.F.R | Clean its air filter & internal parts.
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | 10 | Monitoring Instruments | Check & clean physical condition.
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 1 | Actuator | Unscrew the actuator from bracket
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 1 | Actuator | Check the actuator kit & adjustable spring.
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 1 | Actuator | Proper lubricant & assembling all parts.
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 2 | Body | Check physical condition. | [5 empty] | Yes
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 2 | Body | Clean body surface for scaling and foreign particles.
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 3 | Seat | Replace if any requirement
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 4 | Plug | Clean body surface for scaling and foreign particles.
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 6 | Positioner | Check Relay ,cam,spring & kit.
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 6 | Positioner | Check with loop calibrator.
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 7 | Electronic Equipment | Verfied Calibration Status.
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 8 | A.F.R | Clean its air filter & internal parts.
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | 10 | Monitoring Instruments | Check & clean physical condition.
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 1 | Actuator | Unscrew the actuator from bracket
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 1 | Actuator | Check the actuator kit & adjustable spring.
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 1 | Actuator | Proper lubricant & assembling all parts.
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 2 | Body | Check physical condition. | [5 empty] | Yes
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 2 | Body | Clean body surface for scaling and foreign particles.
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 3 | Seat | Replace if any requirement
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 4 | Plug | Clean body surface for scaling and foreign particles.
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 6 | Positioner | Check Relay ,cam,spring & kit.
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 6 | Positioner | Check with loop calibrator.
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 7 | Electronic Equipment | Verfied Calibration Status.
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 8 | A.F.R | Clean its air filter & internal parts.
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | 10 | Monitoring Instruments | Check & clean physical condition.
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 1 | Actuator | Unscrew the actuator from bracket
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 1 | Actuator | Check the actuator kit & adjustable spring.
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 1 | Actuator | Proper lubricant & assembling all parts.
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 2 | Body | Check physical condition. | [5 empty] | Yes
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 2 | Body | Clean body surface for scaling and foreign particles.
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 3 | Seat | Replace if any requirement
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 4 | Plug | Clean body surface for scaling and foreign particles.
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 6 | Positioner | Check Relay ,cam,spring & kit.
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 6 | Positioner | Check with loop calibrator.
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 7 | Electronic Equipment | Verfied Calibration Status.
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 7 | A.F.R | Clean its air filter & internal parts.
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | 9 | Monitoring Instruments | Check & clean physical condition.
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 1 | Actuator | Unscrew the actuator from bracket
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 1 | Actuator | Check the actuator kit & adjustable spring.
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 1 | Actuator | Proper lubricant & assembling all parts.
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 2 | Body | Check physical condition. | [5 empty] | Yes
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 2 | Body | Clean body surface for scaling and foreign particles.
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 3 | Seat | Replace if any requirement
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 4 | Plug | Clean body surface for scaling and foreign particles.
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 6 | Positioner | Check Relay ,cam,spring & kit.
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 6 | Positioner | Check with loop calibrator.
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 7 | Electronic Equipment | Verfied Calibration Status.
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 8 | A.F.R | Clean its air filter & internal parts.
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | 10 | Monitoring Instruments | Check & clean physical condition.
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 1 | Actuator | Unscrew the actuator from bracket
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 1 | Actuator | Check the actuator kit & adjustable spring.
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 1 | Actuator | Proper lubricant & assembling all parts.
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 2 | Body | Check physical condition. | [5 empty] | Yes
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 2 | Body | Clean body surface for scaling and foreign particles.
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 3 | Seat | Replace if any requirement
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 4 | Plug | Clean body surface for scaling and foreign particles.
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 6 | Positioner | Check Relay ,cam,spring & kit.
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 6 | Positioner | Check with loop calibrator.
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 7 | Electronic Equipment | Verfied Calibration Status.
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 8 | A.F.R | Clean its air filter & internal parts.
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | 10 | Monitoring Instruments | Check & clean physical condition.
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 1 | Actuator | Unscrew the actuator from bracket
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 1 | Actuator | Check the actuator kit & adjustable spring.
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 1 | Actuator | Proper lubricant & assembling all parts.
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 2 | Body | Check physical condition. | [5 empty] | Yes
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 2 | Body | Clean body surface for scaling and foreign particles.
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 3 | Seat | Replace if any requirement
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 4 | Plug | Clean body surface for scaling and foreign particles.
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 6 | Solenoid valve | Clean its air kit & internal parts. | [5 empty] | Yes
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 6 | Solenoid valve | Check Air opration
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 7 | A.F.R | Clean its air filter & internal parts.
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 9 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 9 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 9 | Electronic equipment | Veryfied calibration status.
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | 10 | Monitoring Instruments | Check & clean physical condition.
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 1 | Actuator | Unscrew the actuator from bracket
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 1 | Actuator | Check the actuator kit & adjustable spring.
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 1 | Actuator | Proper lubricant & assembling all parts.
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 2 | Body | Check physical condition. | [5 empty] | Yes
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 2 | Body | Clean body surface for scaling and foreign particles.
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 3 | Seat | Replace if any requirement
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 4 | Plug | Clean body surface for scaling and foreign particles.
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 6 | Positioner | Check Relay ,cam,spring & kit.
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 6 | Positioner | Check with loop calibrator.
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 7 | Electronic Equipment | Verfied Calibration Status.
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 8 | A.F.R | Clean its air filter & internal parts.
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | 10 | Monitoring Instruments | Check & clean physical condition.
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 1 | Actuator | Unscrew the actuator from bracket
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 1 | Actuator | Check the actuator kit & adjustable spring.
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 1 | Actuator | Proper lubricant & assembling all parts.
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 2 | Body | Check physical condition. | [5 empty] | Yes
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 2 | Body | Clean body surface for scaling and foreign particles.
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 3 | Seat | Replace if any requirement
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 4 | Plug | Clean body surface for scaling and foreign particles.
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 6 | Positioner | Check Relay ,cam,spring & kit.
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 6 | Positioner | Check with loop calibrator.
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 7 | Electronic Equipment | Verfied Calibration Status.
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 8 | A.F.R | Clean its air filter & internal parts.
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | 10 | Monitoring Instruments | Check & clean physical condition.
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 1 | Actuator | Unscrew the actuator from bracket
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 1 | Actuator | Check the actuator kit & adjustable spring.
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 1 | Actuator | Proper lubricant & assembling all parts.
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 2 | Body | Check physical condition. | [5 empty] | Yes
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 2 | Body | Clean body surface for scaling and foreign particles.
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 3 | Seat | Replace if any requirement
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 4 | Plug | Clean body surface for scaling and foreign particles.
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 6 | Positioner | Check Relay ,cam,spring & kit.
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 6 | Positioner | Check with loop calibrator.
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 7 | Electronic Equipment | Verfied Calibration Status.
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 8 | A.F.R | Clean its air filter & internal parts.
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | 10 | Monitoring Instruments | Check & clean physical condition.
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 1 | Actuator | Unscrew the actuator from bracket
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 1 | Actuator | Check the actuator kit & adjustable spring.
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 1 | Actuator | Proper lubricant & assembling all parts.
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 2 | Body | Check physical condition. | [5 empty] | Yes
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 2 | Body | Clean body surface for scaling and foreign particles.
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 3 | Seat | Replace if any requirement
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 4 | Plug | Clean body surface for scaling and foreign particles.
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 6 | Positioner | Check Relay ,cam,spring & kit.
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 6 | Positioner | Check with loop calibrator.
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 7 | Electronic Equipment | Verfied Calibration Status.
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 8 | A.F.R | Clean its air filter & internal parts.
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | 10 | Monitoring Instruments | Check & clean physical condition.
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 1 | Actuator | Unscrew the actuator from bracket
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 1 | Actuator | Check the actuator kit & adjustable spring.
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 1 | Actuator | Proper lubricant & assembling all parts.
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 2 | Body | Check physical condition. | [5 empty] | Yes
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 2 | Body | Clean body surface for scaling and foreign particles.
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 3 | Seat | Replace if any requirement
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 4 | Plug | Clean body surface for scaling and foreign particles.
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 6 | Positioner | Check Relay ,cam,spring & kit.
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 6 | Positioner | Check with loop calibrator.
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 7 | Electronic Equipment | Verfied Calibration Status.
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 8 | A.F.R | Clean its air filter & internal parts.
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | 10 | Monitoring Instruments | Check & clean physical condition.
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 1 | Actuator | Unscrew the actuator from bracket
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 1 | Actuator | Check the actuator kit & adjustable spring.
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 1 | Actuator | Proper lubricant & assembling all parts.
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 2 | Body | Check physical condition. | [5 empty] | Yes
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 2 | Body | Clean body surface for scaling and foreign particles.
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 3 | Seat | Replace if any requirement
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 4 | Plug | Clean body surface for scaling and foreign particles.
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 6 | Positioner | Check Relay ,cam,spring & kit.
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 6 | Positioner | Check with loop calibrator.
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 7 | Electronic Equipment | Verfied Calibration Status.
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 8 | A.F.R | Clean its air filter & internal parts.
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | 10 | Monitoring Instruments | Check & clean physical condition.
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 1 | Actuator | Unscrew the actuator from bracket
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 1 | Actuator | Check the actuator kit & adjustable spring.
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 1 | Actuator | Proper lubricant & assembling all parts.
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 2 | Body | Check physical condition. | [5 empty] | Yes
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 2 | Body | Clean body surface for scaling and foreign particles.
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 3 | Seat | Replace if any requirement
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 4 | Plug | Clean body surface for scaling and foreign particles.
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 6 | Positioner | Check Relay ,cam,spring & kit.
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 6 | Positioner | Check with loop calibrator.
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 7 | Electronic Equipment | Verfied Calibration Status.
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 8 | A.F.R | Clean its air filter & internal parts.
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | 10 | Monitoring Instruments | Check & clean physical condition.
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 1 | Actuator | Unscrew the actuator from bracket
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 1 | Actuator | Check the actuator kit & adjustable spring.
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 1 | Actuator | Proper lubricant & assembling all parts.
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 2 | Body | Check physical condition. | [5 empty] | Yes
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 2 | Body | Clean body surface for scaling and foreign particles.
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 3 | Seat | Replace if any requirement
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 4 | Plug | Clean body surface for scaling and foreign particles.
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 6 | Positioner | Check Relay ,cam,spring & kit.
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 6 | Positioner | Check with loop calibrator.
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 7 | Electronic Equipment | Verfied Calibration Status.
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 8 | A.F.R | Clean its air filter & internal parts.
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | 10 | Monitoring Instruments | Check & clean physical condition.
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 1 | Actuator | Unscrew the actuator from bracket
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 1 | Actuator | Check the actuator kit & adjustable spring.
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 1 | Actuator | Proper lubricant & assembling all parts.
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 2 | Body | Check physical condition. | [5 empty] | Yes
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 2 | Body | Clean body surface for scaling and foreign particles.
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 3 | Seat | Replace if any requirement
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 4 | Plug | Clean body surface for scaling and foreign particles.
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 6 | Positioner/ Solenoid valve | Check Relay ,cam,spring & kit.
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 7 | Electronic Equipment | Verfied Calibration Status.
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 8 | A.F.R | Clean its air filter & internal parts.
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | 10 | Monitoring Instruments | Check & clean physical condition.
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 1 | Actuator | Unscrew the actuator from bracket
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 1 | Actuator | Check the actuator kit & adjustable spring.
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 1 | Actuator | Proper lubricant & assembling all parts.
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 2 | Body | Check physical condition. | [5 empty] | Yes
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 2 | Body | Clean body surface for scaling and foreign particles.
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 3 | Seat | Replace if any requirement
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 4 | Plug | Clean body surface for scaling and foreign particles.
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 6 | Positioner/ Solenoid valve | Check Relay ,cam,spring & kit.
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 7 | Electronic Equipment | Verfied Calibration Status.
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 8 | A.F.R | Clean its air filter & internal parts.
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | 10 | Monitoring Instruments | Check & clean physical condition.
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 1 | Actuator | Unscrew the actuator from bracket
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 1 | Actuator | Check the actuator kit & adjustable spring.
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 1 | Actuator | Proper lubricant & assembling all parts.
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 2 | Body | Check physical condition. | [5 empty] | Yes
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 2 | Body | Clean body surface for scaling and foreign particles.
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 3 | Seat | Replace if any requirement
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 4 | Plug | Clean body surface for scaling and foreign particles.
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 6 | Positioner | Check Relay ,cam,spring & kit.
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 6 | Positioner | Check with loop calibrator.
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 7 | Electronic Equipment | Verfied Calibration Status.
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 8 | A.F.R | Clean its air filter & internal parts.
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | 10 | Monitoring Instruments | Check & clean physical condition.
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 1 | Actuator | Unscrew the actuator from bracket
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 1 | Actuator | Check the actuator kit & adjustable spring.
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 1 | Actuator | Proper lubricant & assembling all parts.
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 2 | Body | Check physical condition. | [5 empty] | Yes
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 2 | Body | Clean body surface for scaling and foreign particles.
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 3 | Seat | Replace if any requirement
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 4 | Plug | Clean body surface for scaling and foreign particles.
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 6 | Positioner | Check Relay ,cam,spring & kit.
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 6 | Positioner | Check with loop calibrator.
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 7 | Electronic Equipment | Verfied Calibration Status.
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 8 | A.F.R | Clean its air filter & internal parts.
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | 10 | Monitoring Instruments | Check & clean physical condition.
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 1 | Actuator | Unscrew the actuator from bracket
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 1 | Actuator | Check the actuator kit & adjustable spring.
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 1 | Actuator | Proper lubricant & assembling all parts.
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 2 | Body | Check physical condition. | [5 empty] | Yes
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 2 | Body | Clean body surface for scaling and foreign particles.
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 3 | Seat | Replace if any requirement
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 4 | Plug | Clean body surface for scaling and foreign particles.
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 6 | Positioner | Check Relay ,cam,spring & kit.
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 6 | Positioner | Check with loop calibrator.
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 7 | Electronic Equipment | Verfied Calibration Status.
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 8 | A.F.R | Clean its air filter & internal parts.
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | 10 | Monitoring Instruments | Check & clean physical condition.
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 1 | Actuator | Unscrew the actuator from bracket
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 1 | Actuator | Check the actuator kit & adjustable spring.
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 1 | Actuator | Proper lubricant & assembling all parts.
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 2 | Body | Check physical condition. | [5 empty] | Yes
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 2 | Body | Clean body surface for scaling and foreign particles.
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 3 | Seat | Replace if any requirement
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 4 | Plug | Check leakage & Scaling condition.
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 4 | Plug | Clean body surface for scaling and foreign particles.
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 6 | Dome Switch/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 6 | Dome Switch/ Solenoid valve | Check with loop calibrator.
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 6 | Dome Switch/ Solenoid valve | Check Solenoid valve seal kit.
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 7 | Electronic Equipment | Verfied Calibration Status.
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 8 | A.F.R | Clean its air filter & internal parts.
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | 10 | Monitoring Instruments | Check & clean physical condition.
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 1 | Actuator | Unscrew the actuator from bracket
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 1 | Actuator | Check the actuator kit & adjustable spring.
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 1 | Actuator | Proper lubricant & assembling all parts.
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 2 | Body | Check physical condition. | [5 empty] | Yes
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 2 | Body | Clean body surface for scaling and foreign particles.
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 3 | Seat | Replace if any requirement
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 4 | Plug | Check leakage & Scaling condition.
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 4 | Plug | Clean body surface for scaling and foreign particles.
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 6 | Dome Switch/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 6 | Dome Switch/ Solenoid valve | Check with loop calibrator.
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 6 | Dome Switch/ Solenoid valve | Check Solenoid valve seal kit.
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 7 | Electronic Equipment | Verfied Calibration Status.
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 8 | A.F.R | Clean its air filter & internal parts.
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 9 | Calibration | Calibration done after install at position (0-100%). | [5 empty] | Yes
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | 10 | Monitoring Instruments | Check & clean physical condition.
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 1 | Actuator | Unscrew the actuator from bracket
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 1 | Actuator | Check the actuator kit & adjustable spring.
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 1 | Actuator | Proper lubricant & assembling all parts.
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 2 | Body | Check physical condition. | [5 empty] | Yes
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 2 | Body | Clean body surface for scaling and foreign particles.
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 3 | Seat | Replace if any requirement
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 4 | Plug | Check leakage & Scaling condition.
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 4 | Plug | Clean body surface for scaling and foreign particles.
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 6 | Dome Switch/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 6 | Dome Switch/ Solenoid valve | Check with loop calibrator.
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 6 | Dome Switch/ Solenoid valve | Check Solenoid valve seal kit.
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 7 | Electronic Equipment | Verfied Calibration Status.
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 8 | A.F.R | Clean its air filter & internal parts.
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | 10 | Monitoring Instruments | Check & clean physical condition.
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 1 | Actuator | Unscrew the actuator from bracket
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 1 | Actuator | Check the actuator kit & adjustable spring.
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 1 | Actuator | Proper lubricant & assembling all parts.
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 2 | Body | Check physical condition. | [5 empty] | Yes
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 2 | Body | Clean body surface for scaling and foreign particles.
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 3 | Seat | Replace if any requirement
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 4 | Plug | Check leakage & Scaling condition.
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 4 | Plug | Clean body surface for scaling and foreign particles.
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 6 | Dome Switch/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 6 | Dome Switch/ Solenoid valve | Check with loop calibrator.
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 6 | Dome Switch/ Solenoid valve | Check Solenoid valve seal kit.
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 7 | Electronic Equipment | Verfied Calibration Status.
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 8 | A.F.R | Clean its air filter & internal parts.
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | 10 | Monitoring Instruments | Check & clean physical condition.
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 1 | Actuator | Unscrew the actuator from bracket
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 1 | Actuator | Check the actuator kit & adjustable spring.
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 1 | Actuator | Proper lubricant & assembling all parts.
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 2 | Body | Check physical condition. | [5 empty] | Yes
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 2 | Body | Clean body surface for scaling and foreign particles.
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 3 | Seat | Replace if any requirement
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 4 | Plug | Check leakage & Scaling condition.
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 4 | Plug | Clean body surface for scaling and foreign particles.
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 6 | Dome Switch/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 6 | Dome Switch/ Solenoid valve | Check with loop calibrator.
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 6 | Dome Switch/ Solenoid valve | Check Solenoid valve seal kit.
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 7 | Electronic Equipment | Verfied Calibration Status.
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 8 | A.F.R | Clean its air filter & internal parts.
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | 10 | Monitoring Instruments | Check & clean physical condition.
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 1 | Actuator | Unscrew the actuator from bracket
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 1 | Actuator | Check the actuator kit & adjustable spring.
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 1 | Actuator | Proper lubricant & assembling all parts.
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 2 | Body | Check physical condition. | [5 empty] | Yes
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 2 | Body | Clean body surface for scaling and foreign particles.
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 3 | Seat | Replace if any requirement
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 4 | Plug | Check leakage & Scaling condition.
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 4 | Plug | Clean body surface for scaling and foreign particles.
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 6 | Dome Switch/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 6 | Dome Switch/ Solenoid valve | Check with loop calibrator.
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 6 | Dome Switch/ Solenoid valve | Check Solenoid valve seal kit.
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 7 | Electronic Equipment | Verfied Calibration Status.
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 8 | A.F.R | Clean its air filter & internal parts.
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | 10 | Monitoring Instruments | Check & clean physical condition.
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 1 | Actuator | Unscrew the actuator from bracket
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 1 | Actuator | Check the actuator kit & adjustable spring.
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 1 | Actuator | Proper lubricant & assembling all parts.
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 2 | Body | Check physical condition. | [5 empty] | Yes
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 2 | Body | Clean body surface for scaling and foreign particles.
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 3 | Seat | Replace if any requirement
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 4 | Plug | Check leakage & Scaling condition.
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 4 | Plug | Clean body surface for scaling and foreign particles.
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 6 | Dome Switch/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 6 | Dome Switch/ Solenoid valve | Check with loop calibrator.
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 6 | Dome Switch/ Solenoid valve | Check Solenoid valve seal kit.
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 7 | Electronic Equipment | Verfied Calibration Status.
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 8 | A.F.R | Clean its air filter & internal parts.
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | 10 | Monitoring Instruments | Check & clean physical condition.
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 1 | Actuator | Unscrew the actuator from bracket
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 1 | Actuator | Check the actuator kit & adjustable spring.
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 1 | Actuator | Proper lubricant & assembling all parts.
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 2 | Body | Check physical condition. | [5 empty] | Yes
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 2 | Body | Clean body surface for scaling and foreign particles.
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 3 | Seat | Replace if any requirement
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 4 | Plug | Check leakage & Scaling condition.
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 4 | Plug | Clean body surface for scaling and foreign particles.
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 6 | Dome Switch/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 6 | Dome Switch/ Solenoid valve | Check with loop calibrator.
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 6 | Dome Switch/ Solenoid valve | Check Solenoid valve seal kit.
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 7 | Electronic Equipment | Verfied Calibration Status.
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 8 | A.F.R | Clean its air filter & internal parts.
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
13658c4b2ce8 | Weingh-54-65 :: ZIL/SUG./001/DECANTER-1/CV1 | ZIL/SUG./001/DECANTER-1/CV1 | 10 | Monitoring Instruments | Check & clean physical condition.
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 1 | Actuator | Unscrew the actuator from bracket
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 1 | Actuator | Check the actuator kit & adjustable spring.
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 1 | Actuator | Proper lubricant & assembling all parts.
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 2 | Body | Check physical condition. | [5 empty] | Yes
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 2 | Body | Clean body surface for scaling and foreign particles.
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 3 | Seat | Replace if any requirement
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 4 | Plug | Check leakage & Scaling condition.
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 4 | Plug | Clean body surface for scaling and foreign particles.
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 6 | Dome Switch/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 6 | Dome Switch/ Solenoid valve | Check with loop calibrator.
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 6 | Dome Switch/ Solenoid valve | Check Solenoid valve seal kit.
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 7 | Electronic Equipment | Verfied Calibration Status.
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 8 | A.F.R | Clean its air filter & internal parts.
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
1131a0579f8e | Weingh-54-65 :: ZIL/SUG./Decanter-1/CV-2 | ZIL/SUG./Decanter-1/CV-2 | 10 | Monitoring Instruments | Check & clean physical condition.
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 1 | Actuator | Unscrew the actuator from bracket
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 1 | Actuator | Check the actuator kit & adjustable spring.
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 1 | Actuator | Proper lubricant & assembling all parts.
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 2 | Body | Check physical condition. | [5 empty] | Yes
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 2 | Body | Clean body surface for scaling and foreign particles.
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 3 | Seat | Replace if any requirement
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 4 | Plug | Check leakage & Scaling condition.
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 4 | Plug | Clean body surface for scaling and foreign particles.
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 6 | Dome Switch/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 6 | Dome Switch/ Solenoid valve | Check with loop calibrator.
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 6 | Dome Switch/ Solenoid valve | Check Solenoid valve seal kit.
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 7 | Electronic Equipment | Verfied Calibration Status.
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 8 | A.F.R | Clean its air filter & internal parts.
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e004a93ec595 | Weingh-54-65 :: ZIL/SUG./DECANTER-2/CV-2 | ZIL/SUG./DECANTER-2/CV-2 | 10 | Monitoring Instruments | Check & clean physical condition.
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 1 | Actuator | Unscrew the actuator from bracket
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 1 | Actuator | Check the actuator kit & adjustable spring.
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 1 | Actuator | Proper lubricant & assembling all parts.
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 2 | Body | Check physical condition. | [5 empty] | Yes
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 2 | Body | Clean body surface for scaling and foreign particles.
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 3 | Seat | Replace if any requirement
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 4 | Plug | Check leakage & Scaling condition.
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 4 | Plug | Clean body surface for scaling and foreign particles.
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 6 | Dome Switch/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 6 | Dome Switch/ Solenoid valve | Check with loop calibrator.
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 6 | Dome Switch/ Solenoid valve | Check Solenoid valve seal kit.
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 7 | Electronic Equipment | Verfied Calibration Status.
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 8 | A.F.R | Clean its air filter & internal parts.
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
452cb739b3ba | Weingh-54-65 :: ZIL/SUG./DECANTER-CV3 | ZIL/SUG./DECANTER-CV3 | 10 | Monitoring Instruments | Check & clean physical condition.
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 1 | Actuator | Unscrew the actuator from bracket
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 1 | Actuator | Check the actuator kit & adjustable spring.
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 1 | Actuator | Proper lubricant & assembling all parts.
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 2 | Body | Check physical condition. | [5 empty] | Yes
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 2 | Body | Clean body surface for scaling and foreign particles.
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 3 | Seat | Replace if any requirement
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 4 | Plug | Clean body surface for scaling and foreign particles.
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 5 | Solenoid valve | Check all internal part, seal kit clean it. | [5 empty] | Yes
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 5 | Solenoid valve | Check with SOV spring & plunjer
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 5 | Solenoid valve | Check Solenoid valve.
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 6 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 6 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 6 | Electronic Equipment | Verfied Calibration Status.
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 7 | A.F.R | Clean its air filter & internal parts.
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | 9 | Monitoring Instruments | Check & clean physical condition.
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 1 | Actuator | Unscrew the actuator from bracket
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 1 | Actuator | Check the actuator kit & adjustable spring.
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 1 | Actuator | Proper lubricant & assembling all parts.
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 2 | Body | Check physical condition. | [5 empty] | Yes
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 2 | Body | Clean body surface for scaling and foreign particles.
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 3 | Seat | Replace if any requirement
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 4 | Plug | Clean body surface for scaling and foreign particles.
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 5 | Solenoid valve | Check all internal part, seal kit clean it. | [5 empty] | Yes
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 5 | Solenoid valve | Check with SOV spring & plunjer
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 5 | Solenoid valve | Check Solenoid valve.
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 6 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 6 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 6 | Electronic Equipment | Verfied Calibration Status.
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 7 | A.F.R | Clean its air filter & internal parts.
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | 9 | Monitoring Instruments | Check & clean physical condition.
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 1 | Actuator | Unscrew the actuator from bracket
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 1 | Actuator | Check the actuator kit & adjustable spring.
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 1 | Actuator | Proper lubricant & assembling all parts.
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 2 | Body | Check physical condition. | [5 empty] | Yes
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 2 | Body | Clean body surface for scaling and foreign particles.
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 3 | Seat | Replace if any requirement
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 4 | Plug | Clean body surface for scaling and foreign particles.
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 5 | Solenoid valve | Check all internal part, seal kit clean it. | [5 empty] | Yes
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 5 | Solenoid valve | Check with SOV spring & plunjer
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 5 | Solenoid valve | Check Solenoid valve.
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 6 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 6 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 6 | Electronic Equipment | Verfied Calibration Status.
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 7 | A.F.R | Clean its air filter & internal parts.
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | 9 | Monitoring Instruments | Check & clean physical condition.
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 1 | Actuator | Unscrew the actuator from bracket
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 1 | Actuator | Check the actuator kit & adjustable spring.
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 1 | Actuator | Proper lubricant & assembling all parts.
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 2 | Body | Check physical condition. | [5 empty] | Yes
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 2 | Body | Clean body surface for scaling and foreign particles.
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 3 | Seat | Replace if any requirement
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 4 | Plug | Clean body surface for scaling and foreign particles.
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 5 | Solenoid valve | Check all internal part, seal kit clean it. | [5 empty] | Yes
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 5 | Solenoid valve | Check with SOV spring & plunjer
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 5 | Solenoid valve | Check Solenoid valve.
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 6 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 6 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 6 | Electronic Equipment | Verfied Calibration Status.
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 7 | A.F.R | Clean its air filter & internal parts.
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | 9 | Monitoring Instruments | Check & clean physical condition.
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 1 | Actuator | Unscrew the actuator from bracket
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 1 | Actuator | Check the actuator kit & adjustable spring.
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 1 | Actuator | Proper lubricant & assembling all parts.
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 2 | Body | Check physical condition. | [5 empty] | Yes
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 2 | Body | Clean body surface for scaling and foreign particles.
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 3 | Seat | Replace if any requirement
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 4 | Plug | Clean body surface for scaling and foreign particles.
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 5 | Solenoid valve | Check all internal part, seal kit clean it. | [5 empty] | Yes
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 5 | Solenoid valve | Check with SOV spring & plunjer
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 5 | Solenoid valve | Check Solenoid valve.
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 6 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 6 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 6 | Electronic Equipment | Verfied Calibration Status.
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 7 | A.F.R | Clean its air filter & internal parts.
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | 9 | Monitoring Instruments | Check & clean physical condition.
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 1 | Actuator | Unscrew the actuator from bracket
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 1 | Actuator | Check the actuator kit & adjustable spring.
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 1 | Actuator | Proper lubricant & assembling all parts.
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 2 | Body | Check physical condition. | [5 empty] | Yes
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 2 | Body | Clean body surface for scaling and foreign particles.
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 3 | Seat | Replace if any requirement
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 4 | Plug | Clean body surface for scaling and foreign particles.
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 5 | Solenoid valve | Check all internal part, seal kit clean it. | [5 empty] | Yes
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 5 | Solenoid valve | Check with SOV spring & plunjer
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 5 | Solenoid valve | Check Solenoid valve.
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 6 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 6 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 6 | Electronic Equipment | Verfied Calibration Status.
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 7 | A.F.R | Clean its air filter & internal parts.
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | 9 | Monitoring Instruments | Check & clean physical condition.
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 1 | Actuator | Unscrew the actuator from bracket
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 1 | Actuator | Check the actuator kit & adjustable spring.
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 1 | Actuator | Proper lubricant & assembling all parts.
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 2 | Body | Check physical condition. | [5 empty] | Yes
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 2 | Body | Clean body surface for scaling and foreign particles.
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 3 | Seat | Replace if any requirement
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 4 | Plug | Clean body surface for scaling and foreign particles.
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 7 | Electronic Equipment | Verfied Calibration Status.
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 8 | A.F.R | Clean its air filter & internal parts.
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | 10 | Monitoring Instruments | Check & clean physical condition.
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 1 | Actuator | Unscrew the actuator from bracket
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 1 | Actuator | Check the actuator kit & adjustable spring.
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 1 | Actuator | Proper lubricant & assembling all parts.
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 2 | Body | Check physical condition. | [5 empty] | Yes
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 2 | Body | Clean body surface for scaling and foreign particles.
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 3 | Seat | Replace if any requirement
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 4 | Plug | Clean body surface for scaling and foreign particles.
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 5 | Solenoid valve | Check all internal part, seal kit clean it. | [5 empty] | Yes
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 5 | Solenoid valve | Check with SOV spring & plunjer
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 5 | Solenoid valve | Check Solenoid valve.
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 6 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 6 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 6 | Electronic Equipment | Verfied Calibration Status.
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 7 | A.F.R | Clean its air filter & internal parts.
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | 9 | Monitoring Instruments | Check & clean physical condition.
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 1 | Actuator | Unscrew the actuator from bracket
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 1 | Actuator | Check the actuator kit & adjustable spring.
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 1 | Actuator | Proper lubricant & assembling all parts.
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 2 | Body | Check physical condition. | [5 empty] | Yes
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 2 | Body | Clean body surface for scaling and foreign particles.
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 3 | Seat | Replace if any requirement
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 4 | Plug | Clean body surface for scaling and foreign particles.
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 7 | Electronic Equipment | Verfied Calibration Status.
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 8 | A.F.R | Clean its air filter & internal parts.
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | 10 | Monitoring Instruments | Check & clean physical condition.
da94085bd25e | Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | ZIL/SUG./SULPHER/PANEL | 1 | Transmitter Body | Check physical condition. | [5 empty] | Yes
da94085bd25e | Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | ZIL/SUG./SULPHER/PANEL | 1 | Transmitter Body | Clean body surface for scaling and foreign particles.
da94085bd25e | Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | ZIL/SUG./SULPHER/PANEL | 2 | RTD | Check damage rtd wire | [5 empty] | Yes
da94085bd25e | Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | ZIL/SUG./SULPHER/PANEL | 2 | RTD | Check resistance power
da94085bd25e | Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | ZIL/SUG./SULPHER/PANEL | 3 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
da94085bd25e | Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | ZIL/SUG./SULPHER/PANEL | 3 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
da94085bd25e | Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | ZIL/SUG./SULPHER/PANEL | 3 | Electronic equipment | Veryfied calibration status.
da94085bd25e | Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | ZIL/SUG./SULPHER/PANEL | 4 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
da94085bd25e | Transient Heater 66-73 :: ZIL/SUG./SULPHER/PANEL | ZIL/SUG./SULPHER/PANEL | 4 | Monitoring Instruments | Check & clean physical condition.
c2b506d4463f | Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | ZIL/SUG./FILM/PANEL | 1 | Transmitter Body | Check physical condition. | [5 empty] | Yes
c2b506d4463f | Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | ZIL/SUG./FILM/PANEL | 1 | Transmitter Body | Clean body surface for scaling and foreign particles.
c2b506d4463f | Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | ZIL/SUG./FILM/PANEL | 2 | RTD | Check damage rtd wire | [5 empty] | Yes
c2b506d4463f | Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | ZIL/SUG./FILM/PANEL | 2 | RTD | Check resistance power
c2b506d4463f | Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | ZIL/SUG./FILM/PANEL | 3 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
c2b506d4463f | Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | ZIL/SUG./FILM/PANEL | 3 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
c2b506d4463f | Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | ZIL/SUG./FILM/PANEL | 3 | Electronic equipment | Veryfied calibration status.
c2b506d4463f | Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | ZIL/SUG./FILM/PANEL | 4 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c2b506d4463f | Transient Heater 66-73 :: ZIL/SUG./FILM/PANEL | ZIL/SUG./FILM/PANEL | 4 | Monitoring Instruments | Check & clean physical condition.
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | 1 | Controller | Check physical condition. | [5 empty] | Yes
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | 1 | Controller | Clean internal & Extranal Part warm-up
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | 2 | Calibration | Calibration done after install at position. | [5 empty] | Yes
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | 3 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | 3 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | 3 | Electronic equipment | Veryfied calibration status.
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | 4 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e731b480d0d2 | Transient Heater 66-73 :: ZIL/SUG./001/DS-CFM- 01 | ZIL/SUG./001/DS-CFM- 01 | 4 | Monitoring Instruments | Check & clean physical condition.
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | 1 | Sensor | Check its continuity end the conector.
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | 2 | Power supply Card | check Its eatrhing voltage.
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | 3 | Microprocessor Unit | Check its output signal
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | 5 | Liner | Check its scaling. | [5 empty] | Yes
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | 5 | Liner | Check its any deformation parts.
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | 7 | Monitoring Instruments | Check & clean physical condition.
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | 1 | Sensor | Check its continuity end the conector.
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | 2 | Power supply Card | check Its eatrhing voltage.
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | 3 | Microprocessor Unit | Check its output signal
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | 5 | Liner | Check its scaling. | [5 empty] | Yes
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | 5 | Liner | Check its any deformation parts.
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | 7 | Monitoring Instruments | Check & clean physical condition.
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | 1 | Sensor | Check its continuity end the conector.
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | 2 | Power supply Card | check Its eatrhing voltage.
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | 3 | Microprocessor Unit | Check its output signal
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | 5 | Liner | Check its scaling. | [5 empty] | Yes
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | 5 | Liner | Check its any deformation parts.
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | 7 | Monitoring Instruments | Check & clean physical condition.
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | 1 | Sensor | Check its continuity end the conector.
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | 2 | Power supply Card | check Its eatrhing voltage.
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | 3 | Microprocessor Unit | Check its output signal
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | 5 | Liner | Check its scaling. | [5 empty] | Yes
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | 5 | Liner | Check its any deformation parts.
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | 7 | Monitoring Instruments | Check & clean physical condition.
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | 1 | Sensor | Check its continuity end the conector.
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | 2 | Power supply Card | check Its eatrhing voltage.
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | 3 | Microprocessor Unit | Check its output signal
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | 5 | Liner | Check its scaling. | [5 empty] | Yes
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | 5 | Liner | Check its any deformation parts.
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | 7 | Monitoring Instruments | Check & clean physical condition.
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | 1 | Sensor | Check its continuity end the conector.
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | 2 | Power supply Card | check Its eatrhing voltage.
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | 3 | Microprocessor Unit | Check its output signal
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | 5 | Liner | Check its scaling. | [5 empty] | Yes
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | 5 | Liner | Check its any deformation parts.
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | 7 | Monitoring Instruments | Check & clean physical condition.
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | 1 | Sensor | Check its continuity end the conector.
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | 2 | Power supply Card | check Its eatrhing voltage.
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | 3 | Microprocessor Unit | Check its output signal
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | 5 | Liner | Check its scaling. | [5 empty] | Yes
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | 5 | Liner | Check its any deformation parts.
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | 7 | Monitoring Instruments | Check & clean physical condition.
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | 1 | Sensor | Check its continuity end the conector.
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | 2 | Power supply Card | check Its eatrhing voltage.
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | 3 | Microprocessor Unit | Check its output signal
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | 5 | Liner | Check its any deformation parts.
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | 7 | Monitoring Instruments | Check & clean physical condition.
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | 1 | Sensor | Check its continuity end the conector.
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | 2 | Power supply Card | check Its eatrhing voltage.
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | 3 | Microprocessor Unit | Check its output signal
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | 5 | Liner | Check its any deformation parts.
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | 7 | Monitoring Instruments | Check & clean physical condition.
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | 1 | Sensor | Check its continuity end the conector.
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | 2 | Power supply Card | check Its eatrhing voltage.
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | 3 | Microprocessor Unit | Check its output signal
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | 5 | Liner | Check its scaling. | [5 empty] | Yes
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | 5 | Liner | Check its any deformation parts.
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | 7 | Monitoring Instruments | Check & clean physical condition.
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 1 | Sensor | Check its continuity end the conector.
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 2 | Power supply Card | check Its eatrhing voltage.
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 3 | Microprocessor Unit | Check its output signal
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 5 | Liner | Check its any deformation parts.
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | 7 | Monitoring Instruments | Check & clean physical condition.
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | 1 | Sensor | Check its continuity end the conector.
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | 2 | Power supply Card | check Its eatrhing voltage.
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | 3 | Microprocessor Unit | Check its output signal
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | 5 | Liner | Check its scaling. | [5 empty] | Yes
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | 5 | Liner | Check its any deformation parts.
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | 7 | Monitoring Instruments | Check & clean physical condition.
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | 1 | Sensor | Check its continuity end the conector.
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | 2 | Power supply Card | check Its eatrhing voltage.
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | 3 | Microprocessor Unit | Check its output signal
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | 4 | Display | Check Its number & Characters. |  | Yes |  |  |  | Yes
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | 5 | Liner | Check its any deformation parts.
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | 7 | Monitoring Instruments | Check & clean physical condition.
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | 1 | Sensor | Check its continuity end the conector.
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | 2 | Power supply Card | check Its eatrhing voltage.
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | 3 | Microprocessor Unit | Check its output signal
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | 5 | Liner | Check its any deformation parts.
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | 7 | Monitoring Instruments | Check & clean physical condition.
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | 1 | Sensor | Check its continuity end the conector.
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | 2 | Power supply Card | check Its eatrhing voltage.
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | 3 | Microprocessor Unit | Check its output signal
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | 4 | Display | Check Its number & Characters. |  | Yes |  |  |  | Yes
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | 5 | Liner | Check its any deformation parts.
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | 7 | Monitoring Instruments | Check & clean physical condition.
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | 1 | Sensor | Check its continuity end the conector.
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | 2 | Power supply Card | check Its eatrhing voltage.
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | 3 | Microprocessor Unit | Check its output signal
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | 4 | Display | Check Its number & Characters. |  | Yes |  |  |  | Yes
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | 5 | Liner | Check its any deformation parts.
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | 7 | Monitoring Instruments | Check & clean physical condition.
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | 1 | Sensor | Check its continuity end the conector.
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | 2 | Power supply Card | check Its eatrhing voltage.
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | 3 | Microprocessor Unit | Check its output signal
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | 5 | Liner | Check its any deformation parts.
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | 7 | Monitoring Instruments | Check & clean physical condition.
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | 1 | Sensor | Check its continuity end the conector.
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | 2 | Power supply Card | check Its eatrhing voltage.
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | 3 | Microprocessor Unit | Check its output signal
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | 4 | Display | Check Its number & Characters. |  | Yes
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | 5 | Liner | Check its scaling. | [5 empty] | Yes
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | 5 | Liner | Check its any deformation parts.
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | 7 | Monitoring Instruments | Check & clean physical condition.
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | 1 | Sensor | Check its continuity end the conector.
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | 2 | Power supply Card | check Its eatrhing voltage.
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | 3 | Microprocessor Unit | Check its output signal
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | 5 | Liner | Check its scaling. | [5 empty] | Yes
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | 5 | Liner | Check its any deformation parts.
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | 7 | Monitoring Instruments | Check & clean physical condition.
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | 1 | Sensor | Check its continuity end the conector.
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | 2 | Power supply Card | check Its eatrhing voltage.
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | 3 | Microprocessor Unit | Check its output signal
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | 5 | Liner | Check its scaling. | [5 empty] | Yes
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | 5 | Liner | Check its any deformation parts.
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | 7 | Monitoring Instruments | Check & clean physical condition.
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | 1 | Sensor | Check its continuity end the conector.
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | 2 | Power supply Card | check Its eatrhing voltage.
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | 3 | Microprocessor Unit | Check its output signal
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | 5 | Liner | Check its scaling. | [5 empty] | Yes
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | 5 | Liner | Check its any deformation parts.
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | 7 | Monitoring Instruments | Check & clean physical condition.
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | 1 | Sensor | Check its continuity end the conector.
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | 2 | Power supply Card | check Its eatrhing voltage.
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | 3 | Microprocessor Unit | Check its output signal
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | 5 | Liner | Check its any deformation parts.
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | 7 | Monitoring Instruments | Check & clean physical condition.
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | 1 | Sensor | Check its continuity end the conector.
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | 2 | Power supply Card | check Its eatrhing voltage.
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | 3 | Microprocessor Unit | Check its output signal
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | 5 | Liner | Check its scaling. | [5 empty] | Yes
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | 5 | Liner | Check its any deformation parts.
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | 7 | Monitoring Instruments | Check & clean physical condition.
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | 1 | Sensor | Check its continuity end the conector.
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | 2 | Power supply Card | check Its eatrhing voltage.
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | 3 | Microprocessor Unit | Check its output signal
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | 5 | Liner | Check its any deformation parts.
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | 7 | Monitoring Instruments | Check & clean physical condition.
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | 1 | Sensor | Check its continuity end the conector.
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | 2 | Power supply Card | check Its eatrhing voltage.
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | 3 | Microprocessor Unit | Check its output signal
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | 5 | Liner | Check its any deformation parts.
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | 7 | Monitoring Instruments | Check & clean physical condition.
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | 1 | Sensor | Check its continuity end the conector.
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | 2 | Power supply Card | check Its eatrhing voltage.
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | 3 | Microprocessor Unit | Check its output signal
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | 5 | Liner | Check its scaling. | [5 empty] | Yes
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | 5 | Liner | Check its any deformation parts.
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | 7 | Monitoring Instruments | Check & clean physical condition.
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 1 | Pressure Tx-02 | Check physical impulse line condition.
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 2 | Oil Pump | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 2 | Oil Pump | Check physical condition.
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 3 | Relay | Check working & physical Condition.
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 4 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 4 | Solenoid valve | Check Solenoid valve seal kit.
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 4 | Solenoid valve | Check Solenoid valve with water
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 5 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 5 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 5 | Electronic Equipment | Verfied Calibration Status.
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 6 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | 7 | Monitoring Instruments | Check & clean physical condition.
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 1 | Pressure Tx-02 | Check physical impulse line condition.
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 2 | Temp. Tx- 02 | Check & calibration
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 3 | Body | Check physical condition.
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 4 | Nozzle | Check physical condition.
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 5 | N.R.V | Replace if any requirement
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 6 | Relay | Check working & physical Condition.
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 7 | Solenoid valve | Check Solenoid valve seal kit.
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 7 | Solenoid valve | Check Solenoid valve with water
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 8 | Electronic Equipment | Verfied Calibration Status.
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 9 | Hose Pipe | Check leakage, cut and damage sign.
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | 11 | Monitoring Instruments | Check & clean physical condition.
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 1 | Pressure Tx-02 | Check physical impulse line condition.
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 2 | Temp. Tx- 02 | Check & calibration
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 3 | Body | Check physical condition.
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 4 | Nozzle | Check physical condition.
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 5 | N.R.V | Replace if any requirement
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 6 | Relay | Check working & physical Condition.
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 7 | Solenoid valve | Check Solenoid valve seal kit.
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 7 | Solenoid valve | Check Solenoid valve with water
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 8 | Electronic Equipment | Verfied Calibration Status.
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 9 | Hose Pipe | Check leakage, cut and damage sign.
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | 11 | Monitoring Instruments | Check & clean physical condition.
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 1 | Pressure Tx-02 | Check physical impulse line condition.
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 2 | Temp. Tx- 02 | Check & calibration
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 3 | Body | Check physical condition.
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 4 | Nozzle | Check physical condition.
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 5 | N.R.V | Replace if any requirement
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 6 | Relay | Check working & physical Condition.
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 7 | Solenoid valve | Check Solenoid valve seal kit.
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 7 | Solenoid valve | Check Solenoid valve with water
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 8 | Electronic Equipment | Verfied Calibration Status.
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 9 | Hose Pipe | Check leakage, cut and damage sign.
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | 11 | Monitoring Instruments | Check & clean physical condition.
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 1 | Pressure Tx-02 | Check physical impulse line condition.
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 2 | Temp. Tx- 02 | Check & calibration
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 3 | Body | Check physical condition.
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 4 | Nozzle | Check physical condition.
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 5 | N.R.V | Replace if any requirement
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 6 | Relay | Check working & physical Condition.
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 7 | Solenoid valve | Check Solenoid valve seal kit.
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 7 | Solenoid valve | Check Solenoid valve with water
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 8 | Electronic Equipment | Verfied Calibration Status.
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 9 | Hose Pipe | Check leakage, cut and damage sign.
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | 11 | Monitoring Instruments | Check & clean physical condition.
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 1 | Pressure Tx-02 | Check physical impulse line condition.
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 2 | Temp. Tx- 02 | Check & calibration
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 3 | Body | Check physical condition.
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 4 | Nozzle | Check physical condition.
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 5 | N.R.V | Replace if any requirement
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 6 | Relay | Check working & physical Condition.
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 7 | Solenoid valve | Check Solenoid valve seal kit.
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 7 | Solenoid valve | Check Solenoid valve with water
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 8 | Electronic Equipment | Verfied Calibration Status.
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 9 | Hose Pipe | Check leakage, cut and damage sign.
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | 11 | Monitoring Instruments | Check & clean physical condition.
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 1 | Pressure Tx-02 | Check physical impulse line condition.
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 2 | Temp. Tx- 02 | Check physical impulse line condition.
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 3 | Body | Check physical condition.
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 4 | Nozzle | Check physical condition.
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 5 | N.R.V | Replace if any requirement
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 6 | Relay | Check working & physical Condition.
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 7 | Solenoid valve | Check Solenoid valve seal kit.
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 7 | Solenoid valve | Check Solenoid valve with water
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 8 | Electronic Equipment | Verfied Calibration Status.
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 9 | Hose Pipe | Check leakage, cut and damage sign.
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | 11 | Monitoring Instruments | Check & clean physical condition.
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 1 | Pressure Tx-02 | Check physical impulse line condition.
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 2 | Temp. Tx- 02 | Check physical impulse line condition.
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 3 | Body | Check physical condition.
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 4 | Nozzle | Check physical condition.
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 5 | N.R.V | Replace if any requirement
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 6 | Relay | Check working & physical Condition.
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 7 | Solenoid valve | Check Solenoid valve seal kit.
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 7 | Solenoid valve | Check Solenoid valve with water
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 8 | Electronic Equipment | Verfied Calibration Status.
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 9 | Hose Pipe | Check leakage, cut and damage sign.
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | 11 | Monitoring Instruments | Check & clean physical condition.
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 1 | Pressure Tx-02 | Check physical impulse line condition.
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 2 | Temp. Tx- 02 | Check physical impulse line condition.
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 3 | Body | Check physical condition.
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 4 | Nozzle | Check physical condition.
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 5 | N.R.V | Replace if any requirement
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 6 | Relay | Check working & physical Condition.
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 7 | Solenoid valve | Check Solenoid valve seal kit.
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 7 | Solenoid valve | Check Solenoid valve with water
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 8 | Electronic Equipment | Verfied Calibration Status.
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 9 | Hose Pipe | Check leakage, cut and damage sign.
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | 11 | Monitoring Instruments | Check & clean physical condition.
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 1 | Pressure Tx-02 | Check physical impulse line condition.
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 2 | Temp. Tx- 02 | Check physical impulse line condition.
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 3 | Body | Check physical condition.
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 4 | Nozzle | Check physical condition.
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 5 | N.R.V | Replace if any requirement
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 6 | Relay | Check working & physical Condition.
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 7 | Solenoid valve | Check Solenoid valve seal kit.
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 7 | Solenoid valve | Check Solenoid valve with water
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 8 | Electronic Equipment | Verfied Calibration Status.
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 9 | Hose Pipe | Check leakage, cut and damage sign.
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | 11 | Monitoring Instruments | Check & clean physical condition.
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 1 | Pressure Tx-02 | Check physical impulse line condition.
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 2 | Temp. Tx- 02 | Check physical impulse line condition.
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 3 | Body | Check physical condition.
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 4 | Nozzle | Check physical condition.
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 5 | N.R.V | Replace if any requirement
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 6 | Relay | Check working & physical Condition.
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 7 | Solenoid valve | Check Solenoid valve seal kit.
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 7 | Solenoid valve | Check Solenoid valve with water
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 8 | Electronic Equipment | Verfied Calibration Status.
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 9 | Hose Pipe | Check leakage, cut and damage sign.
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | 11 | Monitoring Instruments | Check & clean physical condition.
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 1 | Pressure Tx-02 | Check physical impulse line condition.
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 2 | Temp. Tx- 02 | Check physical impulse line condition.
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 3 | Body | Check physical condition.
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 4 | Nozzle | Check physical condition.
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 5 | N.R.V | Replace if any requirement
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 6 | Relay | Check working & physical Condition.
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 7 | Solenoid valve | Check Solenoid valve seal kit.
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 7 | Solenoid valve | Check Solenoid valve with water
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 8 | Electronic Equipment | Verfied Calibration Status.
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 9 | Hose Pipe | Check leakage, cut and damage sign.
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | 11 | Monitoring Instruments | Check & clean physical condition.
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 1 | Pressure Tx-02 | Check physical impulse line condition.
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 2 | Temp. Tx- 02 | Check physical impulse line condition.
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 3 | Body | Check physical condition.
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 4 | Nozzle | Check physical condition.
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 5 | N.R.V | Replace if any requirement
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 6 | Relay | Check working & physical Condition.
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 7 | Solenoid valve | Check Solenoid valve seal kit.
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 7 | Solenoid valve | Check Solenoid valve with water
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 8 | Electronic Equipment | Verfied Calibration Status.
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 9 | Hose Pipe | Check leakage, cut and damage sign.
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | 11 | Monitoring Instruments | Check & clean physical condition.
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 1 | Pressure Tx-02 | Check physical impulse line condition.
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 2 | Temp. Tx- 02 | Check physical impulse line condition.
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 3 | Body | Check physical condition.
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 4 | Nozzle | Check physical condition.
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 5 | N.R.V | Replace if any requirement
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 6 | Relay | Check working & physical Condition.
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 7 | Solenoid valve | Check Solenoid valve seal kit.
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 7 | Solenoid valve | Check Solenoid valve with water
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 8 | Electronic Equipment | Verfied Calibration Status.
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 9 | Hose Pipe | Check leakage, cut and damage sign.
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | 11 | Monitoring Instruments | Check & clean physical condition.
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 1 | Pressure Tx-02 | Check physical condition & wire | [5 empty] | Yes
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 1 | Pressure Tx-02 | Check physical impulse line condition.
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 2 | Temp. Tx- 02 | Check physical condition & wire terminals. | [5 empty] | Yes
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 2 | Temp. Tx- 02 | Check physical impulse line condition.
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 3 | Body | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 3 | Body | Check physical condition.
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 4 | Nozzle | Clean body surface for scaling and foreign particles. | [5 empty] | Yes
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 4 | Nozzle | Check physical condition.
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 5 | N.R.V | Check leakage, cut and damage sign. | [5 empty] | Yes
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 5 | N.R.V | Replace if any requirement
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 6 | Relay | Check working & physical Condition.
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 7 | Solenoid valve | Check all internal part, spring & clean it. | [5 empty] | Yes
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 7 | Solenoid valve | Check Solenoid valve seal kit.
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 7 | Solenoid valve | Check Solenoid valve with water
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 8 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 8 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 8 | Electronic Equipment | Verfied Calibration Status.
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 9 | Hose Pipe | Check physical condition. | [5 empty] | Yes
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 9 | Hose Pipe | Check leakage, cut and damage sign.
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 10 | Checking & Testing | Checking & Testing done after install at position. | [5 empty] | Yes
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | 11 | Monitoring Instruments | Check & clean physical condition.
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 1 | Cylinder | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 1 | Cylinder | Unscrew the cylinder from sutter ,bagcamp & bucket
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 1 | Cylinder | Check the cylinder kit & air flow valve
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 1 | Cylinder | Proper lubricant & assembling all parts.
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 1 | Cylinder | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 1 | Cylinder | Unscrew the cylinder from sutter ,bagcamp & bucket
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 1 | Cylinder | Check the cylinder kit & air flow valve
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 1 | Cylinder | Proper lubricant & assembling all parts.
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 2 | Bearing | Check physical condition. | [5 empty] | Yes
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 2 | Bearing | Clean body surface for scaling and foreign particles.
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 3 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 3 | Solenoide Valve | Replace if any requirement
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 4 | Suttar Assembly | Check Bearing condition.
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 4 | Suttar Assembly | Clean body surface for scaling and foreign particles.
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 5 | A.F.R | Check filter lement ,spring ,kit proper cleaning. | [5 empty] | Yes
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 6 | Loadcell | Check resitance | [5 empty] | Yes
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 6 | Loadcell | Check output supply.
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 6 | Loadcell | Check ground with supply.
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 7 | Electronic Equipment | Verfied Calibration Status.
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 8 | Calibration | Zero calibration
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 8 | Calibration | Calibration done after install at position. (0-100%)
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | 9 | Monitoring Instruments | Check & clean physical condition.
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 1 | Cylinder | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 1 | Cylinder | Unscrew the cylinder from sutter ,bagcamp & bucket
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 1 | Cylinder | Check the cylinder kit & air flow valve
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 1 | Cylinder | Proper lubricant & assembling all parts.
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 2 | Bearing | Check physical condition. | [5 empty] | Yes
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 2 | Bearing | Clean body surface for scaling and foreign particles.
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 3 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 3 | Solenoide Valve | Replace if any requirement
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 4 | Suttar Assembly | Check Bearing condition.
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 4 | Suttar Assembly | Clean body surface for scaling and foreign particles.
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 5 | A.F.R | Check filter lement ,spring ,kit proper cleaning. | [5 empty] | Yes
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 6 | Loadcell | Check resitance
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 6 | Loadcell | Check output supply.
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 6 | Loadcell | Check ground with supply.
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 7 | Electronic Equipment | Verfied Calibration Status.
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 8 | Calibration | Zero calibration | [5 empty] | Yes
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 8 | Calibration | Calibration done after install at position. (0-100%)
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | 9 | Monitoring Instruments | Check & clean physical condition.
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 1 | Cylinder | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 1 | Cylinder | Unscrew the cylinder from sutter ,bagcamp & bucket
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 1 | Cylinder | Check the cylinder kit & air flow valve
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 1 | Cylinder | Proper lubricant & assembling all parts.
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 2 | Bearing | Check physical condition. | [5 empty] | Yes
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 2 | Bearing | Clean body surface for scaling and foreign particles.
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 3 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 3 | Solenoide Valve | Replace if any requirement
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 4 | Suttar Assembly | Check Bearing condition.
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 4 | Suttar Assembly | Clean body surface for scaling and foreign particles.
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 5 | A.F.R | Check filter lement ,spring ,kit proper cleaning. | [5 empty] | Yes
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 6 | Loadcell | Check resitance | [5 empty] | Yes
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 6 | Loadcell | Check output supply.
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 6 | Loadcell | Check ground with supply.
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 7 | Electronic Equipment | Verfied Calibration Status.
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 8 | Calibration | Zero calibration | [5 empty] | Yes
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 8 | Calibration | Calibration done after install at position. (0-100%)
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | 9 | Monitoring Instruments | Check & clean physical condition.
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 1 | Cylinder | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 1 | Cylinder | Unscrew the cylinder from sutter ,bagcamp & bucket
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 1 | Cylinder | Check the cylinder kit & air flow valve
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 1 | Cylinder | Proper lubricant & assembling all parts.
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 2 | Bearing | Check physical condition. | [5 empty] | Yes
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 2 | Bearing | Clean body surface for scaling and foreign particles.
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 3 | Solenoide Valve | Check Solenoid valve seal kit. | [5 empty] | Yes
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 3 | Solenoide Valve | Replace if any requirement
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 4 | Suttar Assembly | Check Bearing condition. | [5 empty] | Yes
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 4 | Suttar Assembly | Clean body surface for scaling and foreign particles.
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 5 | A.F.R | Check filter lement ,spring ,kit proper cleaning. | [5 empty] | Yes
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 6 | Loadcell | Check resitance | [5 empty] | Yes
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 6 | Loadcell | Check output supply.
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 6 | Loadcell | Check ground with supply.
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 7 | Electronic Equipment | Verfied Calibration Status.
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 8 | Calibration | Zero calibration | [5 empty] | Yes
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 8 | Calibration | Calibration done after install at position. (0-100%)
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | 9 | Monitoring Instruments | Check & clean physical condition.
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 1 | Actuator | Unscrew the actuator from bracket
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 1 | Actuator | Check the actuator kit & adjustable spring.
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 1 | Actuator | Proper lubricant & assembling all parts.
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 2 | Body | Check physical condition. | [5 empty] | Yes
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 2 | Body | Clean body surface for scaling and foreign particles.
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 3 | Seat | Replace if any requirement
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 4 | Plug | Check leakage & Scaling condition.
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 4 | Plug | Clean body surface for scaling and foreign particles.
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 7 | A.F.R | Clean its air filter & internal parts.
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 8 | Electroinc equipment | Check equipment condition & clean. | [5 empty] | Yes
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 8 | Electroinc equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 8 | Electroinc equipment | Veryfied calibration status.
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | 10 | Monitoring Instruments | Check & clean physical condition.
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 1 | Actuator | Unscrew the actuator from bracket
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 1 | Actuator | Check the actuator kit & adjustable spring.
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 1 | Actuator | Proper lubricant & assembling all parts.
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 2 | Body | Check physical condition. | [5 empty] | Yes
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 2 | Body | Clean body surface for scaling and foreign particles.
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 3 | Seat | Replace if any requirement
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 4 | Plug | Check leakage & Scaling condition.
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 4 | Plug | Clean body surface for scaling and foreign particles.
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 7 | A.F.R | Clean its air filter & internal parts.
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 8 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | 9 | Monitoring Instruments | Check & clean physical condition.
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 1 | Actuator | Unscrew the actuator from bracket
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 1 | Actuator | Check the actuator kit & adjustable spring.
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 1 | Actuator | Proper lubricant & assembling all parts.
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 2 | Body | Check physical condition. | [5 empty] | Yes
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 2 | Body | Clean body surface for scaling and foreign particles.
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 3 | Seat | Replace if any requirement
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 4 | Plug | Check leakage & Scaling condition.
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 4 | Plug | Clean body surface for scaling and foreign particles.
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 7 | A.F.R | Clean its air filter & internal parts.
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 8 | Calibration | Calibration done after install at position. (0-100%)
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | 9 | Monitoring Instruments | Check & clean physical condition.
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 1 | Actuator | Unscrew the actuator from bracket
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 1 | Actuator | Check the actuator kit & adjustable spring.
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 1 | Actuator | Proper lubricant & assembling all parts.
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 2 | Body | Check physical condition. | [5 empty] | Yes
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 2 | Body | Clean body surface for scaling and foreign particles.
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 3 | Seat | Replace if any requirement
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 4 | Plug | Check leakage & Scaling condition.
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 4 | Plug | Clean body surface for scaling and foreign particles.
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 7 | A.F.R | Clean its air filter & internal parts.
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 8 | Calibration | Calibration done after install at position. (0-100%)
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | 9 | Monitoring Instruments | Check & clean physical condition.
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 1 | Actuator | Unscrew the actuator from bracket
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 1 | Actuator | Check the actuator kit & adjustable spring.
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 1 | Actuator | Proper lubricant & assembling all parts.
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 2 | Body | Check physical condition. | [5 empty] | Yes
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 2 | Body | Clean body surface for scaling and foreign particles.
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 3 | Seat | Replace if any requirement
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 4 | Plug | Check leakage & Scaling condition.
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 4 | Plug | Clean body surface for scaling and foreign particles.
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 7 | A.F.R | Clean its air filter & internal parts.
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 8 | Calibration | Calibration done after install at position. (0-100%)
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | 9 | Monitoring Instruments | Check & clean physical condition.
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 1 | Actuator | Unscrew the actuator from bracket
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 1 | Actuator | Check the actuator kit & adjustable spring.
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 1 | Actuator | Proper lubricant & assembling all parts.
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 2 | Body | Check physical condition. | [5 empty] | Yes
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 2 | Body | Clean body surface for scaling and foreign particles.
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 3 | Seat | Replace if any requirement
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 4 | Plug | Check leakage & Scaling condition.
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 4 | Plug | Clean body surface for scaling and foreign particles.
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 7 | A.F.R | Clean its air filter & internal parts.
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 8 | Calibration | Calibration done after install at position. (0-100%)
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | 9 | Monitoring Instruments | Check & clean physical condition.
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 1 | Actuator | Unscrew the actuator from bracket
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 1 | Actuator | Check the actuator kit & adjustable spring.
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 1 | Actuator | Proper lubricant & assembling all parts.
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 2 | Body | Check physical condition. | [5 empty] | Yes
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 2 | Body | Clean body surface for scaling and foreign particles.
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 3 | Seat | Replace if any requirement
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 4 | Plug | Check leakage & Scaling condition.
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 4 | Plug | Clean body surface for scaling and foreign particles.
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 7 | A.F.R | Clean its air filter & internal parts.
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 8 | Calibration | Calibration done after install at position. (0-100%)
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | 9 | Monitoring Instruments | Check & clean physical condition.
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 1 | Actuator | Unscrew the actuator from bracket
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 1 | Actuator | Proper lubricant & assembling all parts.
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 2 | Body | Clean body surface for scaling and foreign particles.
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 3 | Seat | Replace if any requirement
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 4 | Plug | Check leakage & Scaling condition.
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 7 | A.F.R | Clean its air filter & internal parts.
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | 9 | Monitoring Instruments | Check & clean physical condition.
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 1 | Actuator | Unscrew the actuator from bracket
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 1 | Actuator | Check the actuator kit & adjustable spring.
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 1 | Actuator | Proper lubricant & assembling all parts.
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 2 | Body | Check physical condition. | [5 empty] | Yes
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 2 | Body | Clean body surface for scaling and foreign particles.
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 3 | Seat | Replace if any requirement
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 4 | Plug | Check leakage & Scaling condition.
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 4 | Plug | Clean body surface for scaling and foreign particles.
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 7 | A.F.R | Clean its air filter & internal parts.
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 8 | Calibration | Calibration done after install at position. (0-100%)
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | 9 | Monitoring Instruments | Check & clean physical condition.
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 1 | Actuator | Unscrew the actuator from bracket
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 1 | Actuator | Check the actuator kit & adjustable spring.
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 1 | Actuator | Proper lubricant & assembling all parts.
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 2 | Body | Check physical condition. | [5 empty] | Yes
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 2 | Body | Clean body surface for scaling and foreign particles.
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 3 | Seat | Replace if any requirement
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 4 | Plug | Check leakage & Scaling condition.
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 4 | Plug | Clean body surface for scaling and foreign particles.
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 7 | A.F.R | Clean its air filter & internal parts.
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 8 | Calibration | Calibration done after install at position. (0-100%)
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | 9 | Monitoring Instruments | Check & clean physical condition.
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 1 | Actuator | Unscrew the actuator from bracket
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 1 | Actuator | Check the actuator kit & adjustable spring.
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 1 | Actuator | Proper lubricant & assembling all parts.
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 2 | Body | Check physical condition. | [5 empty] | Yes
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 2 | Body | Clean body surface for scaling and foreign particles.
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 3 | Seat | Replace if any requirement
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 4 | Plug | Check leakage & Scaling condition.
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 4 | Plug | Clean body surface for scaling and foreign particles.
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 7 | A.F.R | Clean its air filter & internal parts.
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 8 | Calibration | Calibration done after install at position. (0-100%)
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | 9 | Monitoring Instruments | Check & clean physical condition.
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 1 | Actuator | Unscrew the actuator from bracket
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 1 | Actuator | Check the actuator kit & adjustable spring.
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 1 | Actuator | Proper lubricant & assembling all parts.
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 2 | Body | Check physical condition. | [5 empty] | Yes
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 2 | Body | Clean body surface for scaling and foreign particles.
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 3 | Seat | Replace if any requirement
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 4 | Plug | Check leakage & Scaling condition.
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 4 | Plug | Clean body surface for scaling and foreign particles.
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 7 | A.F.R | Clean its air filter & internal parts.
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 8 | Calibration | Calibration done after install at position. (0-100%)
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | 9 | Monitoring Instruments | Check & clean physical condition.
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 1 | Actuator | Unscrew the actuator from bracket
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 1 | Actuator | Check the actuator kit & adjustable spring.
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 1 | Actuator | Proper lubricant & assembling all parts.
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 2 | Body | Check physical condition. | [5 empty] | Yes
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 2 | Body | Clean body surface for scaling and foreign particles.
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 3 | Seat | Replace if any requirement
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 4 | Plug | Check leakage & Scaling condition.
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 4 | Plug | Clean body surface for scaling and foreign particles.
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 7 | A.F.R | Clean its air filter & internal parts.
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 8 | Electroinc equipment | Check equipment condition & clean. | [5 empty] | Yes
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 8 | Electroinc equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 8 | Electroinc equipment | Veryfied calibration status.
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 9 | Calibration | Calibration done after install at position. (0-100%)
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | 10 | Monitoring Instruments | Check & clean physical condition.
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 1 | Actuator | Unscrew the actuator from bracket
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 1 | Actuator | Check the actuator kit & adjustable spring.
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 1 | Actuator | Proper lubricant & assembling all parts.
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 2 | Body | Check physical condition. | [5 empty] | Yes
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 2 | Body | Clean body surface for scaling and foreign particles.
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 3 | Seat | Replace if any requirement
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 4 | Plug | Check leakage & Scaling condition.
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 4 | Plug | Clean body surface for scaling and foreign particles.
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 7 | A.F.R | Clean its air filter & internal parts.
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 8 | Calibration | Calibration done after install at position. (0-100%)
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | 9 | Monitoring Instruments | Check & clean physical condition.
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 1 | Actuator | Unscrew the actuator from bracket
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 1 | Actuator | Check the actuator kit & adjustable spring.
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 1 | Actuator | Proper lubricant & assembling all parts.
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 2 | Body | Check physical condition. | [5 empty] | Yes
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 2 | Body | Clean body surface for scaling and foreign particles.
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 3 | Seat | Replace if any requirement
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 4 | Plug | Check leakage & Scaling condition.
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 4 | Plug | Clean body surface for scaling and foreign particles.
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 7 | A.F.R | Clean its air filter & internal parts.
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 8 | Calibration | Calibration done after install at position. (0-100%)
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | 9 | Monitoring Instruments | Check & clean physical condition.
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 1 | Actuator | Unscrew the actuator from bracket
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 1 | Actuator | Check the actuator kit & adjustable spring.
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 1 | Actuator | Proper lubricant & assembling all parts.
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 2 | Body | Check physical condition. | [5 empty] | Yes
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 2 | Body | Clean body surface for scaling and foreign particles.
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 3 | Seat | Replace if any requirement
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 4 | Plug | Check leakage & Scaling condition.
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 4 | Plug | Clean body surface for scaling and foreign particles.
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 7 | A.F.R | Clean its air filter & internal parts.
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 8 | Calibration | Calibration done after install at position. (0-100%)
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | 9 | Monitoring Instruments | Check & clean physical condition.
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 1 | Actuator | Unscrew the actuator from bracket
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 1 | Actuator | Check the actuator kit & adjustable spring.
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 1 | Actuator | Proper lubricant & assembling all parts.
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 2 | Body | Check physical condition. | [5 empty] | Yes
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 2 | Body | Clean body surface for scaling and foreign particles.
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 3 | Seat | Replace if any requirement
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 4 | Plug | Check leakage & Scaling condition.
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 4 | Plug | Clean body surface for scaling and foreign particles.
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 7 | A.F.R | Clean its air filter & internal parts.
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 8 | Calibration | Calibration done after install at position. (0-100%)
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | 9 | Monitoring Instruments | Check & clean physical condition.
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 1 | Actuator | Unscrew the actuator from bracket
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 1 | Actuator | Check the actuator kit & adjustable spring.
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 1 | Actuator | Proper lubricant & assembling all parts.
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 2 | Body | Check physical condition. | [5 empty] | Yes
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 2 | Body | Clean body surface for scaling and foreign particles.
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 3 | Seat | Replace if any requirement
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 4 | Plug | Check leakage & Scaling condition.
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 4 | Plug | Clean body surface for scaling and foreign particles.
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 7 | A.F.R | Clean its air filter & internal parts.
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 8 | Calibration | Calibration done after install at position. (0-100%)
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | 9 | Monitoring Instruments | Check & clean physical condition.
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 1 | Actuator | Unscrew the actuator from bracket
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 1 | Actuator | Check the actuator kit & adjustable spring.
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 1 | Actuator | Proper lubricant & assembling all parts.
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 2 | Body | Check physical condition. | [5 empty] | Yes
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 2 | Body | Clean body surface for scaling and foreign particles.
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 3 | Seat | Replace if any requirement
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 4 | Plug | Check leakage & Scaling condition.
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 4 | Plug | Clean body surface for scaling and foreign particles.
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 7 | A.F.R | Clean its air filter & internal parts.
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 8 | Calibration | Calibration done after install at position. (0-100%)
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | 9 | Monitoring Instruments | Check & clean physical condition.
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 1 | Actuator | Unscrew the actuator from bracket
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 1 | Actuator | Check the actuator kit & adjustable spring.
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 1 | Actuator | Proper lubricant & assembling all parts.
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 2 | Body | Check physical condition. | [5 empty] | Yes
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 2 | Body | Clean body surface for scaling and foreign particles.
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 3 | Seat | Replace if any requirement
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 4 | Plug | Check leakage & Scaling condition.
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 4 | Plug | Clean body surface for scaling and foreign particles.
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 7 | A.F.R | Clean its air filter & internal parts.
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 8 | Calibration | Calibration done after install at position. (0-100%)
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | 9 | Monitoring Instruments | Check & clean physical condition.
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 1 | Actuator | Unscrew the actuator from bracket
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 1 | Actuator | Check the actuator kit & adjustable spring.
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 1 | Actuator | Proper lubricant & assembling all parts.
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 2 | Body | Check physical condition. | [5 empty] | Yes
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 2 | Body | Clean body surface for scaling and foreign particles.
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 3 | Seat | Replace if any requirement
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 4 | Plug | Check leakage & Scaling condition.
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 4 | Plug | Clean body surface for scaling and foreign particles.
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 7 | A.F.R | Clean its air filter & internal parts.
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 8 | Calibration | Calibration done after install at position. (0-100%)
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | 9 | Monitoring Instruments | Check & clean physical condition.
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 1 | Actuator | Unscrew the actuator from bracket
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 1 | Actuator | Check the actuator kit & adjustable spring.
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 1 | Actuator | Proper lubricant & assembling all parts.
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 2 | Body | Check physical condition. | [5 empty] | Yes
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 2 | Body | Clean body surface for scaling and foreign particles.
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 3 | Seat | Replace if any requirement
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 4 | Plug | Check leakage & Scaling condition.
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 4 | Plug | Clean body surface for scaling and foreign particles.
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 7 | A.F.R | Clean its air filter & internal parts.
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 8 | Calibration | Calibration done after install at position. (0-100%)
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | 9 | Monitoring Instruments | Check & clean physical condition.
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 1 | Actuator | Unscrew the actuator from bracket
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 1 | Actuator | Proper lubricant & assembling all parts.
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 2 | Body | Clean body surface for scaling and foreign particles.
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 3 | Seat | Replace if any requirement
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 4 | Plug | Check leakage & Scaling condition.
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 7 | A.F.R | Clean its air filter & internal parts.
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | 9 | Monitoring Instruments | Check & clean physical condition.
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 1 | Actuator | Unscrew the actuator from bracket
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 1 | Actuator | Check the actuator kit & adjustable spring.
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 1 | Actuator | Proper lubricant & assembling all parts.
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 2 | Body | Check physical condition. | [5 empty] | Yes
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 2 | Body | Clean body surface for scaling and foreign particles.
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 3 | Seat | Replace if any requirement
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 4 | Plug | Check leakage & Scaling condition.
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 4 | Plug | Clean body surface for scaling and foreign particles.
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 7 | A.F.R | Clean its air filter & internal parts.
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 8 | Calibration | Calibration done after install at position. (0-100%)
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | 9 | Monitoring Instruments | Check & clean physical condition.
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 1 | Actuator | Unscrew the actuator from bracket
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 1 | Actuator | Check the actuator kit & adjustable spring.
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 1 | Actuator | Proper lubricant & assembling all parts.
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 2 | Body | Check physical condition. | [5 empty] | Yes
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 2 | Body | Clean body surface for scaling and foreign particles.
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 3 | Seat | Replace if any requirement
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 4 | Plug | Check leakage & Scaling condition.
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 4 | Plug | Clean body surface for scaling and foreign particles.
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 7 | A.F.R | Clean its air filter & internal parts.
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 8 | Electroinc equipment | Check equipment condition & clean. | [5 empty] | Yes
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 8 | Electroinc equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 8 | Electroinc equipment | Veryfied calibration status.
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 9 | Calibration | Calibration done after install at position. (0-100%)
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | 10 | Monitoring Instruments | Check & clean physical condition.
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 1 | Actuator | Unscrew the actuator from bracket
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 1 | Actuator | Check the actuator kit & adjustable spring.
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 1 | Actuator | Proper lubricant & assembling all parts.
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 2 | Body | Check physical condition. | [5 empty] | Yes
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 2 | Body | Clean body surface for scaling and foreign particles.
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 3 | Seat | Replace if any requirement
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 4 | Plug | Check leakage & Scaling condition.
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 4 | Plug | Clean body surface for scaling and foreign particles.
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 7 | A.F.R | Clean its air filter & internal parts.
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 8 | Calibration | Calibration done after install at position. (0-100%)
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | 9 | Monitoring Instruments | Check & clean physical condition.
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 1 | Actuator | Unscrew the actuator from bracket
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 1 | Actuator | Check the actuator kit & adjustable spring.
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 1 | Actuator | Proper lubricant & assembling all parts.
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 2 | Body | Check physical condition. | [5 empty] | Yes
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 2 | Body | Clean body surface for scaling and foreign particles.
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 3 | Seat | Replace if any requirement
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 4 | Plug | Check leakage & Scaling condition.
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 4 | Plug | Clean body surface for scaling and foreign particles.
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 7 | A.F.R | Clean its air filter & internal parts.
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 8 | Calibration | Calibration done after install at position. (0-100%)
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | 9 | Monitoring Instruments | Check & clean physical condition.
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 1 | Actuator | Unscrew the actuator from bracket
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 1 | Actuator | Check the actuator kit & adjustable spring.
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 1 | Actuator | Proper lubricant & assembling all parts.
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 2 | Body | Check physical condition. | [5 empty] | Yes
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 2 | Body | Clean body surface for scaling and foreign particles.
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 3 | Seat | Replace if any requirement
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 4 | Plug | Check leakage & Scaling condition.
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 4 | Plug | Clean body surface for scaling and foreign particles.
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 7 | A.F.R | Clean its air filter & internal parts.
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 8 | Calibration | Calibration done after install at position. (0-100%)
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | 9 | Monitoring Instruments | Check & clean physical condition.
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 1 | Actuator | Unscrew the actuator from bracket
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 1 | Actuator | Check the actuator kit & adjustable spring.
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 1 | Actuator | Proper lubricant & assembling all parts.
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 2 | Body | Check physical condition. | [5 empty] | Yes
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 2 | Body | Clean body surface for scaling and foreign particles.
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 3 | Seat | Replace if any requirement
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 4 | Plug | Check leakage & Scaling condition.
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 4 | Plug | Clean body surface for scaling and foreign particles.
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 7 | A.F.R | Clean its air filter & internal parts.
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 8 | Calibration | Calibration done after install at position. (0-100%)
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | 9 | Monitoring Instruments | Check & clean physical condition.
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 1 | Actuator | Unscrew the actuator from bracket
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 1 | Actuator | Check the actuator kit & adjustable spring.
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 1 | Actuator | Proper lubricant & assembling all parts.
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 2 | Body | Check physical condition. | [5 empty] | Yes
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 2 | Body | Clean body surface for scaling and foreign particles.
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 3 | Seat | Replace if any requirement
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 4 | Plug | Check leakage & Scaling condition.
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 4 | Plug | Clean body surface for scaling and foreign particles.
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 7 | A.F.R | Clean its air filter & internal parts.
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 8 | Calibration | Calibration done after install at position. (0-100%)
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | 9 | Monitoring Instruments | Check & clean physical condition.
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 1 | Actuator | Unscrew the actuator from bracket
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 1 | Actuator | Check the actuator kit & adjustable spring.
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 1 | Actuator | Proper lubricant & assembling all parts.
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 2 | Body | Check physical condition. | [5 empty] | Yes
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 2 | Body | Clean body surface for scaling and foreign particles.
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 3 | Seat | Replace if any requirement
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 4 | Plug | Check leakage & Scaling condition.
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 4 | Plug | Clean body surface for scaling and foreign particles.
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 7 | A.F.R | Clean its air filter & internal parts.
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 8 | Calibration | Calibration done after install at position. (0-100%)
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | 9 | Monitoring Instruments | Check & clean physical condition.
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 1 | Actuator | Unscrew the actuator from bracket
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 1 | Actuator | Check the actuator kit & adjustable spring.
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 1 | Actuator | Proper lubricant & assembling all parts.
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 2 | Body | Check physical condition. | [5 empty] | Yes
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 2 | Body | Clean body surface for scaling and foreign particles.
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 3 | Seat | Replace if any requirement
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 4 | Plug | Check leakage & Scaling condition.
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 4 | Plug | Clean body surface for scaling and foreign particles.
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 7 | A.F.R | Clean its air filter & internal parts.
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 8 | Calibration | Calibration done after install at position. (0-100%)
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | 9 | Monitoring Instruments | Check & clean physical condition.
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 1 | Actuator | Unscrew the actuator from bracket
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 1 | Actuator | Check the actuator kit & adjustable spring.
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 1 | Actuator | Proper lubricant & assembling all parts.
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 2 | Body | Check physical condition. | [5 empty] | Yes
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 2 | Body | Clean body surface for scaling and foreign particles.
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 3 | Seat | Replace if any requirement
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 4 | Plug | Check leakage & Scaling condition.
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 4 | Plug | Clean body surface for scaling and foreign particles.
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 7 | A.F.R | Clean its air filter & internal parts.
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 8 | Calibration | Calibration done after install at position. (0-100%)
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | 9 | Monitoring Instruments | Check & clean physical condition.
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 1 | Actuator | Unscrew the actuator from bracket
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 1 | Actuator | Check the actuator kit & adjustable spring.
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 1 | Actuator | Proper lubricant & assembling all parts.
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 2 | Body | Check physical condition. | [5 empty] | Yes
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 2 | Body | Clean body surface for scaling and foreign particles.
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 3 | Seat | Replace if any requirement
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 4 | Plug | Check leakage & Scaling condition.
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 4 | Plug | Clean body surface for scaling and foreign particles.
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 7 | A.F.R | Clean its air filter & internal parts.
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 8 | Calibration | Calibration done after install at position. (0-100%)
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | 9 | Monitoring Instruments | Check & clean physical condition.
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 1 | Actuator | Unscrew the actuator from bracket
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 1 | Actuator | Check the actuator kit & adjustable spring.
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 1 | Actuator | Proper lubricant & assembling all parts.
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 2 | Body | Check physical condition. | [5 empty] | Yes
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 2 | Body | Clean body surface for scaling and foreign particles.
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 3 | Seat | Replace if any requirement
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 4 | Plug | Check leakage & Scaling condition.
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 4 | Plug | Clean body surface for scaling and foreign particles.
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 7 | A.F.R | Clean its air filter & internal parts.
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 8 | Calibration | Calibration done after install at position. (0-100%)
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | 9 | Monitoring Instruments | Check & clean physical condition.
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 1 | Actuator | Unscrew the actuator from bracket
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 1 | Actuator | Check the actuator kit & adjustable spring.
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 1 | Actuator | Proper lubricant & assembling all parts.
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 2 | Body | Check physical condition. | [5 empty] | Yes
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 2 | Body | Clean body surface for scaling and foreign particles.
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 3 | Seat | Replace if any requirement
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 4 | Plug | Check leakage & Scaling condition.
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 4 | Plug | Clean body surface for scaling and foreign particles.
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 7 | A.F.R | Clean its air filter & internal parts.
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 8 | Calibration | Calibration done after install at position. (0-100%)
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | 9 | Monitoring Instruments | Check & clean physical condition.
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 1 | Actuator | Unscrew the actuator from bracket
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 1 | Actuator | Check the actuator kit & adjustable spring.
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 1 | Actuator | Proper lubricant & assembling all parts.
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 2 | Body | Check physical condition. | [5 empty] | Yes
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 2 | Body | Clean body surface for scaling and foreign particles.
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 3 | Seat | Replace if any requirement
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 4 | Plug | Check leakage & Scaling condition.
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 4 | Plug | Clean body surface for scaling and foreign particles.
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 7 | A.F.R | Clean its air filter & internal parts.
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 8 | Electroinc equipment | Check equipment condition & clean. | [5 empty] | Yes
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 8 | Electroinc equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 8 | Electroinc equipment | Veryfied calibration status.
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | 10 | Monitoring Instruments | Check & clean physical condition.
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 1 | Actuator | Unscrew the actuator from bracket
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 1 | Actuator | Check the actuator kit & adjustable spring.
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 1 | Actuator | Proper lubricant & assembling all parts.
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 2 | Body | Check physical condition. | [5 empty] | Yes
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 2 | Body | Clean body surface for scaling and foreign particles.
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 3 | Seat | Replace if any requirement
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 4 | Plug | Check leakage & Scaling condition.
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 4 | Plug | Clean body surface for scaling and foreign particles.
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 7 | A.F.R | Clean its air filter & internal parts.
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 8 | Electronic equipment | Veryfied calibration status.
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 9 | Calibration | Calibration done after install at position. (0-100%)
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | 10 | Monitoring Instruments | Check & clean physical condition.
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 1 | Actuator | Unscrew the actuator from bracket
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 1 | Actuator | Check the actuator kit & adjustable spring.
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 1 | Actuator | Proper lubricant & assembling all parts.
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 2 | Body | Check physical condition. | [5 empty] | Yes
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 2 | Body | Clean body surface for scaling and foreign particles.
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 3 | Seat | Replace if any requirement
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 4 | Plug | Check leakage & Scaling condition.
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 4 | Plug | Clean body surface for scaling and foreign particles.
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 7 | A.F.R | Clean its air filter & internal parts.
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 8 | Electronic equipment | Veryfied calibration status.
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 9 | Calibration | Calibration done after install at position. (0-100%)
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | 10 | Monitoring Instruments | Check & clean physical condition.
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 1 | Actuator | Unscrew the actuator from bracket
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 1 | Actuator | Proper lubricant & assembling all parts.
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 2 | Body | Clean body surface for scaling and foreign particles.
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 3 | Seat | Replace if any requirement
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 4 | Plug | Check leakage & Scaling condition.
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 7 | A.F.R | Clean its air filter & internal parts.
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 8 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 8 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 8 | Electronic equipment | Veryfied calibration status.
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 9 | Calibration | Calibration done after install at position. (0-100%)
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | 10 | Monitoring Instruments | Check & clean physical condition.
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 1 | Actuator | Unscrew the actuator from bracket
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 1 | Actuator | Proper lubricant & assembling all parts.
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 2 | Body | Clean body surface for scaling and foreign particles.
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 3 | Seat | Replace if any requirement
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 7 | A.F.R | Clean its air filter & internal parts.
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 8 | Electroinc equipment | Check equipment condition & clean. | [5 empty] | Yes
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 8 | Electroinc equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 8 | Electroinc equipment | Veryfied calibration status.
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | 10 | Monitoring Instruments | Check & clean physical condition.
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 1 | Actuator | Unscrew the actuator from bracket
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 1 | Actuator | Check the actuator kit & adjustable spring.
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 1 | Actuator | Proper lubricant & assembling all parts.
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 2 | Body | Check physical condition. | [5 empty] | Yes
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 2 | Body | Clean body surface for scaling and foreign particles.
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 3 | Seat | Replace if any requirement
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 4 | Plug | Check leakage & Scaling condition.
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 4 | Plug | Clean body surface for scaling and foreign particles.
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 7 | A.F.R | Clean its air filter & internal parts.
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 8 | Calibration | Calibration done after install at position. (0-100%)
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | 9 | Monitoring Instruments | Check & clean physical condition.
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 1 | Actuator | Unscrew the actuator from bracket
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 1 | Actuator | Proper lubricant & assembling all parts.
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 2 | Body | Clean body surface for scaling and foreign particles.
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 3 | Seat | Replace if any requirement
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 4 | Plug | Check leakage & Scaling condition.
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 7 | A.F.R | Clean its air filter & internal parts.
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | 9 | Monitoring Instruments | Check & clean physical condition.
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 1 | Actuator | Unscrew the actuator from bracket
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 1 | Actuator | Proper lubricant & assembling all parts.
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 2 | Body | Clean body surface for scaling and foreign particles.
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 3 | Seat | Replace if any requirement
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 4 | Plug | Check leakage & Scaling condition.
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 7 | A.F.R | Clean its air filter & internal parts.
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | 9 | Monitoring Instruments | Check & clean physical condition.
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 1 | Actuator | Unscrew the actuator from bracket
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 1 | Actuator | Proper lubricant & assembling all parts.
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 2 | Body | Clean body surface for scaling and foreign particles.
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 3 | Seat | Replace if any requirement
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 4 | Plug | Check leakage & Scaling condition.
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 7 | A.F.R | Clean its air filter & internal parts.
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | 9 | Monitoring Instruments | Check & clean physical condition.
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 1 | Actuator | Unscrew the actuator from bracket
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 1 | Actuator | Check the actuator kit & adjustable spring.
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 1 | Actuator | Proper lubricant & assembling all parts.
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 2 | Body | Check physical condition. | [5 empty] | Yes
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 2 | Body | Clean body surface for scaling and foreign particles.
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 3 | Seat | Replace if any requirement
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 4 | Plug | Check leakage & Scaling condition.
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 4 | Plug | Clean body surface for scaling and foreign particles.
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 7 | A.F.R | Clean its air filter & internal parts.
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 8 | Calibration | Calibration done after install at position. (0-100%)
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | 9 | Monitoring Instruments | Check & clean physical condition.
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 1 | Actuator | Unscrew the actuator from bracket
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 1 | Actuator | Check the actuator kit & adjustable spring.
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 1 | Actuator | Proper lubricant & assembling all parts.
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 2 | Body | Check physical condition. | [5 empty] | Yes
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 2 | Body | Clean body surface for scaling and foreign particles.
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 3 | Seat | Replace if any requirement
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 4 | Plug | Check leakage & Scaling condition.
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 4 | Plug | Clean body surface for scaling and foreign particles.
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 7 | A.F.R | Clean its air filter & internal parts.
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 8 | Calibration | Calibration done after install at position. (0-100%)
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | 9 | Monitoring Instruments | Check & clean physical condition.
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 1 | Actuator | Unscrew the actuator from bracket
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 1 | Actuator | Check the actuator kit & adjustable spring.
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 1 | Actuator | Proper lubricant & assembling all parts.
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 2 | Body | Check physical condition. | [5 empty] | Yes
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 2 | Body | Clean body surface for scaling and foreign particles.
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 3 | Seat | Replace if any requirement
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 4 | Plug | Check leakage & Scaling condition.
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 4 | Plug | Clean body surface for scaling and foreign particles.
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 7 | A.F.R | Clean its air filter & internal parts.
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 8 | Calibration | Calibration done after install at position. (0-100%)
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | 9 | Monitoring Instruments | Check & clean physical condition.
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 1 | Actuator | Unscrew the actuator from bracket
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 1 | Actuator | Check the actuator kit & adjustable spring.
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 1 | Actuator | Proper lubricant & assembling all parts.
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 2 | Body | Check physical condition. | [5 empty] | Yes
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 2 | Body | Clean body surface for scaling and foreign particles.
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 3 | Seat | Replace if any requirement
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 4 | Plug | Check leakage & Scaling condition.
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 4 | Plug | Clean body surface for scaling and foreign particles.
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 7 | A.F.R | Clean its air filter & internal parts.
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 8 | Calibration | Calibration done after install at position. (0-100%)
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | 9 | Monitoring Instruments | Check & clean physical condition.
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 1 | Actuator | Unscrew the actuator from bracket
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 1 | Actuator | Check the actuator kit & adjustable spring.
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 1 | Actuator | Proper lubricant & assembling all parts.
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 2 | Body | Check physical condition. | [5 empty] | Yes
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 2 | Body | Clean body surface for scaling and foreign particles.
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 3 | Seat | Replace if any requirement
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 4 | Plug | Check leakage & Scaling condition.
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 4 | Plug | Clean body surface for scaling and foreign particles.
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 7 | A.F.R | Clean its air filter & internal parts.
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 8 | Calibration | Calibration done after install at position. (0-100%)
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | 9 | Monitoring Instruments | Check & clean physical condition.
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 1 | Actuator | Unscrew the actuator from bracket
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 1 | Actuator | Check the actuator kit & adjustable spring.
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 1 | Actuator | Proper lubricant & assembling all parts.
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 2 | Body | Check physical condition. | [5 empty] | Yes
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 2 | Body | Clean body surface for scaling and foreign particles.
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 3 | Seat | Replace if any requirement
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 4 | Plug | Check leakage & Scaling condition.
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 4 | Plug | Clean body surface for scaling and foreign particles.
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 7 | A.F.R | Clean its air filter & internal parts.
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 8 | Calibration | Calibration done after install at position. (0-100%)
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | 9 | Monitoring Instruments | Check & clean physical condition.
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 1 | Actuator | Unscrew the actuator from bracket
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 1 | Actuator | Proper lubricant & assembling all parts.
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 2 | Body | Clean body surface for scaling and foreign particles.
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 3 | Seat | Replace if any requirement
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 4 | Plug | Check leakage & Scaling condition.
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 7 | A.F.R | Clean its air filter & internal parts.
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | 9 | Monitoring Instruments | Check & clean physical condition.
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 1 | Actuator | Unscrew the actuator from bracket
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 1 | Actuator | Check the actuator kit & adjustable spring.
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 1 | Actuator | Proper lubricant & assembling all parts.
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 2 | Body | Check physical condition. | [5 empty] | Yes
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 2 | Body | Clean body surface for scaling and foreign particles.
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 3 | Seat | Replace if any requirement
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 4 | Plug | Check leakage & Scaling condition.
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 4 | Plug | Clean body surface for scaling and foreign particles.
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 7 | A.F.R | Clean its air filter & internal parts.
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 8 | Calibration | Calibration done after install at position. (0-100%)
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | 9 | Monitoring Instruments | Check & clean physical condition.
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 1 | Actuator | Unscrew the actuator from bracket
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 1 | Actuator | Check the actuator kit & adjustable spring.
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 1 | Actuator | Proper lubricant & assembling all parts.
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 2 | Body | Check physical condition. | [5 empty] | Yes
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 2 | Body | Clean body surface for scaling and foreign particles.
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 3 | Seat | Replace if any requirement
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 4 | Plug | Check leakage & Scaling condition.
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 4 | Plug | Clean body surface for scaling and foreign particles.
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 7 | A.F.R | Clean its air filter & internal parts.
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 8 | Calibration | Calibration done after install at position. (0-100%)
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | 9 | Monitoring Instruments | Check & clean physical condition.
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 1 | Actuator | Unscrew the actuator from bracket
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 1 | Actuator | Proper lubricant & assembling all parts.
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 2 | Body | Clean body surface for scaling and foreign particles.
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 3 | Seat | Replace if any requirement
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 4 | Plug | Check leakage & Scaling condition.
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 7 | A.F.R | Clean its air filter & internal parts.
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | 9 | Monitoring Instruments | Check & clean physical condition.
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 1 | Actuator | Unscrew the actuator from bracket
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 1 | Actuator | Proper lubricant & assembling all parts.
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 2 | Body | Clean body surface for scaling and foreign particles.
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 3 | Seat | Replace if any requirement
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 4 | Plug | Check leakage & Scaling condition.
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 7 | A.F.R | Clean its air filter & internal parts.
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | 9 | Monitoring Instruments | Check & clean physical condition.
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 1 | Actuator | Unscrew the actuator from bracket
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 1 | Actuator | Proper lubricant & assembling all parts.
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 2 | Body | Clean body surface for scaling and foreign particles.
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 3 | Seat | Replace if any requirement
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 4 | Plug | Check leakage & Scaling condition.
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 7 | A.F.R | Clean its air filter & internal parts.
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | 9 | Monitoring Instruments | Check & clean physical condition.
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 1 | Actuator | Unscrew the actuator from bracket
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 1 | Actuator | Check the actuator kit & adjustable spring.
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 1 | Actuator | Proper lubricant & assembling all parts.
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 2 | Body | Check physical condition. | [5 empty] | Yes
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 2 | Body | Clean body surface for scaling and foreign particles.
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 3 | Seat | Replace if any requirement
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 4 | Plug | Check leakage & Scaling condition.
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 4 | Plug | Clean body surface for scaling and foreign particles.
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 7 | A.F.R | Clean its air filter & internal parts.
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 8 | Calibration | Calibration done after install at position. (0-100%)
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | 9 | Monitoring Instruments | Check & clean physical condition.
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 1 | Actuator | Unscrew the actuator from bracket
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 1 | Actuator | Proper lubricant & assembling all parts.
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 2 | Body | Clean body surface for scaling and foreign particles.
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 3 | Seat | Replace if any requirement
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 4 | Plug | Check leakage & Scaling condition.
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 7 | A.F.R | Clean its air filter & internal parts.
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 8 | Calibration | Calibration done after install at position. (0-100%)
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | 9 | Monitoring Instruments | Check & clean physical condition.
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 1 | Actuator | Unscrew the actuator from bracket
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 1 | Actuator | Check the actuator kit & adjustable spring.
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 1 | Actuator | Proper lubricant & assembling all parts.
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 2 | Body | Check physical condition. | [5 empty] | Yes
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 2 | Body | Clean body surface for scaling and foreign particles.
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 3 | Seat | Replace if any requirement
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 4 | Plug | Check leakage & Scaling condition.
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 4 | Plug | Clean body surface for scaling and foreign particles.
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 7 | A.F.R | Clean its air filter & internal parts.
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 8 | Calibration | Calibration done after install at position. (0-100%)
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | 9 | Monitoring Instruments | Check & clean physical condition.
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 1 | Actuator | Unscrew the actuator from bracket
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 1 | Actuator | Check the actuator kit & adjustable spring.
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 1 | Actuator | Proper lubricant & assembling all parts.
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 2 | Body | Check physical condition. | [5 empty] | Yes
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 2 | Body | Clean body surface for scaling and foreign particles.
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 3 | Seat | Replace if any requirement
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 4 | Plug | Check leakage & Scaling condition.
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 4 | Plug | Clean body surface for scaling and foreign particles.
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 7 | A.F.R | Clean its air filter & internal parts.
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 8 | Calibration | Calibration done after install at position. (0-100%)
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | 9 | Monitoring Instruments | Check & clean physical condition.
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 1 | Actuator | Unscrew the actuator from bracket
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 1 | Actuator | Proper lubricant & assembling all parts.
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 2 | Body | Clean body surface for scaling and foreign particles.
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 3 | Seat | Replace if any requirement
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 4 | Plug | Check leakage & Scaling condition.
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 7 | A.F.R | Clean its air filter & internal parts.
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | 9 | Monitoring Instruments | Check & clean physical condition.
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 1 | Actuator | Unscrew the actuator from bracket
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 1 | Actuator | Check the actuator kit & adjustable spring.
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 1 | Actuator | Proper lubricant & assembling all parts.
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 2 | Body | Check physical condition. | [5 empty] | Yes
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 2 | Body | Clean body surface for scaling and foreign particles.
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 3 | Seat | Replace if any requirement
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 4 | Plug | Check leakage & Scaling condition.
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 4 | Plug | Clean body surface for scaling and foreign particles.
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 7 | A.F.R | Clean its air filter & internal parts.
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 8 | Calibration | Calibration done after install at position. (0-100%)
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | 9 | Monitoring Instruments | Check & clean physical condition.
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 1 | Actuator | Unscrew the actuator from bracket
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 1 | Actuator | Check the actuator kit & adjustable spring.
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 1 | Actuator | Proper lubricant & assembling all parts.
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 2 | Body | Check physical condition. | [5 empty] | Yes
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 2 | Body | Clean body surface for scaling and foreign particles.
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 3 | Seat | Replace if any requirement
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 4 | Plug | Check leakage & Scaling condition.
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 4 | Plug | Clean body surface for scaling and foreign particles.
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 7 | A.F.R | Clean its air filter & internal parts.
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 8 | Calibration | Calibration done after install at position. (0-100%)
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | 9 | Monitoring Instruments | Check & clean physical condition.
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 1 | Actuator | Unscrew the actuator from bracket
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 1 | Actuator | Proper lubricant & assembling all parts.
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 2 | Body | Clean body surface for scaling and foreign particles.
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 3 | Seat | Replace if any requirement
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 4 | Plug | Check leakage & Scaling condition.
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 7 | A.F.R | Clean its air filter & internal parts.
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | 9 | Monitoring Instruments | Check & clean physical condition.
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 1 | Actuator | Unscrew the actuator from bracket
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 1 | Actuator | Proper lubricant & assembling all parts.
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 2 | Body | Clean body surface for scaling and foreign particles.
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 3 | Seat | Replace if any requirement
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 4 | Plug | Check leakage & Scaling condition.
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 7 | A.F.R | Clean its air filter & internal parts.
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 8 | Calibration | Calibration done after install at position. (0-100%)
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | 9 | Monitoring Instruments | Check & clean physical condition.
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 1 | Actuator | Unscrew the actuator from bracket
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 1 | Actuator | Proper lubricant & assembling all parts.
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 2 | Body | Clean body surface for scaling and foreign particles.
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 3 | Seat | Replace if any requirement
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 4 | Plug | Check leakage & Scaling condition.
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 7 | A.F.R | Clean its air filter & internal parts.
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 8 | Calibration | Calibration done after install at position. (0-100%)
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | 9 | Monitoring Instruments | Check & clean physical condition.
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 1 | Actuator | Unscrew the actuator from bracket
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 1 | Actuator | Check the actuator kit & adjustable spring.
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 1 | Actuator | Proper lubricant & assembling all parts.
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 2 | Body | Check physical condition. | [5 empty] | Yes
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 2 | Body | Clean body surface for scaling and foreign particles.
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 3 | Seat | Replace if any requirement
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 4 | Plug | Check leakage & Scaling condition.
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 4 | Plug | Clean body surface for scaling and foreign particles.
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 7 | A.F.R | Clean its air filter & internal parts.
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 8 | Calibration | Calibration done after install at position. (0-100%)
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | 9 | Monitoring Instruments | Check & clean physical condition.
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 1 | Actuator | Unscrew the actuator from bracket
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 1 | Actuator | Check the actuator kit & adjustable spring.
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 1 | Actuator | Proper lubricant & assembling all parts.
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 2 | Body | Check physical condition. | [5 empty] | Yes
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 2 | Body | Clean body surface for scaling and foreign particles.
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 3 | Seat | Replace if any requirement
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 4 | Plug | Check leakage & Scaling condition.
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 4 | Plug | Clean body surface for scaling and foreign particles.
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 7 | A.F.R | Clean its air filter & internal parts.
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 8 | Calibration | Calibration done after install at position. (0-100%)
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | 9 | Monitoring Instruments | Check & clean physical condition.
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 1 | Actuator | Unscrew the actuator from bracket
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 1 | Actuator | Proper lubricant & assembling all parts.
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 2 | Body | Clean body surface for scaling and foreign particles.
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 3 | Seat | Replace if any requirement
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 4 | Plug | Check leakage & Scaling condition.
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 7 | A.F.R | Clean its air filter & internal parts.
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | 9 | Monitoring Instruments | Check & clean physical condition.
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 1 | Actuator | Unscrew the actuator from bracket
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 1 | Actuator | Proper lubricant & assembling all parts.
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 2 | Body | Clean body surface for scaling and foreign particles.
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 3 | Seat | Replace if any requirement
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 4 | Plug | Check leakage & Scaling condition.
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 7 | A.F.R | Clean its air filter & internal parts.
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 8 | Calibration | Calibration done after install at position. (0-100%)
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | 9 | Monitoring Instruments | Check & clean physical condition.
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 1 | Actuator | Unscrew the actuator from bracket
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 1 | Actuator | Check the actuator kit & adjustable spring.
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 1 | Actuator | Proper lubricant & assembling all parts.
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 2 | Body | Check physical condition. | [5 empty] | Yes
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 2 | Body | Clean body surface for scaling and foreign particles.
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 3 | Seat | Replace if any requirement
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 4 | Plug | Check leakage & Scaling condition.
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 4 | Plug | Clean body surface for scaling and foreign particles.
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 7 | A.F.R | Clean its air filter & internal parts.
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 8 | Calibration | Calibration done after install at position. (0-100%)
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | 9 | Monitoring Instruments | Check & clean physical condition.
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 1 | Actuator | Unscrew the actuator from bracket
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 1 | Actuator | Check the actuator kit & adjustable spring.
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 1 | Actuator | Proper lubricant & assembling all parts.
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 2 | Body | Check physical condition. | [5 empty] | Yes
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 2 | Body | Clean body surface for scaling and foreign particles.
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 3 | Seat | Replace if any requirement
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 4 | Plug | Check leakage & Scaling condition.
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 4 | Plug | Clean body surface for scaling and foreign particles.
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 7 | A.F.R | Clean its air filter & internal parts.
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 8 | Calibration | Calibration done after install at position. (0-100%)
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | 9 | Monitoring Instruments | Check & clean physical condition.
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 1 | Actuator | Unscrew the actuator from bracket
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 1 | Actuator | Proper lubricant & assembling all parts.
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 2 | Body | Clean body surface for scaling and foreign particles.
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 3 | Seat | Replace if any requirement
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 4 | Plug | Check leakage & Scaling condition.
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 7 | A.F.R | Clean its air filter & internal parts.
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | 9 | Monitoring Instruments | Check & clean physical condition.
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 1 | Actuator | Unscrew the actuator from bracket
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 1 | Actuator | Proper lubricant & assembling all parts.
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 2 | Body | Clean body surface for scaling and foreign particles.
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 3 | Seat | Replace if any requirement
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 4 | Plug | Check leakage & Scaling condition.
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 7 | A.F.R | Clean its air filter & internal parts.
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 8 | Calibration | Calibration done after install at position. (0-100%)
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | 9 | Monitoring Instruments | Check & clean physical condition.
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 1 | Actuator | Unscrew the actuator from bracket
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 1 | Actuator | Check the actuator kit & adjustable spring.
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 1 | Actuator | Proper lubricant & assembling all parts.
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 2 | Body | Check physical condition. | [5 empty] | Yes
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 2 | Body | Clean body surface for scaling and foreign particles.
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 3 | Seat | Replace if any requirement
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 4 | Plug | Check leakage & Scaling condition.
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 4 | Plug | Clean body surface for scaling and foreign particles.
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 7 | A.F.R | Clean its air filter & internal parts.
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 8 | Calibration | Calibration done after install at position. (0-100%)
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | 9 | Monitoring Instruments | Check & clean physical condition.
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 1 | Actuator | Unscrew the actuator from bracket
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 1 | Actuator | Check the actuator kit & adjustable spring.
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 1 | Actuator | Proper lubricant & assembling all parts.
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 2 | Body | Check physical condition. | [5 empty] | Yes
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 2 | Body | Clean body surface for scaling and foreign particles.
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 3 | Seat | Replace if any requirement
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 4 | Plug | Check leakage & Scaling condition.
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 4 | Plug | Clean body surface for scaling and foreign particles.
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 7 | A.F.R | Clean its air filter & internal parts.
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 8 | Calibration | Calibration done after install at position. (0-100%)
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | 9 | Monitoring Instruments | Check & clean physical condition.
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 1 | Actuator | Unscrew the actuator from bracket
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 1 | Actuator | Proper lubricant & assembling all parts.
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 2 | Body | Clean body surface for scaling and foreign particles.
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 3 | Seat | Replace if any requirement
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 4 | Plug | Check leakage & Scaling condition.
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 7 | A.F.R | Clean its air filter & internal parts.
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | 9 | Monitoring Instruments | Check & clean physical condition.
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 1 | Actuator | Unscrew the actuator from bracket
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 1 | Actuator | Proper lubricant & assembling all parts.
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 2 | Body | Clean body surface for scaling and foreign particles.
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 3 | Seat | Replace if any requirement
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 4 | Plug | Check leakage & Scaling condition.
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 7 | A.F.R | Clean its air filter & internal parts.
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 8 | Calibration | Calibration done after install at position. (0-100%)
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | 9 | Monitoring Instruments | Check & clean physical condition.
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 1 | Actuator | Unscrew the actuator from bracket
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 1 | Actuator | Check the actuator kit & adjustable spring.
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 1 | Actuator | Proper lubricant & assembling all parts.
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 2 | Body | Check physical condition. | [5 empty] | Yes
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 2 | Body | Clean body surface for scaling and foreign particles.
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 3 | Seat | Replace if any requirement
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 4 | Plug | Check leakage & Scaling condition.
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 4 | Plug | Clean body surface for scaling and foreign particles.
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 7 | A.F.R | Clean its air filter & internal parts.
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 8 | Calibration | Calibration done after install at position. (0-100%)
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | 9 | Monitoring Instruments | Check & clean physical condition.
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 1 | Actuator | Unscrew the actuator from bracket
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 1 | Actuator | Check the actuator kit & adjustable spring.
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 1 | Actuator | Proper lubricant & assembling all parts.
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 2 | Body | Check physical condition. | [5 empty] | Yes
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 2 | Body | Clean body surface for scaling and foreign particles.
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 3 | Seat | Replace if any requirement
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 4 | Plug | Check leakage & Scaling condition.
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 4 | Plug | Clean body surface for scaling and foreign particles.
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 7 | A.F.R | Clean its air filter & internal parts.
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 8 | Calibration | Calibration done after install at position. (0-100%)
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | 9 | Monitoring Instruments | Check & clean physical condition.
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 1 | Actuator | Unscrew the actuator from bracket
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 1 | Actuator | Proper lubricant & assembling all parts.
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 2 | Body | Clean body surface for scaling and foreign particles.
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 3 | Seat | Replace if any requirement
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 4 | Plug | Check leakage & Scaling condition.
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 7 | A.F.R | Clean its air filter & internal parts.
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | 9 | Monitoring Instruments | Check & clean physical condition.
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 1 | Actuator | Unscrew the actuator from bracket
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 1 | Actuator | Proper lubricant & assembling all parts.
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 2 | Body | Clean body surface for scaling and foreign particles.
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 3 | Seat | Replace if any requirement
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 4 | Plug | Check leakage & Scaling condition.
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 7 | A.F.R | Clean its air filter & internal parts.
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | 9 | Monitoring Instruments | Check & clean physical condition.
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 1 | Actuator | Unscrew the actuator from bracket
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 1 | Actuator | Proper lubricant & assembling all parts.
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 2 | Body | Clean body surface for scaling and foreign particles.
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 3 | Seat | Replace if any requirement
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 4 | Plug | Check leakage & Scaling condition.
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 7 | A.F.R | Clean its air filter & internal parts.
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | 9 | Monitoring Instruments | Check & clean physical condition.
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 1 | Actuator | Unscrew the actuator from bracket
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 1 | Actuator | Check the actuator kit & adjustable spring.
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 1 | Actuator | Proper lubricant & assembling all parts.
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 2 | Body | Check physical condition. | [5 empty] | Yes
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 2 | Body | Clean body surface for scaling and foreign particles.
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 3 | Seat | Replace if any requirement
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 4 | Plug | Check leakage & Scaling condition.
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 4 | Plug | Clean body surface for scaling and foreign particles.
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 7 | A.F.R | Clean its air filter & internal parts.
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 8 | Calibration | Calibration done after install at position. (0-100%)
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | 9 | Monitoring Instruments | Check & clean physical condition.
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 1 | Actuator | Unscrew the actuator from bracket
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 1 | Actuator | Check the actuator kit & adjustable spring.
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 1 | Actuator | Proper lubricant & assembling all parts.
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 2 | Body | Check physical condition. | [5 empty] | Yes
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 2 | Body | Clean body surface for scaling and foreign particles.
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 3 | Seat | Replace if any requirement
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 4 | Plug | Check leakage & Scaling condition.
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 4 | Plug | Clean body surface for scaling and foreign particles.
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 7 | A.F.R | Clean its air filter & internal parts.
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 8 | Calibration | Calibration done after install at position. (0-100%)
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | 9 | Monitoring Instruments | Check & clean physical condition.
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 1 | Actuator | Unscrew the actuator from bracket
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 1 | Actuator | Proper lubricant & assembling all parts.
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 2 | Body | Clean body surface for scaling and foreign particles.
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 3 | Seat | Replace if any requirement
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 4 | Plug | Check leakage & Scaling condition.
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 7 | A.F.R | Clean its air filter & internal parts.
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | 9 | Monitoring Instruments | Check & clean physical condition.
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 1 | Actuator | Unscrew the actuator from bracket
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 1 | Actuator | Check the actuator kit & adjustable spring.
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 1 | Actuator | Proper lubricant & assembling all parts.
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 2 | Body | Check physical condition. | [5 empty] | Yes
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 2 | Body | Clean body surface for scaling and foreign particles.
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 3 | Seat | Replace if any requirement
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 4 | Plug | Check leakage & Scaling condition.
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 4 | Plug | Clean body surface for scaling and foreign particles.
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 7 | A.F.R | Clean its air filter & internal parts.
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 8 | Calibration | Calibration done after install at position. (0-100%)
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | 9 | Monitoring Instruments | Check & clean physical condition.
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 1 | Actuator | Unscrew the actuator from bracket
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 1 | Actuator | Proper lubricant & assembling all parts.
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 2 | Body | Clean body surface for scaling and foreign particles.
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 3 | Seat | Replace if any requirement
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 4 | Plug | Check leakage & Scaling condition.
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 7 | A.F.R | Clean its air filter & internal parts.
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | 9 | Monitoring Instruments | Check & clean physical condition.
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 1 | Actuator | Unscrew the actuator from bracket
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 1 | Actuator | Check the actuator kit & adjustable spring.
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 1 | Actuator | Proper lubricant & assembling all parts.
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 2 | Body | Check physical condition. | [5 empty] | Yes
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 2 | Body | Clean body surface for scaling and foreign particles.
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 3 | Seat | Replace if any requirement
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 4 | Plug | Check leakage & Scaling condition.
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 4 | Plug | Clean body surface for scaling and foreign particles.
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 7 | A.F.R | Clean its air filter & internal parts.
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 8 | Calibration | Calibration done after install at position. (0-100%)
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | 9 | Monitoring Instruments | Check & clean physical condition.
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 1 | Actuator | Unscrew the actuator from bracket
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 1 | Actuator | Check the actuator kit & adjustable spring.
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 1 | Actuator | Proper lubricant & assembling all parts.
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 2 | Body | Check physical condition. | [5 empty] | Yes
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 2 | Body | Clean body surface for scaling and foreign particles.
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 3 | Seat | Replace if any requirement
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 4 | Plug | Check leakage & Scaling condition.
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 4 | Plug | Clean body surface for scaling and foreign particles.
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 7 | A.F.R | Clean its air filter & internal parts.
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 8 | Calibration | Calibration done after install at position. (0-100%)
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | 9 | Monitoring Instruments | Check & clean physical condition.
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 1 | Actuator | Unscrew the actuator from bracket
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 1 | Actuator | Check the actuator kit & adjustable spring.
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 1 | Actuator | Proper lubricant & assembling all parts.
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 2 | Body | Check physical condition. | [5 empty] | Yes
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 2 | Body | Clean body surface for scaling and foreign particles.
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 3 | Seat | Replace if any requirement
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 4 | Plug | Check leakage & Scaling condition.
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 4 | Plug | Clean body surface for scaling and foreign particles.
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 7 | A.F.R | Clean its air filter & internal parts.
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 8 | Calibration | Calibration done after install at position. (0-100%)
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | 9 | Monitoring Instruments | Check & clean physical condition.
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 1 | Actuator | Unscrew the actuator from bracket
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 1 | Actuator | Check the actuator kit & adjustable spring.
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 1 | Actuator | Proper lubricant & assembling all parts.
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 2 | Body | Check physical condition. | [5 empty] | Yes
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 2 | Body | Clean body surface for scaling and foreign particles.
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 3 | Seat | Replace if any requirement
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 4 | Plug | Check leakage & Scaling condition.
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 4 | Plug | Clean body surface for scaling and foreign particles.
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 7 | A.F.R | Clean its air filter & internal parts.
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 8 | Calibration | Calibration done after install at position. (0-100%)
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
fa7bc5cf2fa1 | Ref. Condensor 57 :: ZIL/SUG./001/CV1 | ZIL/SUG./001/CV1 | 9 | Monitoring Instruments | Check & clean physical condition.
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 1 | Actuator | Unscrew the actuator from bracket
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 1 | Actuator | Check the actuator kit & adjustable spring.
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 1 | Actuator | Proper lubricant & assembling all parts.
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 2 | Body | Check physical condition. | [5 empty] | Yes
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 2 | Body | Clean body surface for scaling and foreign particles.
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 3 | Seat | Replace if any requirement
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 4 | Plug | Check leakage & Scaling condition.
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 4 | Plug | Clean body surface for scaling and foreign particles.
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication. | [5 empty] | Yes
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 6 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 6 | Positioner/ Solenoid valve | Check with loop calibrator.
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 6 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 7 | A.F.R | Check Air output supply. | [5 empty] | Yes
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 7 | A.F.R | Clean its air filter & internal parts.
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 8 | Calibration | Calibration done after install at position. (0-100%)
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 9 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
e02aff0e8587 | Ref. Condensor 57 :: ZIL/SUG./001/CV2 | ZIL/SUG./001/CV2 | 9 | Monitoring Instruments | Check & clean physical condition.
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | 1 | Sensor | Sensor cleaning & check its shape . | [5 empty] | Yes
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | 1 | Sensor | Check its continuity end the conector.
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | 2 | Power supply Card | check Its eatrhing voltage.
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | 3 | Microprocessor Unit | Check its output signal
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | 5 | Liner | Check its any deformation parts.
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | 7 | Monitoring Instruments | Check & clean physical condition.
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | 1 | Sensor | Check its continuity end the conector.
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | 2 | Power supply Card | check Its eatrhing voltage.
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | 3 | Microprocessor Unit | Check its output signal
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | 5 | Liner | Check its scaling. | [5 empty] | Yes
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | 5 | Liner | Check its any deformation parts.
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | 7 | Monitoring Instruments | Check & clean physical condition.
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | 1 | Sensor | Check its continuity end the conector.
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | 2 | Power supply Card | check Its eatrhing voltage.
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | 3 | Microprocessor Unit | Check its output signal
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | 5 | Liner | Check its scaling. | [5 empty] | Yes
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | 5 | Liner | Check its any deformation parts.
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | 7 | Monitoring Instruments | Check & clean physical condition.
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | 1 | Sensor | Check its continuity end the conector.
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | 2 | Power supply Card | check Its eatrhing voltage.
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | 3 | Microprocessor Unit | Check its output signal
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | 5 | Liner | Check its scaling. | [5 empty] | Yes
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | 5 | Liner | Check its any deformation parts.
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | 7 | Monitoring Instruments | Check & clean physical condition.
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | 1 | Sensor | Check its continuity end the conector.
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | 2 | Power supply Card | check Its eatrhing voltage.
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | 3 | Microprocessor Unit | Check its output signal
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | 5 | Liner | Check its scaling. | [5 empty] | Yes
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | 5 | Liner | Check its any deformation parts.
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | 7 | Monitoring Instruments | Check & clean physical condition.
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | 1 | Sensor | Check its continuity end the conector.
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | 2 | Power supply Card | check Its eatrhing voltage.
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | 3 | Microprocessor Unit | Check its output signal
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | 5 | Liner | Check its scaling. | [5 empty] | Yes
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | 5 | Liner | Check its any deformation parts.
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | 7 | Monitoring Instruments | Check & clean physical condition.
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | 1 | Sensor | Check its continuity end the conector.
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | 2 | Power supply Card | check Its eatrhing voltage.
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | 3 | Microprocessor Unit | Check its output signal
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | 5 | Liner | Check its scaling. | [5 empty] | Yes
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | 5 | Liner | Check its any deformation parts.
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | 7 | Monitoring Instruments | Check & clean physical condition.
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | 1 | Sensor | Check its continuity end the conector.
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | 2 | Power supply Card | check Its eatrhing voltage.
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | 3 | Microprocessor Unit | Check its output signal
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | 5 | Liner | Check its scaling. | [5 empty] | Yes
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | 5 | Liner | Check its any deformation parts.
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | 7 | Monitoring Instruments | Check & clean physical condition.
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | 1 | Sensor | Check its continuity end the conector.
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | 2 | Power supply Card | check Its eatrhing voltage.
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | 3 | Microprocessor Unit | Check its output signal
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | 5 | Liner | Check its scaling. | [5 empty] | Yes
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | 5 | Liner | Check its any deformation parts.
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | 7 | Monitoring Instruments | Check & clean physical condition.
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | 1 | Sensor | Check its continuity end the conector.
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | 2 | Power supply Card | check Its eatrhing voltage.
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | 3 | Microprocessor Unit | Check its output signal
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | 5 | Liner | Check its scaling. | [5 empty] | Yes
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | 5 | Liner | Check its any deformation parts.
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | 7 | Monitoring Instruments | Check & clean physical condition.
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | 1 | Sensor | Check its continuity end the conector.
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | 2 | Power supply Card | check Its eatrhing voltage.
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | 3 | Microprocessor Unit | Check its output signal
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | 5 | Liner | Check its scaling. | [5 empty] | Yes
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | 5 | Liner | Check its any deformation parts.
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | 7 | Monitoring Instruments | Check & clean physical condition.
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | 1 | Sensor | Check its continuity end the conector.
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | 2 | Power supply Card | check Its eatrhing voltage.
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | 3 | Microprocessor Unit | Check its output signal
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | 5 | Liner | Check its scaling. | [5 empty] | Yes
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | 5 | Liner | Check its any deformation parts.
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | 7 | Monitoring Instruments | Check & clean physical condition.
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | 1 | Sensor | Check its continuity end the conector.
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | 2 | Power supply Card | check Its eatrhing voltage.
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | 3 | Microprocessor Unit | Check its output signal
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | 5 | Liner | Check its scaling. | [5 empty] | Yes
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | 5 | Liner | Check its any deformation parts.
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | 7 | Monitoring Instruments | Check & clean physical condition.
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | 1 | Sensor | Check its continuity end the conector.
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | 2 | Power supply Card | check Its eatrhing voltage.
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | 3 | Microprocessor Unit | Check its output signal
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | 5 | Liner | Check its scaling. | [5 empty] | Yes
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | 5 | Liner | Check its any deformation parts.
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | 7 | Monitoring Instruments | Check & clean physical condition.
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | 1 | Sensor | Check its continuity end the conector.
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | 2 | Power supply Card | check Its eatrhing voltage.
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | 3 | Microprocessor Unit | Check its output signal
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | 5 | Liner | Check its scaling. | [5 empty] | Yes
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | 5 | Liner | Check its any deformation parts.
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | 7 | Monitoring Instruments | Check & clean physical condition.
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | 1 | Sensor | Check its continuity end the conector.
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | 2 | Power supply Card | check Its eatrhing voltage.
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | 3 | Microprocessor Unit | Check its output signal
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | 5 | Liner | Check its scaling. | [5 empty] | Yes
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | 5 | Liner | Check its any deformation parts.
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | 7 | Monitoring Instruments | Check & clean physical condition.
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | 1 | Sensor | Check its continuity end the conector.
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | 2 | Power supply Card | check Its eatrhing voltage.
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | 3 | Microprocessor Unit | Check its output signal
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | 5 | Liner | Check its scaling. | [5 empty] | Yes
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | 5 | Liner | Check its any deformation parts.
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | 7 | Monitoring Instruments | Check & clean physical condition.
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | 1 | Sensor | Check its continuity end the conector.
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | 2 | Power supply Card | check Its eatrhing voltage.
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | 3 | Microprocessor Unit | Check its output signal
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | 5 | Liner | Check its scaling. | [5 empty] | Yes
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | 5 | Liner | Check its any deformation parts.
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | 7 | Monitoring Instruments | Check & clean physical condition.
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | 1 | Sensor | Check its continuity end the conector.
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | 2 | Power supply Card | check Its eatrhing voltage.
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | 3 | Microprocessor Unit | Check its output signal
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | 5 | Liner | Check its scaling. | [5 empty] | Yes
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | 5 | Liner | Check its any deformation parts.
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
d2cecfab4a9d | Ref Flow Meter h :: ZIL/SUG./01/IER-4-FEED | ZIL/SUG./01/IER-4-FEED | 7 | Monitoring Instruments | Check & clean physical condition.
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 1 | Program and Data Backups | Up-to-date and routine backup of the controller programing. | [5 empty] | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 1 | Program and Data Backups | This is done by saving a copy of your controller program in a compact disk. | [5 empty] | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 1 | Program and Data Backups | Be sure to keep them safely away from high humidity,extreme temperatures, and exposure to RFI and EMI. | [5 empty] | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 2 | Check Program Functionality | Check the functionality of the operating program to ensure the equipment or process being controlled is functioning as required. | [5 empty] | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 2 | Check Program Functionality | This is done by comprehensively testing the controller program for correctness in functionality, safety, reliability, and predictability. | [5 empty] | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 3 | Check the Power & Controller LED Indicator | Check all indicator. |  | Yes |  | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 4 | Check the Operating Voltage and Current | Check all value. |  | Yes |  |  |  | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 5 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 6 | Inspect the Overall Condition of the Controller Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 7 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 8 | Inspect the Cleanliness of your controller Module | Check to Dust Removal |  | Yes |  |  |  | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 8 | Inspect the Cleanliness of your controller Module | Clean and Change Filters |  | Yes |  |  |  | Yes
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | 8 | Inspect the Cleanliness of your controller Module | Maintain Ventilation |  | Yes |  |  |  | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 1 | Program and Data Backups | Up-to-date and routine backup of the controller programing. | [5 empty] | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 1 | Program and Data Backups | This is done by saving a copy of your controller program in a compact disk. | [5 empty] | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 1 | Program and Data Backups | Be sure to keep them safely away from high humidity,extreme temperatures, and exposure to RFI and EMI. | [5 empty] | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 2 | Check Program Functionality | Check the functionality of the operating program to ensure the equipment or process being controlled is functioning as required. | [5 empty] | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 2 | Check Program Functionality | This is done by comprehensively testing the controller program for correctness in functionality, safety, reliability, and predictability. | [5 empty] | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 3 | Check the Power & Controller LED Indicator | Check all indicator. |  | Yes |  |  |  | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 4 | Check the Operating Voltage and Current | Check all value. |  | Yes |  |  |  | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 5 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 6 | Inspect the Overall Condition of the Controller Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 7 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 8 | Inspect the Cleanliness of your controller Module | Check to Dust Removal |  | Yes |  |  |  | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 8 | Inspect the Cleanliness of your controller Module | Clean and Change Filters |  | Yes |  |  |  | Yes
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | 8 | Inspect the Cleanliness of your controller Module | Maintain Ventilation |  | Yes |  |  |  | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 1 | Program and Data Backups | Up-to-date and routine backup of the controller programing. | [5 empty] | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 1 | Program and Data Backups | This is done by saving a copy of your controller program in a compact disk. | [5 empty] | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 1 | Program and Data Backups | Be sure to keep them safely away from high humidity,extreme temperatures, and exposure to RFI and EMI. | [5 empty] | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 2 | Check Program Functionality | Check the functionality of the operating program to ensure the equipment or process being controlled is functioning as required. | [5 empty] | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 2 | Check Program Functionality | This is done by comprehensively testing the controller program for correctness in functionality, safety, reliability, and predictability. | [5 empty] | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 3 | Check the Power & Controller LED Indicator | Check all indicator. |  | Yes |  |  |  | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 4 | Check the Operating Voltage and Current | Check all value. |  | Yes |  |  |  | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 5 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 6 | Inspect the Overall Condition of the Controller Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 7 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 8 | Inspect the Cleanliness of your controller Module | Check to Dust Removal |  | Yes |  |  |  | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 8 | Inspect the Cleanliness of your controller Module | Clean and Change Filters |  | Yes |  |  |  | Yes
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | 8 | Inspect the Cleanliness of your controller Module | Maintain Ventilation |  | Yes |  |  |  | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 1 | Program and Data Backups | Up-to-date and routine backup of the controller programing. | [5 empty] | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 1 | Program and Data Backups | This is done by saving a copy of your controller program in a compact disk. | [5 empty] | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 1 | Program and Data Backups | Be sure to keep them safely away from high humidity,extreme temperatures, and exposure to RFI and EMI. | [5 empty] | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 2 | Check Program Functionality | Check the functionality of the operating program to ensure the equipment or process being controlled is functioning as required. | [5 empty] | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 2 | Check Program Functionality | This is done by comprehensively testing the controller program for correctness in functionality, safety, reliability, and predictability. | [5 empty] | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 3 | Check the Power & Controller LED Indicator | Check all indicator. |  | Yes |  |  |  | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 4 | Check the Operating Voltage and Current | Check all value. |  | Yes |  |  |  | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 5 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 6 | Inspect the Overall Condition of the Controller Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 7 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 8 | Inspect the Cleanliness of your controller Module | Check to Dust Removal |  | Yes |  |  |  | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 8 | Inspect the Cleanliness of your controller Module | Clean and Change Filters |  | Yes |  |  |  | Yes
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | 8 | Inspect the Cleanliness of your controller Module | Maintain Ventilation |  | Yes |  |  |  | Yes
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. | [5 empty] | Yes
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. | [5 empty] | Yes
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal | [5 empty] | Yes
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters | [5 empty] | Yes
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation | [5 empty] | Yes
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | 1 | Check the Power & module LED Indicator | Check all indicator. | [5 empty] | Yes
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | 2 | Check the Operating Voltage and Current | Check all value. | [5 empty] | Yes
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | 3 | Check Connections | Periodically check all connections to the controller system such as communication cables, terminal strips, sockets, plugs, field wiring, and I/O modules. | [5 empty] | Yes
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | 4 | Inspect the Overall Condition of the module Components | Visually inspect the CPU and the other controller modules for wear, warping, distortion indications of overheated components like burnt odors or discoloration. |  | Yes |  |  |  | Yes
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | 5 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the controller components. |  | Yes |  |  |  | Yes
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | 6 | Inspect the Cleanliness of your cluster Module | Check to Dust Removal |  | Yes |  |  |  | Yes
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | 6 | Inspect the Cleanliness of your cluster Module | Clean and Change Filters |  | Yes |  |  |  | Yes
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | 6 | Inspect the Cleanliness of your cluster Module | Maintain Ventilation |  | Yes |  |  |  | Yes
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | 1 | Physical Inspection | Cleanliness: Ensure the workstation is clean and free from dust and debris |  | Yes |  |  |  | Yes
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes |  |  |  | Yes
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | 1 | Physical Inspection | Power Supply: Verify that the workstation is properly connected to a power source and is receiving power. |  | Yes |  |  |  | Yes
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | 2 | Hardware Check | Monitor: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | 2 | Hardware Check | Keyboard and Mouse: Test the keyboard and mouse for responsiveness. |  | Yes |  |  |  | Yes
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | 3 | Software and System Check | Boot Up: Turn on the workstation and observe the boot process for any error messages. |  |  |  | Yes |  | Yes
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | 3 | Software and System Check | Applications: Ensure all necessary applications are installed and functioning. |  |  |  | Yes |  | Yes
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures can negatively affect the workstation components. |  | Yes |  | Yes |  | Yes
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | 5 | Inspect the Cleanliness of console | Check to Dust Removal |  | Yes |  |  |  | Yes
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | 5 | Inspect the Cleanliness of console | Clean and Change Filters |  | Yes |  |  |  | Yes
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | 5 | Inspect the Cleanliness of console | Maintain Ventilation |  | Yes |  |  |  | Yes
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | 1 | Physical Inspection | Cleanliness: Ensure the panel is clean and free from dust and debris |  | Yes | Yes |  |  | Yes
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes | Yes |  |  | Yes
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | 1 | Physical Inspection | Power Supply: Verify that the panel is properly connected to a power source and is receiving power. |  | Yes | Yes |  |  | Yes
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | 2 | Hardware Check | Display: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | 2 | Hardware Check | Keypad button: Test the keypad buttons for responsiveness. |  | Yes |  |  |  | Yes
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | 3 | Software and System Check | Boot Up: Turn on the panel and observe the boot process for any error messages. | [5 empty] | Yes
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | 3 | Software and System Check | Applications: Ensure all necessary dedector & MCP are functioning. | [5 empty] | Yes
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures ovserve or not. |  |  | Yes |  |  | Yes
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | 5 | Inspect the Cleanliness of panel | Check to Dust Removal |  | Yes |  |  |  | Yes
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | 5 | Inspect the Cleanliness of panel | Cleanness of panel |  | Yes |  |  |  | Yes
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | 5 | Inspect the Cleanliness of panel | Maintain Ventilation |  | Yes |  |  |  | Yes
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | 1 | Physical Inspection | Cleanliness: Ensure the panel is clean and free from dust and debris |  | Yes | Yes |  |  | Yes
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes | Yes |  |  | Yes
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | 1 | Physical Inspection | Power Supply: Verify that the panel is properly connected to a power source and is receiving power. |  | Yes | Yes |  |  | Yes
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | 2 | Hardware Check | Display: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | 2 | Hardware Check | Keypad button: Test the keypad buttons for responsiveness. |  | Yes |  |  |  | Yes
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | 3 | Software and System Check | Boot Up: Turn on the panel and observe the boot process for any error messages. | [5 empty] | Yes
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | 3 | Software and System Check | Applications: Ensure all necessary dedector & MCP are functioning. | [5 empty] | Yes
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures ovserve or not. |  |  | Yes |  |  | Yes
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | 5 | Inspect the Cleanliness of panel | Check to Dust Removal |  | Yes |  |  |  | Yes
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | 5 | Inspect the Cleanliness of panel | Cleanness of panel |  | Yes |  |  |  | Yes
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | 5 | Inspect the Cleanliness of panel | Maintain Ventilation |  | Yes |  |  |  | Yes
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | 1 | Physical Inspection | Cleanliness: Ensure the panel is clean and free from dust and debris |  | Yes | Yes |  |  | Yes
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | 1 | Physical Inspection | Connections: Check all cables and connections for signs of wear or damage. |  | Yes | Yes |  |  | Yes
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | 1 | Physical Inspection | Power Supply: Verify that the panel is properly connected to a power source and is receiving power. |  | Yes | Yes |  |  | Yes
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | 2 | Hardware Check | Display: Ensure the monitor is functioning correctly, with no dead pixels or flickering. |  | Yes |  |  |  | Yes
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | 2 | Hardware Check | Keypad button: Test the keypad buttons for responsiveness. |  | Yes |  |  |  | Yes
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | 2 | Hardware Check | Peripheral Devices: Check other peripherals ports for proper functionality. |  | Yes |  |  |  | Yes
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | 3 | Software and System Check | Boot Up: Turn on the panel and observe the boot process for any error messages. | [5 empty] | Yes
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | 3 | Software and System Check | Applications: Ensure all necessary dedector & MCP are functioning. | [5 empty] | Yes
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | 4 | Check Operating Environmental Conditions | Environmental factors like high humidity and extreme temperatures ovserve or not. |  |  | Yes |  |  | Yes
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | 5 | Inspect the Cleanliness of panel | Check to Dust Removal |  | Yes |  |  |  | Yes
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | 5 | Inspect the Cleanliness of panel | Cleanness of panel |  | Yes |  |  |  | Yes
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | 5 | Inspect the Cleanliness of panel | Maintain Ventilation |  | Yes |  |  |  | Yes
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 1 | Electrode | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 1 | Electrode | Unscrew the Cylinder from body
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 1 | Electrode | Check the cylinder kit & Neck bush.
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 1 | Electrode | Proper lubricant & assembling all parts.
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 2 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 2 | Actuator | Unscrew the actuator from bracket
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 2 | Actuator | Check the actuator kit & adjustable spring.
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 2 | Actuator | Proper lubricant & assembling all parts.
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 3 | Body | Check physical condition. | [5 empty] | Yes
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 3 | Body | Clean body surface for scaling and foreign particles.
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 4 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 4 | Seat | Replace if any requirement
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 5 | Plug | Check leakage & Scaling condition.
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 5 | Plug | Clean body surface for scaling and foreign particles.
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 6 | Gear | Check worm wheel, gear teeth & proper lubrication.
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 7 | Positioner/ Solenoid valve | Check all internal part, gauge & clean it. | [5 empty] | Yes
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 7 | Positioner/ Solenoid valve | Check with loop calibrator.
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 7 | Positioner/ Solenoid valve | Check Solenoid valve seal kit.
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 8 | Brick Transmitter | Check all internal part, gauge & clean it. | [5 empty] | Yes
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 8 | Brick Transmitter | Check & Calibrated
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 9 | A.F.R | Check Air output supply. | [5 empty] | Yes
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 9 | A.F.R | Clean its air filter & internal parts.
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 10 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 11 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | 11 | Monitoring Instruments | Check & clean physical condition.
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 1 | Sensor | Check its continuity end the conector.
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 2 | Power supply Card | check Its eatrhing voltage.
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 3 | Microprocessor Unit | Check its output signal
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 5 | Liner | Check its any deformation parts.
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 6 | Electronic equipment | Check equipment condition & clean. | [5 empty] | Yes
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 6 | Electronic equipment | Check wireing & Terminal,Veryfy Input/output Voltage.
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 6 | Electronic equipment | Veryfied calibration status.
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 7 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 8 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 8 | Monitoring Instruments | Check & clean physical condition.
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 1 | Actuator | Remove all air accessories. Like tubing etc. | [5 empty] | Yes
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 1 | Actuator | Unscrew the actuator from bracket
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 1 | Actuator | Check the actuator kit & adjustable spring.
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 1 | Actuator | Proper lubricant & assembling all parts.
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 2 | Body | Check physical condition. | [5 empty] | Yes
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 2 | Body | Clean body surface for scaling and foreign particles.
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 3 | Seat | Check leakage, cut and damage sign. | [5 empty] | Yes
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 3 | Seat | Replace if any requirement
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 4 | Plug | Check leakage & Scaling condition. | [5 empty] | Yes
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 4 | Plug | Clean body surface for scaling and foreign particles.
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 5 | Gear | Check worm wheel, gear teeth & proper lubrication.
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 6 | Positioner | Check all internal part, gauge & clean it. | [5 empty] | Yes
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 6 | Positioner | Check Relay ,cam,spring & kit.
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 6 | Positioner | Check with loop calibrator.
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 7 | Electronic Equipment | Check Equipment Condition & Clean | [5 empty] | Yes
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 7 | Electronic Equipment | Check wireing & Terminal ,veryfy I/P & O/PVoltage
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 7 | Electronic Equipment | Verfied Calibration Status.
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 8 | A.F.R | Check Air output supply. | [5 empty] | Yes
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 8 | A.F.R | Clean its air filter & internal parts.
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 9 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 10 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  | Yes
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | 10 | Monitoring Instruments | Check & clean physical condition.
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | 1 | Sensor | Check its continuity end the conector.
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | 2 | Power supply Card | check Its eatrhing voltage.
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | 3 | Microprocessor Unit | Check its output signal
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | 5 | Liner | Check its scaling. | [5 empty] | Yes
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | 5 | Liner | Check its any deformation parts.
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | 7 | Monitoring Instruments | Check & clean physical condition.
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | 1 | Sensor | Check its continuity end the conector.
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | 2 | Power supply Card | check Its eatrhing voltage.
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | 3 | Microprocessor Unit | Check its output signal
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | 5 | Liner | Check its scaling. | [5 empty] | Yes
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | 5 | Liner | Check its any deformation parts.
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  | Yes
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | 7 | Monitoring Instruments | Check & clean physical condition.
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | 1 | Sensor | Senor cleaning & check its shape . | [5 empty] | Yes
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | 1 | Sensor | Check its continuity end the conector.
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | 2 | Power supply Card | Check it input Voltage. | [5 empty] | Yes
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | 2 | Power supply Card | check Its eatrhing voltage.
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | 3 | Microprocessor Unit | Check its coil resistance reading. | [5 empty] | Yes
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | 3 | Microprocessor Unit | Check its output signal
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | 4 | Display | Check Its number & Characters. | [5 empty] | Yes
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | 5 | Liner | Check its scaling. | [5 empty] | Yes
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | 5 | Liner | Check its any deformation parts.
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | 6 | Calibration | Calibration done after install at position. (0-100%) | [5 empty] | Yes
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | 7 | Monitoring Instruments | Inspection & Monitoring of all Instrument. |  |  |  |  | Yes
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | 7 | Monitoring Instruments | Check & clean physical condition.

## EQUIPMENT MAINTENANCE HISTORY
sheet id | sheet name | EQUIPMENT TAG NAME/APPLICATION | Season / OFF Season | Year | Date of Start | Date of Finish | Outage/ Observation | Action Taken | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2021-02-08 |  |  | Throttle valve seat found damage. | Throttle valve & seat replace.
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2022-01-08 |  |  | Found oil Seal , Bearing clearance High. | Replace with new oil seal & Bearing..
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2023-12-09 |  |  | Found Gear coupling teeth damage. | Replace Gear coupling with new.
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2024-05-30 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasketfound damage | Gland Packing and Joint replaced by new |  | Internal
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2024-05-26 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2024-05-18 |  |  | 3Nos. Oil Cooler Inlet and Outlet side joint found damage | 3Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2024-09-04 |  |  | 45GPM Oil Filter element Found Choked | 45GPM Oil Filter element Replaced by new |  | Internal
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2024-09-18 |  |  | Emergency Valve 8Nos. Stud Found worn out | Emergency Valve 8Nos. Stud replaced by new |  | External
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2024-10-17 |  |  | Oil chamber lubrication oil servo prime 68/HP | Oil chamber lubrication oil servo prime 68/HP new oil filling in oil chamber |  | Internal
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2025-05-23 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found damage | Gland Packing and Joint replaced by new |  | Internal
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2025-04-22 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2025-07-10 |  |  | Main oil pump bushes 4Nos. Found wear out | Main Oil Pump 4Nos. Bushes replaced by new |  | Internal
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2025-07-05 |  |  | Bottom Casing Diaphragm 3Nos Screw found damage | Bottom Casing Diaphragm 3Nos Screw replaced by new |  | Internal
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2025-08-18 |  |  | Oil Cooler Nos.1,2 tubes total 396 Nos. tubes found leaked | Oil Cooler Nos.1,2 tubes total 396 Nos. tubes Retubing work done |  | Internal
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Off- Season | 2025-08-13 |  |  | Turbine , Oil Cooler, Water Valves,Padstal bearing cover found dirty | Turbine , Oil Cooler, Water Valves,Oil Cooler,Padstal bearing cover Cleaning and painting work done |  | External
9d00e5872e68 | TURBINE :: ZIL/SUG/01 | ZIL/SUG/01 | Season | 2026-01-29 |  |  | 3 mw old main exhaust steam valve steam nut broken | old steam watch then new threded in workshop after that fitted in position |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2021-08-07 |  |  | Throttle valve seat found damage. | Throttle valve & seat replace.
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2022-01-08 |  |  | Found Gear coupling teeth damage. | Replace gear coupling with new.
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2023-07-08 |  |  | Turbine rotter blade worn-out & Diphragm Nozzle worn-out. | Turbine rotter blade replace,inter stage labyrinth under size & diphragm replaced. |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2024-05-27 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found damage | Gland Packing and Joint replaced by new |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2024-05-29 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2024-05-16 |  |  | 2Nos. Oil Cooler Inlet and Outlet side joint found damage | 2Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2024-08-01 |  |  | Casing 1st stage Top&Bottom Diaphragm blades found cracked and worn out | Casing 1st stage Top&Bottom Diaphragm Replaced by new |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2024-09-30 |  |  | 45GPM Oil Filter Found Chocked | 45GPM Oil Filter Replaced by new |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2024-10-01 |  |  | Atlernator D.E Side Top Bottom Bearing 6nos litting pad clearnace found high | Alternator D.E Side Top Bottom Bearing 6Nos. Litting pad replaced by new |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2024-10-21 |  |  | Main lube oil line oil filter 8G.P.M found chocked | Main lube oil line oil filter 8G.P.M replaced by new |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2024-10-22 |  |  | 1Nos Trap Valve found malfunctioned | 1Nos Trap Valve replaced by new |  | External
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2025-05-24 |  |  | 2Nos. Oil Cooler Inlet and Outlet side gasket found damage | 3Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2025-05-26 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found Wornout | Gland Packing and Joint replaced by new |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2025-05-24 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found wornout | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2025-07-02 |  |  | 1Nos.Relay Oil Seal found wornout | 1Nos. Relay Oil Seal replaced by new |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2025-07-10 |  |  | Alternator D.E Side padstal bearing(tittling pad) found chipout | Alternator D.E Side padstal bearing(tittling pad) replaced by remettled bearing |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2025-07-30 |  |  | 1Nos Throttle valve O/L drain valve spindle found bend | 1Nos Throttle valve O/L drain valve replaced by new |  | External
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2025-07-10 |  |  | 1Nos. Oil Baffle found leaked | 1Nos. Oil Baffle Replaced by new |  | Internal
a8964cb61c08 | TURBINE :: ZIL/SUG/02 | ZIL/SUG/02 | Off- Season | 2025-08-14 |  |  | Turbine , Oil Cooler, Water Valves,Padstal bearing cover found dirty | Turbine , Oil Cooler, Water Valves,Oil Cooler,Padstal bearing cover Cleaning and painting work done Sec .Engineer |  | External
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 18/8/2021 |  |  | Turbine governor 2 Nos weight bearing (629ZZ) damage. | Bearing replace with new. |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 25/8/2022 |  |  | Gear Box Bearing & Pinion Thrust bearing damage. | Both bearing Change with new. |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 20/8/2023 |  |  | Turbine governor 4 Nos weight bearing (629ZZ) damage. | Bearing replace with new. |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2024-05-06 |  |  | 2Nos. Oil Cooler Inlet and Outlet side gasket found damage | 2Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2024-06-26 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found damage | Gland Packing and Joint replaced by new |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2024-06-05 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2024-06-28 |  |  | Turbine Governor 07Nos.Weight bearing,2Nos.Needle Roller Bearing,3Split Pin found damage | Turbine Governor 07Nos.Weight bearing,2Nos.Needle Roller Bearing,3Split Pin replaced by new |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2024-09-04 |  |  | 45GPM Oil Filter Found Chocked | 45GPM Oil Filter Replaced by new |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2024-10-19 |  |  | 1Nos. Steam drain valve found malfunctioned | 1Nos. Steam drain valve replaced by new
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2024-10-19 |  |  | 1Nos. Trap valve found malfunctioned | 1Nos. Trap valve replaced by new
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2024-10-22 |  |  | Oil chamber lubrication oil servo prime 68/HP | Oil chamber lubrication oil servo prime 68/HP 3M.W Old turbine old oil refilling done in oil chamber
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2025-05-21 |  |  | 2Nos. Oil Cooler Inlet and Outlet side gasket found damage | 3Nos. Oil Cooler Inlet and Outlet side joint replaced by new |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2025-05-30 |  |  | Main Steam valve,Main Exhaust valve,Exhaust bypass valve gland packing and gasket found damage | Gland Packing and Joint replaced by new |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2025-05-15 |  |  | Steam line drain valves,exhaust line drain valves,turbine drain valves gland packing found damage | Steam line drain valves,exhaust line drain valves,turbine drain valves overhauling done and gland packing replaced by new |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2025-07-02 |  |  | 1Nos Pinion Plain Bearing found chipout | 1Nos Pinion Plain Bearing replaced by new |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2025-07-03 |  |  | 4Nos rotor fore bearing stud found thread found wearout | 4Nos rotor fore bearing stud replaced by new
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2025-05-08 |  |  | Governor 8 Nos weight bearing (629ZZ),2Nos Needle roller bearing,1Nos Race Carrier,1Nos 7205 bearing ,1nos. Fulcrum pin, 4Nos. Split pin found wornout | Governor 8 Nos weight bearing (629ZZ),2Nos Needle roller bearing,1Nos Race Carrier,1Nos 7205 bearing replaced by new |  | Internal
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Off- Season | 2025-08-08 |  |  | Turbine ,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler found dirty | Turbine ,,lubrication line Oil Cooler, Water Valves, Fmg pump ,vertical Cooler Cleaning and painting work done |  | External
2439fbd82dd9 | TURBINE :: ZIL/SUG/03 | ZIL/SUG/03 | Season | 2025-10-29 |  |  | throtle valve opening less then as required | throttle valve opening setting increase 18.5 mm to 20 mm Sec .Engineer
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | OFF Season | 30.06.2022 |  |  | Control valve found scaled and rusty. | Proper cleaning & lubrication work done. |  | Internal | A Varma / V singh
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | OFF Season | 25.07.2023 |  |  | Control valve found scaled and rusty. | Proper Plug,Actuator,seat body,AFR unit Cleaning repairing with checking work done. |  | Internal | A Varma / V singh
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | OFF Season | 27.08.2024 |  |  | Control valve found scaled and rusty. | Proper Plug,Actuator,seat body,AFR unit Cleaning repairing with checking work done.with valve gland fillin & painting work done | 350 | Internal | A Varma / V singh
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | OFF Season | 16.07.2025 |  |  | Control valve found scaled and rusty. | Proper Plug,Actuator,seat body,AFR unit Cleaning repairing with checking work done.with valve gland fillin & painting work done | 350 | Internal | A Varma / V singh
0bf4f35b1931 | Mill-16 :: ZIL/SUG./001 (FCV_101) | ZIL/SUG./001 (FCV_101) | Season | 2025-12-07 |  |  | Control valve Gland liekage | Found Seat gland cap thred missing make new thred with take line. |  | Internal | Anuj Kumar
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | OFF Season | 01.07.2022 |  |  | Control valve found scaled and rusty. | Proper cleaning & lubrication work done. |  | Internal | A Varma / V singh
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | OFF Season | 26.07.2023 |  |  | Control valve found scaled and rusty.AFR & Positioner I/P OK | Seat,positioner,cleaning & Overhauling lubrication checking work done. |  | Internal | A Varma / V singh
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | OFF Season | 29.08.2024 |  |  | Control valve found scaled and rusty.AFR & Positioner I/P OK | Seat,positioner,cleaning & Overhauling lubrication checking work done. | 140 | Internal | A Varma / V singh
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | OFF Season | 17.07.2025 |  |  | Control valve found scaled and rusty. | Proper Plug,Actuator,seat body,AFR unit Cleaning repairing with checking work done.with valve gland fillin & painting work done | 350 | Internal | A Varma / V singh
c5bf7bc1c10d | Mill-16 :: ZIL/SUG./002 (FCV_101) | ZIL/SUG./002 (FCV_101) | Season | 2025-11-09 |  |  | Control valve Actuator Not working found diaphgram damage. | Replaced with new take in line. |  | Internal | Anuj Kumar
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | OFF Season | 01.07.2022 |  |  | Control valve found scaled and rusty. | Proper cleaning,Seat checking overling with lubrication work done. |  | Internal | A Varma / V singh
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | OFF Season | 28.07.2023 |  |  | Control valve found scaled and rusty. I/P,AFR Positioner ok | Proper cleaning,Seat checking overling with lubrication work done. |  | Internal | A Varma / V singh | Running season positioner air passing relay replaced with new.
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | OFF Season | 18.07.2024 |  |  | Control valve found scaled and rusty. | Valve Seat,gear,positioner,cleaning & Overhauling lubrication checking with painting work done. | 150 | Internal | A Varma / V singh
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | OFF Season | 15.07.2025 |  |  | Control valve found scaled and rusty. | Valve Seat,gear,positioner, cleaning & Overhauling ,checking with painting work done. | 250 | Internal | A Varma / V singh
947ee1a0f346 | Mill-16 :: ZIL/SUG./003 (LCV_101) | ZIL/SUG./003 (LCV_101) | Season | 27.01.2026 |  |  | Control valve actuator not working | Found actuator spring is damage replaced it take in line. |  | Internal | Anuj Kumar | Running season actuator spring damage replaced with new.
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | OFF Season | 24.06.2022 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting. |  | Internal | A Varma / V singh
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | OFF Season | 29.07.2023 |  |  | Control valve found seat scaled and liekage AFR,SOV ok | Proper cleaning & Seat replaced with new dome switch checking work done. with painting. |  | Internal | A Varma / V singh
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | OFF Season | 07.05.2024 |  |  | Control valve found seat scaled and liekage AFR,SOV ok | Proper cleaning & Seat replaced with new dome switch checking work done. with painting. | 170 | Internal | A Varma / V singh
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | OFF Season | 12.08.2025 |  |  | Control valve found seat scaled and liekage AFR,SOV ok | Proper cleaning & Seat replaced with new dome switch checking work done. with painting. | 170 | Internal | A Varma / V singh
e029ba2b49f1 | Mill-16 :: ZIL/SUG./004 (XV_RJ1_SOV1) | ZIL/SUG./004 (XV_RJ1_SOV1) | OFF Season | 29.04.2026 |  |  | Control valve found seat scaled AFR,SOV ok | Proper Actuator & Seat SOV dome switch overhauling checking work done. | 250 | Internal | Anuj / V singh
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | OFF Season | 26.04.2022 |  |  | Control valve found scaled and rusty. | Proper cleaning & Seat replaced with new dome switch checking work done. with painting. |  | Internal | A Varma / V singh
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | OFF Season | 24.06.2023 |  |  | Control valve found scaled and rusty,Dome switch out of order .AFR & SOV ok | Proper cleaning & painting. |  | Internal | A Varma / V singh
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | OFF Season | 07.05.2024 |  |  | Control valve found scaled and rusty,Dome switch out of order .AFR & SOV ok | Proper cleaning & overhauling , dome switch checking work done. with Valve painting. | 80 | Internal | A Varma / V singh
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | Season | 08.12.2024 |  |  | Control Valve water passing | Repair it take in line | 200 | Internal | A Varma / V singh
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | OFF Season | 12.08.2025 |  |  | Control valve found seat worn-out actuator air passing | Actuator & seat replaced with new | 16500 | Internal | A Varma / V singh
b171df0157e0 | Mill-16 :: ZIL/SUG./005 (XV_RJ1_SOV1) | ZIL/SUG./005 (XV_RJ1_SOV1) | OFF Season | 29.04.2026 |  |  | Control valve found seat scaled ,AFR,SOV ok | Proper Actuator & Seat SOV dome switch overhauling checking work done. | 250 | Internal | Anuj / V singh
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | OFF Season | 20.08.2022 | [5 empty] | Internal | A Varma / V singh
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | OFF Season | 29.06.2023 |  |  | Lvel sensor spair at absluit in market | Replaced with new | 70000 | Internal | A Varma / V singh
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | OFF Season | 25.05.2024 |  |  | Lvel sensor found good condiction. | Clean with check & calibrated all sensor replaced sensor plate. | 300 | Internal | A Varma / V singh
27b6f162412b | Mill-16 :: ZIL/SUG./010 (LI_101 ) | ZIL/SUG./010 (LI_101 ) | OFF Season | 08.08.2025 |  |  | Lvel sensor Plate is damage | Clean with check & calibrated all sensor replaced sensor plate. | 1800 | Internal | A Varma / V singh
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | OFF Season | [6 empty] | Internal | A Varma / V singh
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | OFF Season | 29.06.2023 |  |  | Lvel sensor spair at absluit in market | Replaced with new | 70000 | Internal | A Varma / V singh
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | OFF Season | 08.05.2024 |  |  | Lvel sensor found good condiction. | Clean with check & calibrated all sensor replaced sensor plate. | 400 | Internal | A Varma / V singh
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | OFF Season | 12.08.2025 |  |  | Lvel sensor Plate is damage | Clean with check & calibrated all sensor replaced sensor plate. | 2000 | Internal | A Varma / V singh
2927091f1041 | Mill-16 :: ZIL/SUG./011 (LI_102 ) | ZIL/SUG./011 (LI_102 ) | Season | 01.01.2025 |  |  | New Arragement for 1st mill Temp. indicater | New indicator fitted at site. | 2000 | Internal | Sushil singh
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | OFF Season | 27.08.2022 |  |  | Lvel sensor found good condiction. | Clean with check & calibrated all sensor replaced sensor plate. |  | Internal | A Varma / V singh
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | OFF Season | 20.06.2023 |  |  | Lvel sensor found good condiction. | Clean with check & calibrated all sensor replaced sensor plate. | 400 | Internal | A Varma / V singh
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | OFF Season | 20.05.2024 |  |  | Lvel sensor Plate is damage | Clean with check & calibrated all sensor replaced sensor plate. | 2000 | Internal | A Varma / V singh
b7fc6d12f62b | Mill-16 :: ZIL/SUG./012 ( LI_103 ) | ZIL/SUG./012 ( LI_103 ) | OFF Season | 26.08.2025 |  |  | Lvel sensor spair at absluit in market | Replaced with new | 70000 | Internal | A Varma / V singh
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | OFF Season | 17.07.2022 |  |  | Lvel sensor found good condiction. | Clean with check & calibrated all sensor replaced sensor plate. |  | Internal | A Varma / V singh
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | OFF Season | 21.06.2023 |  |  | Lvel sensor found good condiction. | Clean with check & calibrated all sensor replaced sensor plate. | 400 | Internal | A Varma / V singh
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | OFF Season | 11.05.2024 |  |  | Lvel sensor Plate is damage | Clean with check & calibrated all sensor replaced sensor plate. | 2000 | Internal | A Varma / V singh
e8816bcbb3ed | Mill-16 :: ZIL/SUG./013 (LI_104 ) | ZIL/SUG./013 (LI_104 ) | OFF Season | 18.08.2025 |  |  | Lvel sensor spair at absluit in market | Replaced with new | 70000 | Internal | A Varma / V singh
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | OFF Season | 27.08.2022 |  |  | Level sensor found good condiction. | Clean with check & calibrated all sensor |  | Internal | A Varma / V singh
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | OFF Season | 29.06.2023 |  |  | Level sensor spair at absluit in market | Replaced with new | 70000 | Internal | A Varma / V singh
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | OFF Season | 10.05.2024 |  |  | Level sensor found good condiction. | Clean with check & calibrated all sensor | 300 | Internal | A Varma / V singh
41800e67671c | Mill-16 :: ZIL/SUG./014 (LI_105 ) | ZIL/SUG./014 (LI_105 ) | OFF Season | 13.08.2025 |  |  | Level sensor Plate is damage | Clean with check & calibrated all sensor replaced sensor plate. | 1800 | Internal | A Varma / V singh
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | OFF Season | 27.09.2022 |  |  | Installation of new instrument | Due to shreder Vibration Monitoring system |  | Internal | A Varma / V singh
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | OFF Season | 25.08.2023 |  |  | Remove all Tx & clean it | Calibration checking work are done. |  | Internal | A Varma / V singh
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | OFF Season | 10.09.2024 |  |  | Remove all Tx & clean it | Calibration checking work are done. |  | Internal | A Varma / V singh
7a33c1c48f41 | Mill-16 :: ZIL/SUG./015 (VIB101,VIB102,VIB106) | ZIL/SUG./015 (VIB101,VIB102,VIB106) | OFF Season | 13.09.2025 |  |  | Remove all Tx & clean it | Calibration checking work are done. |  | Internal | A Varma / V singh
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | OFF Season | 08.07.2022 |  |  | Control valve seat found scaling and rusty. | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done. |  |  | A Varma / V singh
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | OFF Season | 04.08.2023 |  |  | Control valve seat found scaling and rusty. | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done. |  | Internal | A Varma / V singh
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | OFF Season | 24.07.2024 |  |  | Control valve seat found scaling and rusty. | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done. | 250 | Internal | A Varma / V singh
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | OFF Season | 07.07.2025 |  |  | Control valve seat found scaling and rusty. | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done. | 250 | Internal | A Varma / V singh
98d45d854a4c | DCH TOWER 4 :: ZIL/SUG./010 (03.TCV.180.B01) | ZIL/SUG./010 (03.TCV.180.B01) | OFF Season | 12.06.2026 |  |  | Control valve seat found scaling and rusty.with water passing drop drop O Ring worn-out | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done. Actuator O ring replaced with new | 3700 | Internal | Anuj srivastava/ V singh
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | OFF Season | 08.07.2022 |  |  | Control valve seat body found scaling and rusty & actuator spring damage nos-02 | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done actuator spring replace with new. |  |  | A Varma / V singh
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | OFF Season | 16.08.2023 |  |  | Control valve seat,body found scaling and rusty. | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done. |  | Internal | A Varma / V singh
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | OFF Season | 26.07.2024 |  |  | Control valve seat,body found scaling and rusty. | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done.painting work done. | 250 | Internal | A Varma / V singh
c219e585b204 | DCH TOWER 4 :: ZIL/SUG./011 (05.TCV.120.B01) | ZIL/SUG./011 (05.TCV.120.B01) | OFF Season | 03.07.2025 |  |  | Control valve seat,body found scaling and rusty. | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done.painting work done. | 250 | Internal | A Varma / V singh
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | OFF Season | 09.06.2022 |  |  | Control valve seat,body found scaling and rusty. | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done. |  |  | A Varma / V singh
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | OFF Season | 17.08.2023 |  |  | Control valve seat,body found scaling and rusty. | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done. |  | Internal | A Varma / V singh
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | OFF Season | 25.07.2024 |  |  | Control valve seat,body found scaling and rusty.Actuator 1 nos. Spring found damage. | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done.spring replaced with new | 3250 | Internal | A Varma / V singh
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | OFF Season | 05.07.2025 |  |  | Control valve seat,body found scaling and rusty.Actuator 1 nos. Spring found damage. | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done.spring replaced with new | 3250 | Internal | A Varma / V singh
728aab9228cb | DCH TOWER 4 :: ZIL/SUG./012 (03.TCV.190.B01) | ZIL/SUG./012 (03.TCV.190.B01) | OFF Season | 2026-06-16 |  |  | Control valve seat,body found scaling and rusty.Seat body worn-out 30%.Seat worn-out 50%. | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done.spring replaced with new | 500 | Internal | Anuj srivastava / V singh
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | OFF Season | 09.06.2022 |  |  | Control valve seat & body found scaling and rusty. | Gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. |  |  | A Varma / V singh
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | OFF Season | 18.08.2023 |  |  | Control valve seat &body found scaling and rusty found spring damage nos-01 | Gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting spring replaced with new. | 3250 | Internal | A Varma / V singh
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | OFF Season | 26..07.2024 |  |  | Control valve seat &body found scaling and rusty | Gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting work done. | 150 | Internal | A Varma / V singh
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | OFF Season | 05.07.2025 |  |  | Control valve seat & body found scaling and rusty. | Gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. | 200 | Internal | A Varma / V singh
0e16f540bdb9 | DCH TOWER 4 :: ZIL/SUG./013 ( 05TCV.130.B01) | ZIL/SUG./013 ( 05TCV.130.B01) | OFF Season | 2026-06-15 |  |  | Control valve seat,body found scaling and rusty.Seat body worn-out 30%.Seat water passing with moister found in actuator | Gear,actuator,seat body,positioner,AFR ,valve seat cleaning ,checking & repairing work done.spring replaced with new | 500 | Internal | Anuj srivastava / V singh
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | OFF Season | 14.06.2022 |  |  | Control valve is found seat,body scaling and rusty. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. | 200 | Internal | A Varma / V singh
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | OFF Season | 24.06.2023 |  |  | Control valve is found seat,body scaling and rusty with spring damage nos-01 | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. spring replaced with new | 2500 | Internal | A Varma / V singh
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | OFF Season | 11.05.2024 |  |  | Control valve is found seat,body scalingrusty and spring ,repair kit,APF positioner ok | Proper Gear,Actuator,seat body,AFR unit Cleaning repairing with checking work done. | 150 | Internal | A Varma / V singh
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | OFF Season | 07.07.2025 |  |  | Control valve is found seat,body scalingrusty and spring found healthy. | Proper Gear,Actuator,seat body,AFR unit Cleaning repairing with checking work done. | 250 | Internal | A Varma / V singh
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | Season | 2026-03-05 |  |  | Deficated juice tank level transmitter diaphrgam wear-out. Not trim zero. | Level transmitter show false reading when tank is empty. Many time trim zero but show value is too low alaram. |  | Internal | Anuj Srivastava. / V singh | To be Repair
dba6174703a9 | RJH-21-27 :: ZIL/SUG./014 (03.TCV.100.B01) | ZIL/SUG./014 (03.TCV.100.B01) | OFF Season | 09.06.2026 |  |  | Control valve is found actuator inner side sceling with 01 nos. spring damage | Proper Gear,Actuator,body,AFR unit Cleaning repairing damage spring replace with new. | 3000 | Internal | Anuj kr. / V singh
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | OFF Season | 14.06.2022 |  |  | Control valve found seat scaling and rusty. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. | 100 | Internal | A Varma / V singh
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | OFF Season | 24.06.2023 |  |  | Control valve is found seat scaling and rusty. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. | 100 | Internal | A Varma / V singh
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | OFF Season | 11.05.2024 |  |  | Control valve is found seat,body scaling rusty and spring ,repair kit,AFR positioner ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. | 150 | Internal | A Varma / V singh
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | OFF Season | 08.07.2025 |  |  | Control valve is found seat,body scaling rusty and spring ,repair kit,AFR positioner ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. | 200 | Internal | A Varma / V singh
5f800da90b4a | RJH-21-27 :: ZIL/SUG./015 ( 03.TCV.100.B01) | ZIL/SUG./015 ( 03.TCV.100.B01) | OFF Season | 10.06.2026 |  |  | Control valve is found actuator inner side sceling with light screch in actuator. | Proper Gear,Actuator,body,AFR unit Cleaning repairing damage spring replace with new. | 5000 | Internal | Anuj kr. / V singh
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | OFF Season | 13.06.2022 |  |  | Control valve found syrup scaling and rusty. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. |  | Internal | A Varma / V singh
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | OFF Season | 27.06.2023 |  |  | Control valve found syrup scaling and rusty. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. |  | Internal | A Varma / V singh
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | OFF Season | 07.05.2024 |  |  | Control valve found rusty. | Proper Gear,Actuator,Seat Body,positioner,AFR Unit cleaning repairing, Work Done. |  | Internal | A Varma / V singh
526ac52027dc | RJH-21-27 :: ZIL/SUG./018 ( 05LCV.060B01) | ZIL/SUG./018 ( 05LCV.060B01) | OFF Season | 10.07.2025 |  |  | Control valve found scaled and rusty. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. | 200 | Internal | A Varma / V singh
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | OFF Season | 29.08.2022 |  |  | Control valve found scaling with Alenkey bolt is damage | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. |  | Internal | A Varma / V singh
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | OFF Season | 27.06.2023 |  |  | Control valve found Dirty | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. | 150 | Internal | A Varma / V singh
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | OFF Season | 21.06.2024 |  |  | Control valve found Dirty | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. | 150 | Internal | A Varma / V singh
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | OFF Season | 11.07.2025 |  |  | Control valve found Dirty | Proper gear,actuator,seat body,positioner,AFR cleaning Overhauling work are done. | 200 | Internal | A Varma / V singh
1412c805983c | RJH-21-27 :: ZIL/SUG./019 | ZIL/SUG./019 | OFF Season | 17.06.2026 |  |  | Control valve found Dirty found air loc relay not working | Proper gear,actuator,seat body,positioner,AFR cleaning Overhauling work are done.air lock replaced with new | 4000 | Internal | Anuj kr. / V singh
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | OFF Season | 11.06.2022 |  |  | Control valve found syrup scaling and rusty. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. | 100 | Internal | A Varma / V singh
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | OFF Season | 03.08.2023 |  |  | Control valve found syrup scaling and rusty. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, seat checking with painting. | 100 | Internal | A Varma / V singh
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | OFF Season | 21.06.2024 |  |  | Control valve Condiction rusty.AFR,positioner OK | Proper Gear,Actuator,Seat Body,Positioner,AFR cleaning repairing, seat checking work done. | 100 | Internal | A Varma / V singh
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | OFF Season | 31.05.2025 |  |  | Control valve Condiction rusty.AFR,positioner OK | Proper Gear,Actuator,Seat Body,Positioner,AFR cleaning repairing, seat checking work done. | 100 | Internal | A Varma / V singh
4d4569238db2 | RJH-21-27 :: ZIL/SUG./001 ( 16.BCV.050.B01) | ZIL/SUG./001 ( 16.BCV.050.B01) | OFF Season | 29.05.2026 |  |  | Control valve found scaled and rusty.AFR & Positioner found ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, work are done. | 200 | Internal | Anuj Kr. / V singh | Seat on Patch with Water Droping
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | OFF Season | 04.07.2022 |  |  | Control valve found molasess sceling and rusty | Actuator,body,gear,positioner,valve seat checking,AFR cleaning repairing & painting work done. | 70 | Internal | A Varma / V singh
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | OFF Season | 24.05.2023 |  |  | Control valve found molasess sceling and rusty | Actuator,body,gear,positioner,valve seat checking,AFR cleaning repairing work done. | 70 | Internal | A Varma / V singh
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | OFF Season | 20.06.2024 |  |  | Control valve found molasess sceling and rusty,AFR,Positioner ok | Actuator,body,gear,positioner,valve seat checking,AFR cleaning repairing work done. | 80 | Internal | A Varma / V singh
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | OFF Season | 29.05.2025 |  |  | Control valve found syrup scaling and rusty. | Seat,Gear,actuator,body,positioner,valve seat checking,AFR cleaning Overhauling work done. | 250 | Internal | A Varma / V singh
e3a4cd203885 | B COUNTI.PAN 27-65 :: ZIL/SUG./021 (14.TCV.080.B01) | ZIL/SUG./021 (14.TCV.080.B01) | OFF Season | 14.05.2026 |  |  | Control valve found scaled and rusty.AFR & Positioner found ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, work are done. | 200 | Internal | Anuj Kr. / V singh
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | OFF Season | 04.07.2022 |  |  | Control valve found molasess sceling and rusty | Actuator,gear,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | OFF Season | 24.05.2023 |  |  | Control valve found molasess sceling and rusty | Actuator,gear,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | OFF Season | 20.06.2024 |  |  | Control valve found molasess sceling and rusty | Actuator,gear,body,positioner,valve seat checking,AFR cleaning repairing work done. | 90 | Internal | A Varma / V singh
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | OFF Season | 29.05.2025 |  |  | Control valve found syrup scaling and rusty.Actuator Spring damage | Seat,Gear,actuator,body,positioner,valve seat checking,AFR cleaning Overhauling work done.spring replaced with new. | 650 | Internal | A Varma / V singh
f01365191f1a | B COUNTI.PAN 27-65 :: ZIL/SUG./022 (14.TCV.100.B01) | ZIL/SUG./022 (14.TCV.100.B01) | OFF Season | 14.05.2026 |  |  | Control valve found scaled and rusty.AFR & Positioner found ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, work are done. | 200 | Internal | Anuj Kr. / V singh
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | OFF Season | 04.07.2022 |  |  | Control valve found molasess sceling and rusty | Actuator,gear,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | OFF Season | 25.05.2023 |  |  | Control valve found molasess sceling and rusty. | Actuator,gear,body,positioner,valve seat checking,AFR cleaning repairing work done. |  | Internal | A Varma / V singh
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | OFF Season | 21.06.2024 |  |  | Control valve found molasess sceling and rusty | Actuator,body,gear,positioner,valve seat checking,AFR cleaning repairing work done. | 90 | Internal | A Varma / V singh
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | OFF Season | 30.05.2025 |  |  | Control valve found syrup scaling and rusty. | Seat,Gear,actuator,body,positioner, valve seat checking,AFR cleaning Overhauling work done. | 250 | Internal | A Varma / V singh
d396dac8074f | B COUNTI.PAN 27-65 :: ZIL/SUG./023 (14.TCV.090.B01) | ZIL/SUG./023 (14.TCV.090.B01) | OFF Season | 14.05.2026 |  |  | Control valve found scaled and rusty.AFR & Positioner found ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, work are done. | 200 | Internal | Anuj Kr. / V singh
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | OFF Season | 04.07.2022 |  |  | Control valve found molasess sceling and rusty | Actuator,gear,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | OFF Season | 25.05.2023 |  |  | Control valve found molasess sceling and rusty | Actuator,gear,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | OFF Season | 21.06.2024 |  |  | Control valve found molasess sceling and rusty,AFR & positioner OK | Actuator,body,gear,positioner,valve seat checking,AFR cleaning repairing work done. | 90 | Internal | A Varma / V singh
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | OFF Season | 30.05.2025 |  |  | Control valve found syrup scaling and rusty. | Seat,Gear,actuator,body,positioner, valve seat checking,AFR cleaning Overhauling work done. | 250 | Internal | A Varma / V singh
63f546416713 | B COUNTI.PAN 27-65 :: ZIL/SUG./024 (14.TCV.070.B01) | ZIL/SUG./024 (14.TCV.070.B01) | OFF Season | 15.05.2026 |  |  | Control valve found scaled and rusty.AFR & Positioner found ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, work are done. | 200 | Internal | Anuj Kr. / V singh
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | OFF Season | 05.07.2022 |  |  | Control valve found syrup sceling and rusty | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | OFF Season | 05.08.2023 |  |  | Control valve Seat found worn-out & Valve Body rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | OFF Season | 19.05.2024 |  |  | Control valve found Seat & Valve Body rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done. | 100 | Internal | A Varma / V singh
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | OFF Season | 28.05.2025 |  |  | Control valve found Seat & Valve Body rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done. | 150 | Internal | A Varma / V singh
bc6efc435637 | B COUNTI.PAN 27-65 :: ZIL/SUG./(10.TCV.040.B01) | ZIL/SUG./(10.TCV.040.B01) | OFF Season | 28.05.2026 |  |  | Control valve found scaled and rusty.AFR & Positioner found ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, work are done. | 200 | Internal | Anuj Kr. / V singh | found seat worn-out-30%
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | OFF Season | 25.05.2022 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | OFF Season | 05.08.2023 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done. |  | Internal | A Varma / V singh
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | OFF Season | 08.06.2024 |  |  | Control valve found C light scaling and rusty.Actuator body worn-out | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing with actuator &neck bush O ring replace new work done. | 4450 | Internal | A Varma / V singh
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | OFF Season | 05.06.2025 |  |  | Control valve found C light scaling and rusty.Teflon O Ring replace | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing neck bush O ring replace new work done. | 350 | Internal | A Varma / V singh
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | OFF Season | 08.09.2025 |  |  | Brick transmitter with electrode replaced with new | Spare Sensor absulit in market | 81500 | External | A Varma / V singh
6fdc5841fc51 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-01 | ZIL/SUG./B.COMP-CT-01 | OFF Season | 22.04.2026 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | OFF Season | 25.05.2022 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | OFF Season | 05.08.2023 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done. |  | Internal | A Varma / V singh
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | OFF Season | 08.06.2024 |  |  | Control valve found C light scaling and rusty.Actuator body worn-out | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing with actuator &neck bush O ring replace new work done. | 4450 | Internal | A Varma / V singh
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | OFF Season | 05.06.2025 |  |  | Control valve found C light scaling and rusty.Teflon O Ring replace | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing neck bush O ring replace new work done. | 350 | Internal | A Varma / V singh
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | OFF Season | 08.09.2025 |  |  | Brick transmitter with electrode replaced with new | Spare Sensor absulit in market | 81500 | External | A Varma / V singh
3625f4d4442a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-02 | ZIL/SUG./B.COMP-CT-02 | OFF Season | 22.04.2026 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | OFF Season | 25.05.2022 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | OFF Season | 05.08.2023 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done. |  | Internal | A Varma / V singh
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | OFF Season | 07.06.2024 |  |  | Control valve found C light scaling and rusty.electrode teflon rod therad missing | Actuator,body,positioner,valve seat ,AFR cleaning,repairing teflon rod replace with new repairing & checking work done. | 1875 | Internal | A Varma / V singh
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | OFF Season | 05.06.2025 |  |  | Control valve found C light scaling and rusty.Teflon O Ring replace | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing neck bush O ring replace new work done. | 350 | Internal | A Varma / V singh
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | OFF Season | 10.09.2025 |  |  | Brick transmitter with electrode replaced with new | Spare Sensor absulit in market | 81500 | External | A Varma / V singh
12829ae4f18f | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-03 | ZIL/SUG./B.COMP-CT-03 | OFF Season | 22.04.2026 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | OFF Season | 25.05.2022 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | OFF Season | 05.08.2023 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done. |  | Internal | A Varma / V singh
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | OFF Season | 07.06.2024 |  |  | Control valve found C light scaling and rusty.Electrode o ring damage. | Actuator,body,positioner,valve seat ,AFR cleaning,repairing teflon O ring replace with new repairing & checking work done. | 180 | Internal | A Varma / V singh
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | OFF Season | 04.06.2025 |  |  | Control valve found C light scaling and rusty. Actuator air passing & Neck bush o ring damage | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing Actuator & neck bush O ring replace new work done. | 4550 | Internal | A Varma / V singh
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | OFF Season | 10.09.2025 |  |  | Brick transmitter with electrode replaced with new | Spare Sensor absulit in market | 81500 | External | A Varma / V singh
afad394ca1cb | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-04 | ZIL/SUG./B.COMP-CT-04 | OFF Season | 22.04.2026 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | OFF Season | 19.05.2022 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | OFF Season | 07.08.2023 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | OFF Season | 10.06.2024 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,SOV,valve seat checking,AFR cleaning repairing with checking work done. | 100 | Internal | A Varma / V singh
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | OFF Season | 05.06.2025 |  |  | Control valve found C light scaling and rustry,Seat passing with neck bush damage | Actuator,body,positioner,valve seat checking,AFR cleaning repairing seat & Neck bush replaced with new. | 450 | Internal | A Varma / V singh
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | OFF Season | 11.09.2025 |  |  | Brick transmitter with electrode replaced with new | Spare Sensor absulit in market | 81500 | External | A Varma / V singh
597294c3185a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-07 | ZIL/SUG./B.COMP-CT-07 | OFF Season | 23.04.2026 |  |  | Control valve found C light scaling and rusty.found valve seat worn-out | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done.Seat repalced with new | 500 | Internal | Anuj kr./ V singh
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | OFF Season | 19.05.2022 |  |  | Control valve found C light scaling and seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | OFF Season | 07.08.2023 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | OFF Season | 11.06.2024 |  |  | Control valve found scaling and rusty.Electrode cylinder seal kit damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode cylinder seal kit replaced with new | 685 | Internal | A Varma / V singh
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | OFF Season | 05.06.2025 |  |  | Control valve found C light scaling and rustry,Seat & neck bush ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are done. | 150 | Internal | A Varma / V singh
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | OFF Season | 12.09.2025 |  |  | Brick transmitter with electrode replaced with new | Spare Sensor absulit in market | 81500 | External | A Varma / V singh
907a80f96b95 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-08 | ZIL/SUG./B.COMP-CT-08 | OFF Season | 23.04.2026 |  |  | Control valve found C light scaling and rusty.found valve seat worn-out | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done.Seat repalced with new | 500 | Internal | Anuj kr./ V singh
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | OFF Season | 17.05.2022 |  |  | Control valve found C light scaling and seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | OFF Season | 07.08.2023 |  |  | Control valve found C light scaling and rusty.Electrode o-ring damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done.electrode o ring replaced with new |  | Internal | A Varma / V singh
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | OFF Season | 12.06.2024 |  |  | Control valve found scaling and rusty.Electrode cylinder seal kit damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode cylinder seal kit replaced with new | 685 | Internal | A Varma / V singh
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | OFF Season | 06.06.2025 |  |  | Control valve found C light scaling and rustry,Seat & neck bush ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are done. | 150 | Internal | A Varma / V singh
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | OFF Season | 12.09.2025 |  |  | Brick transmitter with electrode replaced with new | Spare Sensor absulit in market | 81500 | External | A Varma / V singh
99f0de160490 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-09 | ZIL/SUG./B.COMP-CT-09 | OFF Season | 23.04.2026 |  |  | Control valve found C light scaling and rusty.found valve seat worn-out | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done.Seat repalced with new | 500 | Internal | Anuj kr./ V singh
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | OFF Season | 17.05.2022 |  |  | Control valve found C light scaling and seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | OFF Season | 07.08.2023 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | OFF Season | 12.06.2024 |  |  | Control valve found scaling and rusty.Electrode neck bush damage | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode cylinder neck bush replaced with new | 180 | Internal | A Varma / V singh
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | OFF Season | 06.06.2025 |  |  | Control valve found C light scaling and rustry,Seal kit & neck bush oring damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are done.seal kit & o ring replaced with new | 750 | Internal | A Varma / V singh
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | OFF Season | 13.09.2025 |  |  | Brick transmitter with electrode replaced with new | Spare Sensor absulit in market | 81500 | External | A Varma / V singh
a65fa8877e60 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-10 | ZIL/SUG./B.COMP-CT-10 | OFF Season | 23.04.2026 |  |  | Control valve found C light scaling and rusty.found valve seat & Actuator worn-out | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done.Seat repalced with new | 4715 | Internal | Anuj kr./ V singh
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | OFF Season | 17.05.2022 |  |  | Control valve found C light scaling and seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | OFF Season | 07.08.2023 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | OFF Season | 12.06.2024 |  |  | Control valve found scaling and rusty.Electrode neck bush damage | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode cylinder neck bush replaced with new | 180 | Internal | A Varma / V singh
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | OFF Season | 06.06.2025 |  |  | Control valve found C light scaling and rustry,Seal kit & neck bush oring damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are done.seal kit & o ring replaced with new | 750 | Internal | A Varma / V singh
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | OFF Season | 13.09.2025 |  |  | Brick transmitter with electrode replaced with new | Spare Sensor absulit in market | 81500 | External | A Varma / V singh
b5bbabc2f896 | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-11 | ZIL/SUG./B.COMP-CT-11 | OFF Season | 22.04.2026 |  |  | electrode found C light scaling and rusty. | Electrode & SOV ,AFR cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | OFF Season | 17.05.2022 |  |  | Control valve found B havy scaling and seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | OFF Season | 08.06.2023 |  |  | Control valve found B havy scaling & rusty.Electrode o-ring damage with actuator problem | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done.electrode o ring replaced with new |  | Internal | A Varma / V singh
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | OFF Season | 31.05.2024 |  |  | Control valve found B havy scaling & rusty.Electrode o-ring damage with actuator air liekage problem,SOV,positioner & AFR Ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & checking work done.electrode o ring & actuator o ring replaced with new | 370 | Internal | A Varma / V singh
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | OFF Season | 07.06.2025 |  |  | Control valve found C light scaling and rustry,Seat & neck bush ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are done. | 250 | Internal | A Varma / V singh
8e3e8411ce0e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-01 | ZIL/SUG./C.COMP-CT-01 | OFF Season | 24.04.2026 |  |  | Control valve & electrode found C light scaling and rusty. | Actuator ,Seat ,Electrode & SOV ,AFR cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | OFF Season | 18.05.2022 |  |  | Control valve found B havy scaling and seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | OFF Season | 08.06.2023 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring,seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done.electrode o ring,seat replaced with new |  | Internal | A Varma / V singh
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | OFF Season | 31.05.2024 |  |  | Control valve found B havy scaling and rusty.Electrode rod,seat damage,SOV,Positioner,AFR ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode cylinder neck bush replaced with new | 1900 | Internal | A Varma / V singh
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | OFF Season | 07.06.2025 |  |  | Control valve found C light scaling and rustry,Seal kit & neck bush oring damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are done.seal kit & o ring replaced with new | 750 | Internal | A Varma / V singh
a45a075bfead | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-02 | ZIL/SUG./C.COMP-CT-02 | OFF Season | 24.04.2026 |  |  | Control valve found C light scaling and rusty.found valve seat & Actuator worn-out | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done.Seat repalced with new | 4715 | Internal | Anuj kr./ V singh
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | OFF Season | 18.05.2022 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done.electrode o ring replaced with new |  | Internal | A Varma / V singh
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | OFF Season | 10.08.2023 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring,seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done.electrode o ring,seat replaced with new |  | Internal | A Varma / V singh
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | OFF Season | 04.05.2024 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring damage,SOV ,Positioner & AFR ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & checking work done.electrode o ring replaced with new | 170 | Internal | A Varma / V singh
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | OFF Season | 07.06.2025 |  |  | Control valve found C light scaling and rustry,Cylinder air passing with neck bush damage | Actuator,body,positioner,valve seat checking,AFR cleaning repairing seat & Neck bush replaced with new. | 450 | Internal | A Varma / V singh
00e3316dc6ca | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-03 | ZIL/SUG./C.COMP-CT-03 | OFF Season | 24.04.2026 |  |  | Control valve & electrode found C light scaling and rusty. | Actuator ,Seat ,Electrode & SOV ,AFR cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | OFF Season | 19.05.2022 |  |  | Control valve found B havy scaling and seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | OFF Season | 10.08.2023 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode o ring replaced with new |  | Internal | A Varma / V singh
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | OFF Season | 04.05.2024 |  |  | Control valve found B havy scaling and rusty,water spray nozal missing.Electrode cylinder liekage ,SOV ,Positioner & AFR ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode cylinder seal kit replaced with new | 1050 | Internal | A Varma / V singh
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | OFF Season | 07.06.2025 |  |  | Control valve found C light scaling and rustry, bush damage | Actuator,body,positioner,valve seat checking,AFR cleaning repairing seat & Neck bush replaced with new. | 250 | Internal | A Varma / V singh
97da6dceec8e | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-04 | ZIL/SUG./C.COMP-CT-04 | OFF Season | 25.04.2026 |  |  | Control valve found C light scaling and rusty.found valve seat & Actuator worn-out | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done.Seat repalced with new | 4715 | Internal | Anuj kr./ V singh
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | OFF Season | 19.05.2022 |  |  | Control valve found B havy scaling and seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | OFF Season | 10.08.2023 |  |  | Control valve found B havy scaling and seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | OFF Season | 06.05.2024 |  |  | Control valve found B havy scaling and rusty.Electrode cylinder liekage ,nek bus O ring damage, SOV ,Positioner & AFR ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing checking work done.electrode cylinder seal kit ,neck bush O ring replaced with new | 850 | Internal | A Varma / V singh
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | OFF Season | 07.06.2025 |  |  | Control valve found C light scaling and rustry,Seat & neck bush ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are done. | 250 | Internal | A Varma / V singh
b5ab141c8d2d | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-05 | ZIL/SUG./C.COMP-CT-05 | OFF Season | 24.04.2026 |  |  | Control valve & electrode found C light scaling and rusty. | Actuator ,Seat ,Electrode & SOV ,AFR cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | OFF Season | 19.05.2022 |  |  | Control valve seat found B havy scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | OFF Season | 10.08.2023 |  |  | Control valve seat found B havy scaling and rusty.Electrode o-ring,actuator guide damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done.electrode o ring ,actuator guide replaced with new |  | Internal | A Varma / V singh
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | OFF Season | 06.05.2024 |  |  | Control valve seat found B havy scaling and rusty.Electrode o-ring,actuator worn-out,SOV,AFR & Positioner Ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & checking work done.electrode o ring ,actuator replaced with new | 4750 | Internal | A Varma / V singh
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | OFF Season | 07.06.2025 |  |  | Control valve found C light scaling and rustry,Seat & neck bush ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are done. | 250 | Internal | A Varma / V singh
26bcd605138c | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-06 | ZIL/SUG./C.COMP-CT-06 | OFF Season | 25.04.2026 |  |  | Control valve found C light scaling and rusty.found valve seat & Actuator worn-out | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done.Seat repalced with new | 4715 | Internal | Anuj kr./ V singh
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | OFF Season | 20.05.2022 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done.electrode o ring replaced with new |  | Internal | A Varma / V singh
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | OFF Season | 20.05.2023 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing checking work done.electrode o ring replaced with new |  | Internal | A Varma / V singh
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | OFF Season | 06.05.2024 |  |  | Control valve found B havy scaling and rusty.water spray nazzal missing,Electrode o-ring damage.SOV,AFR & Positioner OK | Actuator,body,positioner,valve seat checking,AFR cleaning repairing checking work done.electrode o ring,water spray nazzal replaced with new | 410 | Internal | A Varma / V singh
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | Season | 07.11.2024 |  |  | Sov Problem | Replace with new | 1250 | Internal | A Varma / V singh
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | OFF Season | 08.06.2025 |  |  | Control valve found C light scaling and rustry,Seat & neck bush ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are done. | 150 | Internal | A Varma / V singh
9a5aa2c1b3db | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-07 | ZIL/SUG./C.COMP-CT-07 | OFF Season | 27.04.2026 |  |  | Control valve & electrode found C light scaling and rusty. | Actuator ,Seat ,Electrode & SOV ,AFR cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | OFF Season | 20.05.2022 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done.electrode o ring replaced with new |  | Internal | A Varma / V singh
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | OFF Season | 12.08.2023 |  |  | Control valve found B havy scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | OFF Season | 07.05.2024 |  |  | Control valve found B havy scaling and rusty.electrode cylinder seal kit liekage damage.SOV,AFR & Positioner OK | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. | 650 | Internal | A Varma / V singh
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | OFF Season | 08.06.2025 |  |  | Control valve found C light scaling and rustry,cylinder seal kit & neck bush ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are done. | 950 | Internal | A Varma / V singh
67fb92945881 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-08 | ZIL/SUG./C.COMP-CT-08 | OFF Season | 27.04.2026 |  |  | Control valve & electrode found C light scaling and valve seat worn-out. | Actuator ,Seat ,Electrode & SOV ,AFR cleaning repairing seat replaced with new work done. | 1000 | Internal | Anuj kr./ V singh
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | OFF Season | 20.05.2022 |  |  | Control valve found B havy scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | OFF Season | 12.08.2023 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring,seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done.electrode o ring,seat replaced with new |  | Internal | A Varma / V singh
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | OFF Season | 08.05.2024 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring,seat damage.SOV,AFR Positioner OK | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode o ring,seat replaced with new | 480 | Internal | A Varma / V singh
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | OFF Season | 08.06.2025 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring,actuator worn-out,Spray Pipe mishing.SOV,AFR,Positioner OK | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode o ring,Actuator with water spray replaced new | 4850 | Internal | A Varma / V singh
905ecbe97331 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-09 | ZIL/SUG./C.COMP-CT-09 | OFF Season | 27.04.2026 |  |  | Control valve & electrode found C light scaling and valve seat worn-out. | Actuator ,Seat ,Electrode & SOV ,AFR cleaning repairing seat replaced with new work done. | 1000 | Internal | Anuj kr./ V singh
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | OFF Season | 21.05.2022 |  |  | Control valve found B havy scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | OFF Season | 12.08.2023 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring,seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done.electrode o ring,seat replaced with new |  | Internal | A Varma / V singh
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | OFF Season | 08.05.2024 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring,actuator worn-out,Spray Pipe mishing.SOV,AFR,Positioner OK | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode o ring,Actuator with water spray replaced new | 4850 | Internal | A Varma / V singh
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | OFF Season | 08.06.2025 |  |  | Control valve found C light scaling and rustry,Seat & neck bush ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are done. | 250 | Internal | A Varma / V singh
e2401b8b1e50 | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-10 | ZIL/SUG./C.COMP-CT-10 | OFF Season | 27.04.2026 |  |  | Control valve & electrode found C light scaling and rusty. | Actuator ,Seat ,Electrode & SOV ,AFR cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | OFF Season | 21.05.2022 |  |  | Control valve found B havy scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & seat replaced with new. |  | Internal | A Varma / V singh
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | OFF Season | 12.08.2023 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring,seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done.electrode o ring,seat replaced with new |  | Internal | A Varma / V singh
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | OFF Season | 08.05.2024 |  |  | Control valve found B havy scaling and rusty.Electrode o-ring,actuator worn-out,Spray Pipe mishing.SOV,AFR,Positioner OK | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode o ring,Actuator with water spray replaced new | 4850 | Internal | A Varma / V singh
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | OFF Season | 08.06.2025 |  |  | Control valve found C light scaling and rustry,Seat & neck bush ok | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are done. | 250 | Internal | A Varma / V singh
748006fed2de | B COUNTI.PAN 27-65 :: ZIL/SUG./C.COMP-CT-11 | ZIL/SUG./C.COMP-CT-11 | OFF Season | 27.04.2026 |  |  | Control valve & electrode found C light scaling and rusty. | Actuator ,Seat ,Electrode & SOV ,AFR cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | OFF Season | 16.06.2022 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR, & positioner cleaning overhauling & painting work done. |  | Internal | A Varma / V singh
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | OFF Season | 04.07.2023 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR, & positioner cleaning overhauling & painting work done. |  | Internal | A Varma / V singh
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | OFF Season | 11.05.2024 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR, & positioner cleaning overhauling & painting work done. | 200 | Internal | A Varma / V singh
eab4335e0100 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./075 (45XU009) | ZIL/SUG./075 (45XU009) | OFF Season | 09.06.2025 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR, & positioner cleaning overhauling with checking & painting work done. | 350 | Internal | A Varma / V singh
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | OFF Season | 16.06.2022 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR, & positioner cleaning overhauling & painting work done. |  | Internal | A Varma / V singh
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | OFF Season | 04.07.2023 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR, & positioner cleaning overhauling & painting work done. |  | Internal | A Varma / V singh
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | OFF Season | 10.05.2024 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR, & positioner cleaning overhauling & painting work done. | 180 | Internal | A Varma / V singh
662074755756 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./076(13.TCV.005) | ZIL/SUG./076(13.TCV.005) | OFF Season | 09.06.2025 |  |  | Control valve found scaled and rusty.seat passing | Seat,Gear,AFR, & positioner cleaning overhauling & seat replaced with new work done. | 3100 | Internal | A Varma / V singh
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | OFF Season | 17.06.2022 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR, & positioner cleaning overhauling & painting work done. |  | Internal | A Varma / V singh
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | OFF Season | 05.07.2023 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR, & positioner cleaning overhauling & painting work done. |  | Internal | A Varma / V singh
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | OFF Season | 10.05.2024 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR, & positioner cleaning overhauling & painting work done. | 150 | Internal | A Varma / V singh
b23732fe727e | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./077 (15.FCV.027) | ZIL/SUG./077 (15.FCV.027) | OFF Season | 09.06.2025 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR, & positioner cleaning overhauling & painting work done. | 200 | Internal | A Varma / V singh
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | OFF Season | 2022 |  |  | Control valve found scaled and rusty. | Seat,Plug,Gear,AFR,& positioner cleaning overhauling work done. |  | Internal | A Varma / V singh
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | OFF Season | 05.07.2023 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR,& positioner cleaning overhauling work done. |  | Internal | A Varma / V singh
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | OFF Season | 10.05.2024 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR,& positioner cleaning overhauling work done. | 150 | Internal | A Varma / V singh
954e4d4e8c73 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./078 (45.XV.009) | ZIL/SUG./078 (45.XV.009) | OFF Season | 09.06.2025 |  |  | Control valve found scaled and rusty. | Seat,Gear,AFR,& positioner cleaning overhauling work done. | 150 | Internal | A Varma / V singh
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | OFF Season | 17.06.2022 |  |  | Control valve found scaled and rusty. | Proper cleaning repairing & painting work done. |  | Internal | A Varma / V singh
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | OFF Season | 05.08.2023 |  |  | Control valve found scaled and rusty. | Seat,Plug,Gear,AFR, cleaning overhauling & painting work done. |  | Internal | A Varma / V singh
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | OFF Season | 24.06.2024 |  |  | Control valve found scaled and rusty.AFR,Positioner OK | Seat,Plug,Gear,AFR, cleaning overhauling & painting work done. | 180 | Internal | A Varma / V singh
0418af8673f5 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./079(14.BCV.210.B01) | ZIL/SUG./079(14.BCV.210.B01) | OFF Season | 09.06.2025 |  |  | Control valve found scaled and rusty. | Proper cleaning repairing & painting work done. | 150 | Internal | A Varma / V singh
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | OFF Season | 20.06.2022 |  |  | Control valve found scaled and rusty.AFR Positioner OK | Proper gear,actuator,seat body, AFR unit,Cleaning overhauling & checking work done. |  | Internal | A Varma / V singh
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | OFF Season | 07.08.2023 |  |  | Control valve found scaled and rusty.Seat AFR ,Positioner OK | Proper gear,actuator,seat body, AFR unit,Cleaning overhauling & checking work done. |  | Internal | A Varma / V singh
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | OFF Season | 22.06.2024 |  |  | Control valve found scaled and rusty.Seat 20% worn-out AFR,Positioner OK | Proper gear,actuator,seat body, AFR unit,Cleaning overhauling & checking work done. | 180 | Internal | A Varma / V singh
bd3879df9894 | RAW HOUSE GROUND FLOOR 6 :: ZIL/SUG./080 (22.TCV.205.B01) | ZIL/SUG./080 (22.TCV.205.B01) | OFF Season | 19.06.2025 |  |  | Control valve found scaled and rusty.Seat 35% worn-out AFR,Positioner OK | Proper gear,actuator,seat body, AFR unit,Cleaning overhauling & checking work done. | 200 | Internal | A Varma / V singh
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | OFF Season | 21.05.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | OFF Season | 08.06.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | OFF Season | 16.06.2024 |  |  | Control valve Condiction syrup scaling and rusty.AFR,Positioner Ok | Proper Gear,actuator,body,plug,positioner,valve seat checking,AFR Unit cleaning with Overhauling work done. | 150 | Internal | A Varma / V singh
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | OFF Season | 26.05.2025 |  |  | Control valve found syrup scaling and rusty. | Seat,Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning Overhauling work done. | 250 | Internal | A Varma / V singh
bb167ab80e83 | RAW FEED VALVE-33 :: ZIL/SUG./026 (11.BCV.010.B01) | ZIL/SUG./026 (11.BCV.010.B01) | OFF Season | 14.05.2026 |  |  | Control valve found scaled and rusty.AFR & Positioner found ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, work are done. | 200 | Internal | Anuj Kr. / V singh
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | OFF Season | 21.05.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | OFF Season | 08.06.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | OFF Season | 16.06.2024 |  |  | Control valve Condiction syrup scaling and rusty. | Seat,Gear,actuator,body,plug,positioner,valve seat checking,AFR unit cleaning overhauling work done. | 150 | Internal | A Varma / V singh
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | OFF Season | 27.05.2025 |  |  | Control valve found syrup scaling and rusty. | Seat,Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning Overhauling work done. | 250 | Internal | A Varma / V singh
252f350bd646 | RAW FEED VALVE-33 :: ZIL/SUG./027 (11.BCV.020.B01) | ZIL/SUG./027 (11.BCV.020.B01) | OFF Season | 14.05.2026 |  |  | Control valve found scaled and rusty.AFR & Positioner found ok valve scale damage. | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, work are done.scale replace it | 350 | Internal | Anuj Kr. / V singh
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | OFF Season | 21.05.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | OFF Season | 09.06.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | OFF Season | 17.06.2024 |  |  | Control valve Condiction syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & Overhauling work done. | 150 | Internal | A Varma / V singh
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | Season | 17.03.2025 |  |  | Brix Tx display problem | Repair to third party |  | External | Sushil / V singh
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | OFF Season | 27.05.2025 |  |  | Control valve found syrup scaling and rusty. | Seat,Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning Overhauling work done. | 250 | Internal | A Varma / V singh
d55667635172 | RAW FEED VALVE-33 :: ZIL/SUG./028 (11.BCV.030.B01) | ZIL/SUG./028 (11.BCV.030.B01) | OFF Season | 15.05.2026 |  |  | Control valve found scaled and rusty.AFR & Positioner found ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, work are done. | 250 | Internal | Anuj Kr. / V singh
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | OFF Season | 23.05.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | OFF Season | 09.06.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | OFF Season | 18.06.2024 |  |  | Control valve Condiction syrup scaling and rusty. | Seat,Gear,actuator,body,plug,positioner, valve seat checking,AFR Unit cleaning Overhauling work done. | 150 | Internal | A Varma / V singh
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | Season | 18.11.2024 |  |  | Rotary valve handale damage | Replaced with new | 850 | Internal | A Varma / V singh
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | OFF Season | 27.05.2025 |  |  | Control valve found syrup scaling and rusty. | Seat,Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning Overhauling work done. | 250 | Internal | A Varma / V singh
979d9199700e | RAW FEED VALVE-33 :: ZIL/SUG./029 (17.BCV.020.B01) | ZIL/SUG./029 (17.BCV.020.B01) | OFF Season | 15.05.2026 |  |  | Control valve found scaled and rusty.AFR & Positioner found ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, work are done. | 250 | Internal | Anuj Kr. / V singh
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | OFF Season | 23.05.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | OFF Season | 09.06.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | OFF Season | 18.06.2024 |  |  | Control valve found syrup scaling and rusty. | Seat,Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning Overhauling work done. | 150 | Internal | A Varma / V singh
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | OFF Season | 28.05.2025 |  |  | Control valve found syrup scaling and rusty. | Seat,Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning Overhauling work done. | 250 | Internal | A Varma / V singh
ce0886fd193a | RAW FEED VALVE-33 :: ZIL/SUG./030 (11.BCV.050.B01) | ZIL/SUG./030 (11.BCV.050.B01) | OFF Season | 15.05.2026 |  |  | Control valve found scaled and rusty.AFR & Positioner found ok | Proper gear,actuator,seat body,positioner,AFR cleaning repairing, work are done. | 250 | Internal | Anuj Kr. / V singh
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | OFF Season | 24.06.2022 |  |  | Control valve found meltar scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | OFF Season | 10.07.2023 |  |  | Control valve found meltar scaling and rusty, throtal bearing damage. | Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | OFF Season | 24.06.2024 |  |  | Control valve Condiction scaling and rusty, thirst bearing damage. | Gear,actuator,body,plug,positioner,valve seat checking,AFR Unit cleaning overhauling work done.Bearing use aold Spare. | 450 | Internal | A Varma / V singh
8847db57d6c4 | RAW FEED VALVE-33 :: ZIL/SUG./031 (14.TCV.210.B01) | ZIL/SUG./031 (14.TCV.210.B01) | OFF Season | 19.06.2025 |  |  | Control valve Condiction scaling and rusty. | Gear,actuator,body,plug,positioner,valve seat checking,AFR Unit cleaning overhauling work done. | 250 | Internal | A Varma / V singh
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | OFF Season | 24.06.2022 |  |  | Control valve found water scaling and rusty. | Actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | OFF Season | 11.07.2023 |  |  | Control valve found water scaling and rusty. | Actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | OFF Season | 24.06.2024 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. | 160 | Internal | A Varma / V singh
6bd63805c851 | RAW FEED VALVE-33 :: ZIL/SUG./032 /BCV_TCV_601 | ZIL/SUG./032 /BCV_TCV_601 | OFF Season | 11.06.2025 |  |  | Control valve found water scaling and rusty. | Actuator,body,plug,valve seat checking,AFR cleaning repairing & painting work done. | 200 | Internal | A Varma / V singh
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | OFF Season | 24.06.2022 |  |  | Control valve found water scaling and rusty. | Actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | OFF Season | 11.07.2023 |  |  | Control valve found water scaling and rusty. | Actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | OFF Season | 24.06.2024 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Actuator,body,plug,positioner,valve seat checking,AFR cleaning repairing & painting work done. | 150 | Internal | A Varma / V singh
c4a15ad7ef55 | RAW FEED VALVE-33 :: ZIL/SUG./033/BCV_PCV_601 | ZIL/SUG./033/BCV_PCV_601 | OFF Season | 11.06.2025 |  |  | Control valve found water scaling and rusty. | Actuator,body,plug,valve seat checking,AFR cleaning repairing & painting work done. | 200 | Internal | A Varma / V singh
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | OFF Season | 04.07.2022 |  |  | Power cylinder found massecuite scaling and rusty,seal kit damage | Seat,SOV,positioner,rotary disc valve cleaning & lubrication with painting work seal kit replaced with new. |  | Internal | A Varma / V singh
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | OFF Season | 04.08.2023 |  |  | Power cylinder found massecuite scaling and rusty seal kit damage. | Seat,SOV,positioner,rotary disc valve cleaning & lubrication with painting work seal kit replaced with new |  | Internal | A Varma / V singh
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | OFF Season | 26.06.2024 |  |  | Power Cylinder found masscuite scaling ,AFR & SOV OK | Seat,SOV,positioner,rotary disc valve cleaning & overhauling lubrication with checking work done. | 250 | Internal | A Varma / V singh
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | OFF Season | 02.06.2025 |  |  | Power Cylinder found masscuite scaling ,AFR & SOV OK cylinder seal kit leakage. | Seat,SOV,rotary disc valve cleaning & overhauling lubrication with checking work done. Replaced new | 4500 | Internal | A Varma / V singh
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | Season | 27.11.2025 |  |  | Cylinder Disk Rotary Valve Leakage | Replaced with new take in line | 600 | Internal | Anuj Kumar
a6ccee96c381 | RAW FEED VALVE-33 :: ZIL/SUG./034 (12.LCV.070.B01) | ZIL/SUG./034 (12.LCV.070.B01) | OFF Season | 02.06.2026 |  |  | Power Cylinder found masscuite scaling ,AFR & SOV OK cylinder seal kit leakage. | Seat,SOV,rotary disc valve cleaning & overhauling lubrication with checking work done. Replaced new | 5100 | Internal | Anuj Kr. / V singh
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | OFF Season | 04.07.2022 |  |  | Power cylinder found massecuite scaling and rusty | Seat,SOV,positioner,rotary disc valve cleaning & lubrication with painting work |  | Internal | A Varma / V singh
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | OFF Season | 05.08.2023 |  |  | Power cylinder found massecuite scaling and rusty. | Seat,SOV,positioner,rotary disc valve cleaning & lubrication with painting work |  | Internal | A Varma / V singh
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | OFF Season | 27.06.2024 |  |  | Power Cylinder found masscuite scaling ,AFR & SOV OK | Seat,SOV,positioner,rotary disc valve cleaning & overhauling lubrication with checking work done. | 250 | Internal | A Varma / V singh
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | OFF Season | 02.06.2025 |  |  | Power Cylinder found masscuite scaling ,AFR & SOV OK | Seat,SOV,rotary disc valve cleaning & overhauling lubrication with checking work done. | 4500 | Internal | A Varma / V singh
2a97d275d4c2 | RAW FEED VALVE-33 :: ZIL/SUG./035 (12.LCV.080.B01) | ZIL/SUG./035 (12.LCV.080.B01) | OFF Season | 03.06.2026 |  |  | Power Cylinder found masscuite scaling ,AFR & SOV OK | Seat,SOV,rotary disc valve cleaning & overhauling lubrication with checking work done. | 400 | Internal | Anuj Kr. / V singh
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | OFF Season | 05.07.2022 |  |  | Power cylinder found massecuite scaling and rusty | Seat,SOV,positioner,rotary disc valve cleaning & lubrication with painting work |  | Internal | A Varma / V singh
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | OFF Season | 05.08.2023 |  |  | Power cylinder found massecuite scaling and rusty | Seat,SOV,positioner,rotary disc valve cleaning & lubrication with painting work |  | Internal | A Varma / V singh
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | OFF Season | 28.06.2024 |  |  | Power Cylinder found masscuite scaling ,AFR & SOV OK | Seat,SOV,positioner,rotary disc valve cleaning & overhauling lubrication with checking work done. | 250 | Internal | A Varma / V singh
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | OFF Season | 03.06.2025 |  |  | Power Cylinder found masscuite scaling ,AFR & SOV OK | Seat,SOV,rotary disc valve cleaning & overhauling lubrication with checking work done. | 4500 | Internal | A Varma / V singh
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | Season | 27.11.2025 |  |  | Cylinder Rotary Valve Liekage | Replaced with new take in line | 600 | Internal | Anuj Kumar
a86f0652b773 | RAW FEED VALVE-33 :: ZIL/SUG./036 (12.LCV.090.B01) | ZIL/SUG./036 (12.LCV.090.B01) | OFF Season | 04.06.2026 |  |  | Power Cylinder found masscuite scaling ,AFR & SOV OK cylinder seal kit leakage. | Seat,SOV,rotary disc valve cleaning & overhauling lubrication with checking work done. Replaced new | 5100 | Internal | Anuj Kr. / V singh
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | OFF Season | 08.05.2022 |  |  | valve found scaled and rusty. | Proper cleaning & lubrication work done. |  |  | -
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | OFF Season | 01.07.2023 |  |  | valve found scaled and rusty.Potential meter out of order | Proper cleaning & lubrication work done potential meter replaced as Old spare | 150 | Internal | Anil Yadav
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | OFF Season | 01.07.2024 |  |  | valve found scaled and rusty | Proper cleaning & lubrication work done. | 200 | Internal | Anil Yadav
a6fcdab27935 | RAW FEED VALVE-33 :: ZIL/SUG./037 (16.MO.30) | ZIL/SUG./037 (16.MO.30) | OFF Season | 10.06.20225 |  |  | valve found scaled and rusty. | Proper cleaning & lubrication work done. | 1000 | Internal | Anil Yadav
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | OFF Season | 09.05.2022 |  |  | valve found scaled and rusty. | Proper cleaning & lubrication work done. |  |  | -
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | OFF Season | 03.07.2023 |  |  | valve found scaled and rusty. | Proper cleaning & lubrication work done. |  | Internal | Anil Yadav
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | OFF Season | 01.08.2024 |  |  | valve found scaled and rusty. | Proper cleaning & lubrication work done. |  | Internal | Anil Yadav
be91ac565e45 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.40) | ZIL/SUG./038 (16.MO.40) | OFF Season | 10.06.2025 |  |  | valve found scaled and rusty. | Proper cleaning & lubrication with checking work are done. | 200 | Internal | Anil Yadav
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | OFF Season | 09.05.2022 |  |  | valve found scaled and rusty. | Proper cleaning & lubrication work done. |  |  | -
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | OFF Season | 03.07.2023 |  |  | valve found scaled and rusty. | Proper cleaning & lubrication work done. |  |  | -
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | OFF Season | 02.08.2024 |  |  | valve found scaled and rusty. | Proper cleaning & lubrication work done. | 150 | Internal | Anil Yadav
dcf4ecd6d4e3 | RAW FEED VALVE-33 :: ZIL/SUG./038 (16.MO.30) | ZIL/SUG./038 (16.MO.30) | OFF Season | 11.06.2025 |  |  | valve found scaled and rusty. | Proper cleaning & lubrication with checking work are done. | 200 | Internal | Anil Yadav
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | OFF Season | 08.06.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | OFF Season | 02.08.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | OFF Season | 19.06.2024 |  |  | Control valve Condiction syrup scaling,AFR ,Positioner OK | Gear,Actuator,Seat Body,plug,Positioner, AFR Unit cleaning Repairing, seat checking work done. | 180 | Internal | A Varma / V singh
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | OFF Season | 30.05.2025 |  |  | Control valve Condiction syrup scaling,AFR ,Positioner OK | Gear,Actuator,Seat Body,plug,Positioner, AFR Unit cleaning Repairing, seat checking work done. | 180 | Internal | A Varma / V singh
972075a393f6 | RAW QUAD 47 :: ZIL/SUG./039 (15.LCV.030.B01) | ZIL/SUG./039 (15.LCV.030.B01) | OFF Season | 30.05.2026 |  |  | Control valve Condiction syrup scaling,AFR ,Positioner OK | Gear,Actuator,Seat Body,plug,Positioner, AFR Unit cleaning Repairing, seat checking work done. | 200 | Internal | Anuj kr. / V singh
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | OFF Season | 08.06.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | OFF Season | 02.08.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | OFF Season | 20.06.2024 |  |  | Control valve Condiction rusty.AFR,Positioner Ok | Proper gear, actuator,seat ,gland checking,body,plug,postioner & AFR unit cleaning repairing wrk done. | 180 | Internal | A Varma / V singh
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | OFF Season | 29.05.2025 |  |  | Control valve Condiction rusty.AFR,Positioner Ok | Proper gear, actuator,seat ,gland checking,body,plug,postioner & AFR unit cleaning repairing wrk done. | 180 | Internal | A Varma / V singh
5c691766a74b | RAW QUAD 47 :: ZIL/SUG./040 ( 16.LCV.040.B01) | ZIL/SUG./040 ( 16.LCV.040.B01) | OFF Season | 01.06.2026 |  |  | Control valve Condiction syrup scaling,AFR ,Positioner OK | Gear,Actuator,Seat Body,plug,Positioner, AFR Unit cleaning Repairing, seat checking work done. | 200 | Internal | Anuj kr. / V singh
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | OFF Season | 09.06.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | OFF Season | 02.08.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | OFF Season | 21.06.2024 |  |  | Control valve Condiction syrup scaling and rusty.AFR,Positioner OK | Proper gear,actuator,seat body,plug AFR unit,Cleaning overhauling work done. | 180 | Internal | A Varma / V singh
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | OFF Season | 29.05.2025 |  |  | Control valve Condiction rusty.AFR,Positioner Ok | Proper gear, actuator,seat ,gland checking,body,plug,postioner & AFR unit cleaning repairing wrk done. | 180 | Internal | A Varma / V singh
0991d898c1fe | RAW QUAD 47 :: ZIL/SUG./041 (16.LCV.050.B01) | ZIL/SUG./041 (16.LCV.050.B01) | OFF Season | 01.06.2026 |  |  | Control valve Condiction syrup scaling,AFR ,Positioner OK | Gear,Actuator,Seat Body,plug,Positioner, AFR Unit cleaning Repairing, seat checking work done. | 200 | Internal | Anuj kr. / V singh
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | OFF Season | 09.06.2022 |  |  | Control valve found lime scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | OFF Season | 01.08.2023 |  |  | Control valve found lime scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | OFF Season | 22.07.2024 |  |  | Control valve found lime scaling and rusty.Actuator Spring 01 nos found damage.I/P,AFR & Positioner Ok | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, seat checking with valve painting work done ,actuator spring replaced with old spare | 1800 | Internal | A Varma / V singh
5ce37176f8c1 | RAW QUAD 47 :: ZIL/SUG./042 (03.FCV.120.B01) | ZIL/SUG./042 (03.FCV.120.B01) | OFF Season | 07.07.2025 |  |  | Control valve found lime scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, seat checking with valve painting work done. | 350 | Internal | A Varma / V singh
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | OFF Season | 10.06.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | OFF Season | 19.07.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | OFF Season | 07.07.2024 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, seat checking & valve painting work done. | 250 | Internal | A Varma / V singh
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | OFF Season | 15.10.2024 |  |  | Found Valve Seat jamming | Valve Seat replaced with new | 8759 | Internal | A Varma / V singh
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | OFF Season | 30.06.2025 |  |  | Control valve Condiction rusty.AFR,Positioner Ok | Proper gear, actuator,seat ,gland checking,body,plug,postioner & AFR unit cleaning repairing wrk done. | 180 | Internal | A Varma / V singh
c390ef7b0c6c | RAW QUAD 47 :: ZIL/SUG./044 (07.BCV.070.B01) | ZIL/SUG./044 (07.BCV.070.B01) | OFF Season | 27.06.2026 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, seat checking with valve painting work done , | 500 | Internal | Anuj Kr./ V singh
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | OFF Season | 11.06.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | OFF Season | 20.07.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | OFF Season | 08.07.2024 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. | 250 | Internal | A Varma / V singh
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | OFF Season | 01.07.2025 |  |  | Control valve Condiction rusty.AFR,Positioner Ok | Proper gear, actuator,seat ,gland checking,body,plug,postioner & AFR unit cleaning repairing wrk done. | 180 | Internal | A Varma / V singh
cbeaae6311d0 | RAW QUAD 47 :: ZIL/SUG./045 (07.LCV.080.B01) | ZIL/SUG./045 (07.LCV.080.B01) | OFF Season | 02.07.2026 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, seat checking with valve painting work done , | 500 | Internal | Anuj Kr./ V singh
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | OFF Season | 12.06.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | OFF Season | 21.07.2023 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | OFF Season | 09.07.2024 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. | 250 | Internal | A Varma / V singh
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | OFF Season | 01.07.2025 |  |  | Control valve Condiction rusty.AFR,Positioner Ok | Proper gear, actuator,seat ,gland checking,body,plug,postioner & AFR unit cleaning repairing wrk done. | 180 | Internal | A Varma / V singh
8080e0713182 | RAW QUAD 47 :: ZIL/SUG./046 (07.BCV.080.B01) | ZIL/SUG./046 (07.BCV.080.B01) | OFF Season | 29.06.2026 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, seat checking with valve painting work done , | 500 | Internal | Anuj Kr./ V singh
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | OFF Season | 12.06.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | OFF Season | 21.07.2023 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | OFF Season | 09.07.2024 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. | 250 | Internal | A Varma / V singh
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | OFF Season | 30.06.2025 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper gear, actuator,seat ,gland checking,body,plug,postioner & AFR unit cleaning repairing wrk done. | 180 | Internal | A Varma / V singh
fc898c1d8e7e | RAW QUAD 47 :: ZIL/SUG./046 (07.LCV.070B01) | ZIL/SUG./046 (07.LCV.070B01) | OFF Season | 29.06.2026 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, seat checking with valve painting work done , | 500 | Internal | Anuj Kr./ V singh
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | OFF Season | 13.06.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | OFF Season | 22.08.2023 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | OFF Season | 09.07.2024 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. | 250 | Internal | A Varma / V singh
62393dae1725 | RAW QUAD 47 :: ZIL/SUG./047 (07.LCV.050.B01) | ZIL/SUG./047 (07.LCV.050.B01) | OFF Season | 02.07.2025 |  |  | Control valve found syrup scaling and rusty. | Seat,Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning Overhauling work done. | 250 | Internal | A Varma / V singh
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | OFF Season | 13.06.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | OFF Season | 22.08.2023 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | OFF Season | 11.07.2024 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. | 250 | Internal | A Varma / V singh
7d8200d43fdb | RAW QUAD 47 :: ZIL/SUG./048 (FCV-204) | ZIL/SUG./048 (FCV-204) | OFF Season | 03.07.2025 |  |  | Control valve found syrup scaling and Seat Damage | Seat,Gear,actuator,body,plug,positioner,valve seat replaced with checking,AFR cleaning Overhauling work done. | 12500 | Internal | A Varma / V singh | Found Valve Passing
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | OFF Season | 25.07.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | OFF Season | 07.08.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | OFF Season | 13.07.2024 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. | 250 | Internal | A Varma / V singh
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | OFF Season | 02.07.2025 |  |  | Control valve found syrup scaling and rusty. | Seat,Gear,actuator,body,plug,positioner,valve seat checking,AFR cleaning Overhauling work done. | 250 | Internal | A Varma / V singh
224cb1e8b151 | RAW QUAD 47 :: ZIL/SUG./049 (07LCV.040.B01) | ZIL/SUG./049 (07LCV.040.B01) | OFF Season | 15.01.2026 |  |  | 3400 body level transmitter diaphrgm tube leakage upper side | Level transmitter calibartion out. Due to diaphargm seal damage. | 250 | Internal | A Varma / V singh
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | OFF Season | 26.07.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | OFF Season | 09.08.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | OFF Season | 19.07.2024 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. | 250 | Internal | A Varma / V singh
360a63aa1908 | RAW QUAD 47 :: ZIL/SUG./050 (07LCV.050.B01) | ZIL/SUG./050 (07LCV.050.B01) | OFF Season | 03.07.2025 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. | 250 | Internal | A Varma / V singh
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | OFF Season | 26.07.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | OFF Season | 01.08.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | OFF Season | 22.07.2024 |  |  | Control valve Seat & Body found highly scalefull. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing,with seat checking & valve painting. | 250 | Internal | A Varma / V singh
49e1cd515e1c | RAW QUAD 47 :: ZIL/SUG./051 (07LCV.020B01) | ZIL/SUG./051 (07LCV.020B01) | OFF Season | 12.07.2025 |  |  | Control valve Seat & Body found highly scalefull. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing,with seat checking & valve painting. | 250 | Internal | A Varma / V singh
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | OFF Season | 04.08.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | OFF Season | 12.08.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | OFF Season | 16.07.2024 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, with seat checking & valve painting. | 250 | Internal | A Varma / V singh
aaf0cecbc41e | RAW QUAD 47 :: ZIL/SUG./052 (07LCV.060B01) | ZIL/SUG./052 (07LCV.060B01) | OFF Season | 12.07.2025 |  |  | Control valve Seat & Body found highly scalefull. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing,with seat checking & valve painting. | 250 | Internal | A Varma / V singh
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | OFF Season | 21.06.2022 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, checking with seat & valve painting. |  | Internal | A Varma / V singh
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | OFF Season | 08.08.2023 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, with seat checking & valve painting. |  | Internal | A Varma / V singh
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | OFF Season | 05.07.2024 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, with seat checking & valve painting. | 250 | Internal | A Varma / V singh
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | Season | 16.11.2024 |  |  | Positioner problem | Repair Positioner replaced with take in line |  | Internal | A Varma / V singh
619fc7f42e81 | RAW QUAD 47 :: ZIL/SUG./053 (07LCV.030B01) | ZIL/SUG./053 (07LCV.030B01) | OFF Season | 25.08.2025 |  |  | Control valve found syrup scaling and rusty. | Gear,actuator,seat body,plug,positioner,AFR cleaning repairing, with seat checking & valve painting. | 300 | Internal | A Varma / V singh
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | OFF Season | 21.06.2022 |  |  | Control valve found scaling and rusty. | Gear,actuator,seat body,plug,SOV,AFR cleaning repairing, with seat checking & valve painting. |  | Internal | A Varma / V singh
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | OFF Season | 08.08.2023 |  |  | Control valve found scaling and rusty. | Gear,actuator,seat body,plug,SOV,AFR cleaning repairing, with seat checking & valve painting. |  | Internal | A Varma / V singh
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | OFF Season | 05.07.2024 |  |  | Control valve found scaling and rusty. | Gear,actuator,seat body,plug,SOV,AFR cleaning repairing, with seat checking & valve painting. | 200 | Internal | A Varma / V singh
afdf7d239cec | RAW QUAD 47 :: ZIL/SUG./054/SAFETY | ZIL/SUG./054/SAFETY | OFF Season | 15.07.2025 |  |  | Control valve found scaling and rusty. | Gear,actuator,seat body,plug,SOV,AFR cleaning repairing, with seat checking & valve painting. | 200 | Internal | A Varma / V singh
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | OFF Season | 2023-06-20 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | OFF Season | 2024-07-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | OFF Season | 2025-06-13 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
e420b9453293 | FLOW METER :: ZIL/SUG/01/DS_MASS_FLW_DUMMY | ZIL/SUG/01/DS_MASS_FLW_DUMMY | OFF Season | 19.09.2025 |  |  | Age Complete | Replaced with newMASS FLOW METER,CMF-400M451N2BIEZZZ+2700R1288IEZZZSR NO-13870446+13863043 WITH CABLE -10MTR MOUNTING U CLAMP & SS FLANGE -2 NOS MAKE-EMERSON | 162500 | Internal | Mr. Anirudh Varma
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | OFF Season | 2023-06-20 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | OFF Season | 2024-07-30 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
720a91e7c2e5 | FLOW METER :: ZIL/SUG/01/_03_FI_040_B01 | ZIL/SUG/01/_03_FI_040_B01 | OFF Season | 2025-06-13 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | OFF Season | 2023-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | OFF Season | 2024-07-30 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
957ad8dc5034 | FLOW METER :: ZIL/SUG/01/FT_SJMG | ZIL/SUG/01/FT_SJMG | OFF Season | 2025-06-14 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | OFF Season | 2023-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | OFF Season | 2024-07-30 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
be2378ecb451 | FLOW METER :: ZIL/SUG./01/_03_FI_040_B02 | ZIL/SUG./01/_03_FI_040_B02 | OFF Season | 2025-06-14 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | OFF Season | 2023-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | OFF Season | 2024-07-30 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | OFF Season | 2025-06-14 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
cd4285a04f9d | FLOW METER :: ZIL/SUG./01/FT_IMWF_101 | ZIL/SUG./01/FT_IMWF_101 | ON Season | 2025-10-24 |  |  | Flow Tx not working tube is OK | Replaced Control Card | 82000 | Internal | Mr. Anirudh Varma
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | OFF Season | 2023-06-24 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | OFF Season | 2024-07-15 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
b3385a37c807 | FLOW METER :: ZIL/SUG./01/FT_RWF_102 | ZIL/SUG./01/FT_RWF_102 | OFF Season | 2025-06-07 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | OFF Season | 2023-06-24 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | OFF Season | 2024-07-15 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | OFF Season | 2025-06-07 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
1dade74e949f | FLOW METER :: ZIL/SUG./01/UGR-FM-1 | ZIL/SUG./01/UGR-FM-1 | Season | 2025-11-01 |  |  | Flow meter display not healthy | Replaced with new take in line | 18000 | Internal | Mr. Anirudh Varma
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | OFF Season | 2023-06-24 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | OFF Season | 2024-07-15 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
e2d0d566e3c3 | FLOW METER :: ZIL/SUG./CPU-WFM | ZIL/SUG./CPU-WFM | OFF Season | 2025-06-07 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | OFF Season | 2023-06-24 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | OFF Season | 2024-07-15 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
18035210f01c | FLOW METER :: ZIL/SUG./001/COLD-WATER | ZIL/SUG./001/COLD-WATER | OFF Season | 2025-06-07 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | OFF Season | 2023-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | OFF Season | 2024-07-09 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
6246406e90fc | FLOW METER :: ZIL/SUG./01/_05_FT_100_B01 | ZIL/SUG./01/_05_FT_100_B01 | OFF Season | 2025-06-17 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | OFF Season | 2023-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | OFF Season | 2024-07-09 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
30fd196df9a0 | FLOW METER :: ZIL/SUG./01/03.FT140.B01. | ZIL/SUG./01/03.FT140.B01. | OFF Season | 2025-06-17 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | OFF Season | 2023-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | OFF Season | 2024-07-09 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
bd1904436933 | FLOW METER :: ZIL/SUG./01/_03_FT_120_B01 | ZIL/SUG./01/_03_FT_120_B01 | OFF Season | 2025-06-17 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | OFF Season | 2023-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | OFF Season | 2024-07-09 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
a1fc27d3d05a | FLOW METER :: ZIL/SUG./01/DE-SWEETING | ZIL/SUG./01/DE-SWEETING | OFF Season | 2025-06-17 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | OFF Season | 2023-06-02 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | OFF Season | 2024-07-19 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
bd2155ca5019 | FLOW METER :: ZIL/SUG./01/05.FT060.B01. | ZIL/SUG./01/05.FT060.B01. | OFF Season | 2025-06-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | OFF Season | 2023-06-02 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | OFF Season | 2024-07-19 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
35a210b6557b | FLOW METER :: ZIL/SUG./01/_05_FT_040_B01 | ZIL/SUG./01/_05_FT_040_B01 | OFF Season | 2025-06-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | OFF Season | 2023-06-02 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | OFF Season | 2024-07-19 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
5023db2c9a2a | FLOW METER :: ZIL/SUG/01/_07_FT_100_B01 | ZIL/SUG/01/_07_FT_100_B01 | OFF Season | 2025-06-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | OFF Season | 2023-06-02 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | OFF Season | 2024-07-19 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
0991cf792b3d | FLOW METER :: ZIL/SUG./01/_15_FT_013_B01 | ZIL/SUG./01/_15_FT_013_B01 | OFF Season | 2025-06-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | OFF Season | 2023-06-02 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | OFF Season | 2024-07-19 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
d9fb31fb1206 | FLOW METER :: ZIL/SUG./C.CONTI/FT_25 | ZIL/SUG./C.CONTI/FT_25 | OFF Season | 2025-06-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | OFF Season | 2023-06-02 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | OFF Season | 2024-07-19 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
8af6187bbb9e | FLOW METER :: ZIL/SUG./C.CONTI/FT_26 | ZIL/SUG./C.CONTI/FT_26 | OFF Season | 2025-06-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | OFF Season | 2023-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | OFF Season | 2024-08-18 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
bc3c1501a99c | FLOW METER :: ZIL/SUG./B.CONTI/FT_23 | ZIL/SUG./B.CONTI/FT_23 | OFF Season | 2025-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | OFF Season | 2023-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | OFF Season | 2024-08-18 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
8fa2fb7ddc7c | FLOW METER :: ZIL/SUG./B.CONTI/FT_24 | ZIL/SUG./B.CONTI/FT_24 | OFF Season | 2025-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | OFF Season | 2023-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | OFF Season | 2024-08-18 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
1ed56a8556e2 | FLOW METER :: ZIL/SUG./B.CONTI/FT_Grain | ZIL/SUG./B.CONTI/FT_Grain | OFF Season | 2025-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | OFF Season | 2023-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | OFF Season | 2024-08-18 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
7499bc8d58d4 | FLOW METER :: ZIL/SUG./C.CONTI/FT_Grain | ZIL/SUG./C.CONTI/FT_Grain | OFF Season | 2025-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | OFF Season | 2023-06-10 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | OFF Season | 2024-08-28 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
b59871438033 | FLOW METER :: ZIL/SUG./01/05.FT.130.B01 | ZIL/SUG./01/05.FT.130.B01 | OFF Season | 2025-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | OFF Season | 2023-06-10 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | OFF Season | 2024-08-28 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
bb677b5e85f7 | FLOW METER :: ZIL/SUG./01/OVER-HEAD-FM | ZIL/SUG./01/OVER-HEAD-FM | OFF Season | 2025-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | OFF Season | 2023-06-10 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | OFF Season | 2024-08-28 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | OFF Season | 2025-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
43cdc8679bf2 | FLOW METER :: ZIL/SUG./01/UGR-FM-2 | ZIL/SUG./01/UGR-FM-2 | ON Season | 2025-11-01 |  |  | Flow Tx. Not working | Replaced Card with Take in Line |  |  | Mr. Anirudh Varma
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | OFF Season | 2023-06-23 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | OFF Season | 2024-08-10 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | OFF Season | 2025-06-15 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
895b3ba52928 | FLOW METER :: ZIL/SUG./01/ADMIN-FM | ZIL/SUG./01/ADMIN-FM | Season | 2026-03-20 |  |  | Flow Tx. Not healthy. | Replaced electronic Card with Take in Line |  | Internal | Mr. Anirudh Varma
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | OFF Season | 2023-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | OFF Season | 2024-08-24 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | OFF Season | 2025-06-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
fd337d3480ae | FLOW METER :: ZIL/SUG./01/STP-FM | ZIL/SUG./01/STP-FM | Season | 2026-03-20 |  |  | Flow meter not working | Replace flow meter with Take in Line |  | Internal | Mr. Anirudh Varma
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | OFF Season | 2023-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | OFF Season | 2024-07-22 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
f7ba61246ec7 | FLOW METER :: ZIL/SUG./01/T-YARD-FM | ZIL/SUG./01/T-YARD-FM | OFF Season | 2025-07-13 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | OFF Season | 2023-06-12 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | OFF Season | 2024-07-15 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
769599b2370f | FLOW METER :: ZIL/SUG./01/DIS.-TW-FM-1 | ZIL/SUG./01/DIS.-TW-FM-1 | OFF Season | 2025-07-10 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | OFF Season | 27.05.2022 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking Load bucket Bearing ,Course Cylinder Seal kit replaced |  | Internal | A Varma / V Singh
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | OFF Season | 10.08.2023 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking, Load bucket Bearing ,Course Cylinder Seal kit replaced. | 900 | Internal | A Varma / V Singh
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | OFF Season | 27.06.2024 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking , Load bucket ,Course Cylinder Seal kit replaced replaced. | 700 | Internal | A Varma / V Singh
6386c46456f5 | WEIGHING MACHINE :: ZIL/SUG./001/L-DWM-1 | ZIL/SUG./001/L-DWM-1 | OFF Season | 12.06.25 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust.4 nos FCV not working | All Cylinder & SOV AFR repair & checking Seal kit replaced of Load bucket & Bag clamp cylinder SOV base screw also replace. | 800 | Internal | A Varma / V Singh
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | OFF Season | 25.05.2022 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking Seal kit replaced of fine & bag clamp Cylinder |  | Internal | A Varma / V Singh
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | OFF Season | 09.08.2023 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking,Load bucket Bearing ,Course Cylinder seal kit replaced | 900 | Internal | A Varma / V Singh
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | OFF Season | 29.06.2024 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking, Load bucket ,Course Cylinder Seal kit replaced. | 600 | Internal | A Varma / V Singh
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Season | 20.11.2024 |  |  | M1 SOV problem | Replaced with new | 900 | Internal | A Varma / V Singh
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Season | 23.11.2024 |  |  | M2 SOV problem | Repair it | 210 | Internal | A Varma / V Singh
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Season | 04.12.2024 |  |  | M1 SOV problem | Replaced with new | 900 | Internal | A Varma / V Singh
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Season | 08.10.2025 |  |  | M2 Load Bucket Cylinder Problem | Repair it | 650 | Internal | A Varma / V Singh
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | OFF Season | 10.06.25 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust.4 nos FCV not working | All Cylinder & SOV AFR repair & checking Seal kit replaced of Load bucket SOV base screw also replace. | 400 | Internal | A Varma / V Singh
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | ON Season | 01.11.2025 |  |  | Leval switch not working | Replaced it Take in Line |  | Internal | A Varma
0f487f52027c | WEIGHING MACHINE :: ZIL/SUG./001/M-DWM-2 | ZIL/SUG./001/M-DWM-2 | Season | 02.11.2025 |  |  | Fine sutter not working found SOV not working. | Replaced it Take in Line |  | Internal | Anuj Kumar
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | OFF Season | 23.05.2022 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking Seal kit replaced of Load bucket ,Course ,fine Cylinder |  | Internal | A Varma / V Singh
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | OFF Season | 09.08.2023 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking,Load bucket ,Course ,fine Cylinder Seal kit & load bucket bearing replaced. | 1200 | Internal | A Varma / V Singh
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | OFF Season | 23.06.24 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking Seal kit replaced of Load bucket , Fine Cylinder | 600 | Internal | A Varma / V Singh
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | Season | 23.11.2024 |  |  | SOV problem | Replaced with new | 900 | Internal | A Varma / V Singh
e586dcabb084 | WEIGHING MACHINE :: ZIL/SUG./001/S-DWM-3 | ZIL/SUG./001/S-DWM-3 | OFF Season | 17.06.25 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust.4 nos FCV not working | All Cylinder & SOV AFR repair & checking Seal kit replaced of Load bucket , Fine Cylinder | 800 | Internal | A Varma / V Singh
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | OFF Season | 26.05.2022 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking work done. | 150 | Internal | A Varma / V Singh
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | OFF Season | 08.08.2023 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking Seal kit replaced of Load bucket ,Course ,fine Cylinder | 650 | Internal | A Varma / V Singh
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | OFF Season | 26.07.2024 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking work done. | 250 | Internal | A Varma / V Singh
f016b81a848a | WEIGHING MACHINE :: ZIL/SUG./001/25KG-SWM-5 | ZIL/SUG./001/25KG-SWM-5 | OFF Season | 19.06.25 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust.4 nos FCV not working | All Cylinder & SOV AFR repair & checking Seal kit replaced of Load bucket , Fine & mid Cylinder | 1200 | Internal | A Varma / V Singh
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | OFF Season | 26.05.2022 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder & SOV AFR repair & checking Seal kit replaced of Load bucket ,Course ,fine Cylinder |  | Internal | A Varma / V Singh
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | OFF Season | 07.08.2023 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder , SOV,AFR repair & checking Seal kit replaced of Load bucket Cylinder |  | Internal | A Varma / V Singh
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | OFF Season | 29.06.2024 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust. | All Cylinder,SOV ,AFR repair & checking Seal kit replaced of Load bucket ,Course Cylinder | 1150 | Internal | A Varma / V Singh
17005bd31542 | WEIGHING MACHINE :: ZIL/SUG./001/PH-DWM-04 | ZIL/SUG./001/PH-DWM-04 | OFF Season | 11.06.25 |  |  | Corse ,fine, S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing found sugar dust.5 nos FCV not working | All Cylinder & SOV AFR repair & checking Seal kit replaced of Load bucket , Fine Cylinder | 800 | Internal | A Varma / V Singh
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | OFF Season | 20.05.2022 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | OFF Season | 15.08.2023 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | OFF Season | 26.06.2024 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
df263fd8dd87 | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-01 | ZIL/SUG./001/B-CFM-01 | OFF Season | 10.06.2025 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | OFF Season | 20.05.2022 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | OFF Season | 15.08.2023 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | OFF Season | 26.06.2024 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
f2a80d59cb5b | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-02 | ZIL/SUG./001/B-CFM-02 | OFF Season | 10.06.2025 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | OFF Season | 20.05.2022 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | OFF Season | 15.08.2023 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | OFF Season | 26.06.2024 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
4dfb948743da | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-03 | ZIL/SUG./001/B-CFM-03 | OFF Season | 10.06.2025 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | OFF Season | 18.05.2022 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | OFF Season | 26.08.2023 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | OFF Season | 20.06.2024 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
84bfaa76d74a | CENTRIFUGAL B & C :: ZIL/SUG./001/B-CFM-04 | ZIL/SUG./001/B-CFM-04 | OFF Season | 19.06.2025 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | OFF Season | 18.05.2022 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | OFF Season | 26.08.2023 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | OFF Season | 20.06.2024 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
d19aae6716bd | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-01 | ZIL/SUG./001/C-CFM-01 | OFF Season | 19.06.2025 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | OFF Season | 18.05.2022 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | OFF Season | 26.08.2023 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | OFF Season | 20.06.2024 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | OFF Season | 19.06.2025 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
cb36bcb64470 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-02 | ZIL/SUG./001/C-CFM-02 | Season | 11.11.2025 |  |  | Controller power not on | Replaced with new controller | 10800 | Internal | Anuj Kumar
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | OFF Season | 18.05.2022 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | OFF Season | 26.08.2023 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | OFF Season | 20.06.2024 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | OFF Season | 19.06.2025 |  |  | Sov with feed back sensor sugar dust. | All sov Clean & feed back sensor repair with checking work |  | Internal | A Varma
27d85fa2b593 | CENTRIFUGAL B & C :: ZIL/SUG./001/C-CFM-03 | ZIL/SUG./001/C-CFM-03 | Season | 11.11.2025 |  |  | Controller power not on | Replaced with new controller | 10800 | Internal | Anuj Kumar
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | OFF Season | 07.05.2022 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 300 | Internal | A Varma / V Singh
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | OFF Season | 11.08.2023 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 400 | Internal | A Varma / V Singh
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | OFF Season | 17.06.2024 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 400 | Internal | A Varma / V Singh
c188745054f4 | AIR COMP & DRYER :: ZIL/SUG./001/AC-1 | ZIL/SUG./001/AC-1 | OFF Season | 12.06.2025 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 350 | Internal | A Varma / V Singh
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | OFF Season | 07.05.2022 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work |  | Internal | Mr. A Varma / Mr.V Singh
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | OFF Season | 11.08.2023 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 900 | Internal | Mr. A Varma / Mr.V Singh
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | OFF Season | 17.06.2024 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 700 | Internal | Mr. A Varma / Mr.V Singh | .
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | OFF Season | 12.06.2025 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 800 | Internal | Mr. A Varma / Mr.V Singh
cd41d6b59f65 | AIR COMP & DRYER :: ZIL/SUG./001/AC-2 | ZIL/SUG./001/AC-2 | Season | 07.11.2025 |  |  | Outlat temp. error rtd Not healthy | Replaced with new | 1800 | Internal | Mr.Anuj kr./ Mr.V Singh
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | OFF Season | 27.05.2022 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work |  | Internal | A Varma / V Singh
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | OFF Season | 10.08.2023 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 900 | Internal | A Varma / V Singh
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | OFF Season | 27.06.2024 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 700 | Internal | A Varma / V Singh
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | OFF Season | 12.06.2025 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 800 | Internal | A Varma / V Singh
fb2f08d5c731 | AIR COMP & DRYER :: ZIL/SUG./001/AC-3 | ZIL/SUG./001/AC-3 | Season | 27.11.2025 |  |  | Found flow switch not working | Replaced with new | 7000 | Internal | A Varma / V Singh
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | OFF Season | 27.05.2022 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work |  | Internal | A Varma / V Singh
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | OFF Season | 10.08.2023 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 900 | Internal | A Varma / V Singh
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | OFF Season | 27.06.2024 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 700 | Internal | A Varma / V Singh
8fb00e31b753 | AIR COMP & DRYER :: ZIL/SUG./001/AC-4 | ZIL/SUG./001/AC-4 | OFF Season | 12.06.2025 |  |  | All SOV, flow switch ,gauge with pressure switch found healthy | All SOV AFR repair & checking with calibration work | 800 | Internal | A Varma / V Singh
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | OFF Season | 06.05.2022 |  |  | All SOV, 3 way valve found healthy | All SOV & 3 Way valve repair checking with work |  | Internal | A Varma / V Singh
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | OFF Season | 11.08.2023 |  |  | All SOV, 3 way valve found healthy | All SOV & 3 Way valve repair checking with work | 900 | Internal | A Varma / V Singh
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | OFF Season | 28.06.2024 |  |  | All SOV, 3 way valve found healthy | All SOV & 3 Way valve repair checking with work | 700 | Internal | A Varma / V Singh
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | OFF Season | 27.06.2025 |  |  | All SOV, 3 way valve found healthy Alumina ball rusted | All SOV & 3 Way valve repair & checking with Alumina ball replaced with new. | 35000 | Internal | A Varma / V Singh
710c680f5b8e | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-1 | ZIL/SUG./001/AC dryer-1 | Season | 04.02.2026 |  |  | found air dryer drain valve timer not working | Timer controller replaced with new. | 7000 | Internal | A Varma / V Singh
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | OFF Season | 06.05.2022 |  |  | All SOV, 3 way valve found healthy | All SOV & 3 Way valve repair checking with work |  | Internal | A Varma / V Singh
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | OFF Season | 11.08.2023 |  |  | All SOV, 3 way valve found healthy | All SOV & 3 Way valve repair checking with work | 900 | Internal | A Varma / V Singh
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | OFF Season | 28.06.2024 |  |  | All SOV, 3 way valve found healthy | All SOV & 3 Way valve repair checking with work | 700 | Internal | A Varma / V Singh
a50eb0d41272 | AIR COMP & DRYER :: ZIL/SUG./001/AC dryer-2 | ZIL/SUG./001/AC dryer-2 | OFF Season | 27.06.2025 |  |  | All SOV, 3 way valve found healthy Alumina ball rusted | All SOV & 3 Way valve repair & checking with Alumina ball replaced with new. | 35000 | Internal | A Varma / V Singh
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | OFF Season | 17/05/2022 |  |  | Control valve PTFE seat found worn-out, Body found rusty. IP & Positioner Found healty. | Replace PTFE seat with new Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | OFF Season | 2023-06-01 |  |  | Control valve Seat, Body found rusty. IP & Positioner Found healty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | OFF Season | 2024-05-23 |  |  | Control valve Seat,Body found worn-out. IP& Positioner Found healty. Found AFR spring seat worn Out. | Control valve Body replace with New spare.Proper cleaning ,lubrication & Overhauling work done. | 30000 | Internal | Mr Anuj / Mr V.Singh
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | OFF Season | 2025-06-06 |  |  | Control valve Seat, Body found rusty. IP & Positioner Found healty. | Proper cleaning , lubriaction & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
c827e7da1a31 | Pan-1-23 :: ZIL/SUG./001/APFC-01 | ZIL/SUG./001/APFC-01 | OFF Season | 2026-04-24 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 350 | Internal | Mr A. Varma / Mr V.Singh
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | OFF Season | 17/05/2022 |  |  | Control valve Actuator spring found crack. Seat also worn-out. | Replace Seat & spring with new. Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | OFF Season | 2023-01-06 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | OFF Season | 2024-05-25 |  |  | Control valve found scaled and rusty. Afr Spring seat wornout. | Proper cleaning,lubrication & overhauling work done. AFR Spring seat replace. | 150 | Internal | Mr Anuj / Mr V.Singh
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | OFF Season | 2025-06-07 |  |  | Control valve Seat, Body found rusty. IP & Positioner Found healty. | Proper cleaning , lubriaction & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | Season | 2025-11-12 |  |  | 03 Nos Controller not working | Replaced with new | 6318 | Internal | Mr Anuj / Mr V.Singh
05187a35ba10 | Pan-1-23 :: ZIL/SUG./001/APFC-02 | ZIL/SUG./001/APFC-02 | OFF Season | 2026-04-24 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 350 | Internal | Mr A. Varma / Mr V.Singh
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | OFF Season | 20/05/2022 |  |  | Control valve Actuator Diaphragm found leakage. Body & seat scaled and rusty. IP ,Positioner & AFR found healty. | Control valve Diaphragm repair , cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | OFF Season | 2023-02-06 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | OFF Season | 2024-05-25 |  |  | Control valve found scaled and rusty. Afr Drain assembly wornout. | Proper cleaning,lubrication & overhauling work done. Replace drain assembly. | 250 | Internal | Mr Anuj / Mr V.Singh
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | OFF Season | 2025-06-07 |  |  | Control valve Seat, Body found rusty. IP & Positioner Found healty.AFR filter assembly is worn-out | Proper cleaning , lubriaction & painting work done.AFR filter assembly replace with new. | 350 | Internal | Mr Anuj / Mr V.Singh
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | Season | 2025-12-15 |  |  | Signal malfunctioning problem,wiring problem | Check many time but interanl wiring problem & mulfuctioning signal | 350 | Internal | Mr Anuj / Mr V.Singh
278ad771b6bc | Pan-1-23 :: ZIL/SUG./001/APFC-03 | ZIL/SUG./001/APFC-03 | OFF Season | 2026-04-23 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 350 | Internal | Mr A. Varma / Mr V.Singh
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | OFF Season | 17/06/2022 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | OFF Season | 2023-07-06 |  |  | Control valve PTFE seat found worn-out. Positioner ,AFR are healthy. | Replace control valve seat with new. Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | OFF Season | 2024-06-03 |  |  | Control valve Seat & Body found rusty . AFR Internal Plastic Parts wornout & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. Replace afr internal parts . | 650 | Internal | Mr Anuj / Mr V.Singh
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | OFF Season | 2025-06-09 |  |  | Control valve Seat, Body found rusty. IP & Positioner Found healty.AFR filter assembly is worn-out | Proper cleaning , lubriaction & painting work done.AFR filter assembly replace with new. | 350 | Internal | Mr Anuj / Mr V.Singh
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | Season | 2025-12-20 |  |  | Signal malfunctioning problem,wiring problem | Check many time but interanl wiring problem & mulfuctioning signal | 350 | Internal | Mr Anuj / Mr V.Singh
ce0a187f8376 | Pan-1-23 :: ZIL/SUG./001/APFC-04 | ZIL/SUG./001/APFC-04 | OFF Season | 2026-05-09 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 350 | Internal | Mr A. Varma / Mr V.Singh
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | OFF Season | 20/05/2022 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | OFF Season | 2023-06-06 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | OFF Season | 2024-07-06 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | OFF Season | 2025-06-16 |  |  | Control valve Seat, Body found rusty. IP & Positioner Found healty. | Proper cleaning , lubriaction & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | Season | 2025-11-13 |  |  | Controller Input Not working | Replaced with new Controller 3no | 6318 | Internal | Mr Anuj / Mr V.Singh
782baa8ab1ae | Pan-1-23 :: ZIL/SUG./001/APFC-05 | ZIL/SUG./001/APFC-05 | OFF Season | 2026-05-09 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 350 | Internal | Mr A. Varma / Mr V.Singh
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | OFF Season | 20/05/2022 |  |  | Control valve Actuator spring found broken . Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Actuator spring Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | OFF Season | 2023-06-06 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | OFF Season | 2024-06-05 |  |  | Control valve Seat & Body found rusty .Positioner found Healthy & AFR drain valve assembly wornout. | Control Valve Proper cleaning & painting work done. Replace Afr drain assembly. | 280 | Internal | Mr Anuj / Mr V.Singh
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | OFF Season | 2025-06-17 |  |  | Control valve Seat, Body found rusty. IP & Positioner Found healty. | Proper cleaning , lubriaction & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
c628710cdf3a | Pan-1-23 :: ZIL/SUG./001/APFC-06 | ZIL/SUG./001/APFC-06 | OFF Season | 2026-05-15 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 350 | Internal | Mr A. Varma / Mr V.Singh
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | OFF Season | 23/05/2022 |  |  | Control valve found Gland packing leakage & Seat worn-out. Body found rusty .AFR & Positioner found Healthy. | Control Valve Actuator spring Proper cleaning & painting work done. | 100 | Internal | Mr Anuj / Mr V.Singh
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | OFF Season | 14/7/2023 |  |  | Control valve Seat guide found worn-out. Positioner , AFR & IP are healthy position. | Welding and machining work done. After overhauling Proper cleaning & painting work done. | 200 | Internal | Mr Anuj / Mr V.Singh
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | OFF Season | 2024-06-05 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 120 | Internal | Mr Anuj / Mr V.Singh
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Season | 2024-12-04 |  |  | Valve dismantale due to leakage cantrol valve body found . The bodi ofcantrol valve wornout | cantrol valve bodi riplace with new | 20000 | Internal | Mr Anuj / Mr V.Singh
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Season | 2025-03-15 |  |  | Control valve dismantale due to passing.found actuator diaphragm ,spring & Diaphargm supporting Dcsk damage. | Actuator spring & diaphragm riplace with new.Diaphragm supporting disc was repaired. | 5767 | Internal | Mr Anuj / Mr V.Singh
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | OFF Season | 2025-06-17 |  |  | Control valve Seat, Body found rusty. IP & Positioner Found healty. | Proper cleaning , lubriaction & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Season | 2026-01-02 |  |  | Tail pipe indicator power not on | Replaced with new | 2000 | Internal | Mr Anuj / Mr V.Singh
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | Season | 2026-01-09 |  |  | Pan Body temp. indicator power not on | Replaced with new | 2001 | Internal | Mr Anuj / Mr V.Singh
543d7e2c8e59 | Pan-1-23 :: ZIL/SUG./001/APFC-07 | ZIL/SUG./001/APFC-07 | OFF Season | 2026-05-15 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 350 | Internal | Mr A. Varma / Mr V.Singh
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | OFF Season | 31/05/2022 |  |  | Control valve actuator o-ring found damage. AFR, Positioner & IP are healthy. | Replace with new O-ring. After overhauling Proper cleaning & painting work done. | 100 | Internal | Mr Anuj / Mr V.Singh
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | OFF Season | 2023-09-06 |  |  | Control valve Body found scaled and rusty. Control valve gland packing worn-out. AFR, Positioner & IP are healthy. | Replace new gland packing. After overhauling Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | OFF Season | 2024-05-28 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 120 | Internal | Mr Anuj / Mr V.Singh
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | Season | 2025-03-15 |  |  | Control valve dismantale due to passing masscute ,Found actuator spring was damage. | Actuator spring replace with new. | 2433 | Internal | Mr Anuj / Mr V.Singh
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | OFF Season | 2025-06-18 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
de63f992d023 | Pan-1-23 :: ZIL/SUG./001 /APFC-08 | ZIL/SUG./001 /APFC-08 | OFF Season | 2026-05-18 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 350 | Internal | Mr A. Varma / Mr V.Singh
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | OFF Season | 31/05/2022 |  |  | Control valve actuator o-ring ,Spring found broken, Gland packing also leakage. AFR, Positioner & IP are healthy. | Replace O-ring , Spring And gland packing with new. After overhauling Proper cleaning & painting work done. | 100 | Internal | Mr Anuj / Mr V.Singh
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | OFF Season | 2023-09-06 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 200 | Internal | Mr Anuj / Mr V.Singh
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | OFF Season | 2024-05-27 |  |  | Control valve Seat & Body found rusty .Positioner found Healthy & AFR gauge worn out. | Control Valve Proper cleaning & painting work done. Afr replace with new Spare gauge. | 800 | Internal | Mr Anuj / Mr V.Singh
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | OFF Season | 2025-06-18 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & overhalling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | Season | 2025-01-30 |  |  | Signal malfunctioning problem,wiring problem | Check many time but interanl wiring problem & mulfuctioning signal |  | Internal | Mr Anuj / Mr V.Singh
058911f68dfa | Pan-1-23 :: ZIL/SUG./001 /APFC-09 | ZIL/SUG./001 /APFC-09 | OFF Season | 2026-05-19 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 350 | Internal | Mr A. Varma / Mr V.Singh
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | OFF Season | 2022-06-01 |  |  | Control valve actuator o-ring ,Gland packing also leakage . AFR, Positioner & IP are healthy. | Replace O-ring And gland packing with new. After overhauling Proper cleaning & painting work done. | 100 | Internal | Mr Anuj / Mr V.Singh
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | OFF Season | 2023-06-10 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | OFF Season | 2024-06-06 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 120 | Internal | Mr Anuj / Mr V.Singh
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | OFF Season | 2025-06-19 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
559e712e58dc | Pan-1-23 :: ZIL/SUG./001 /APFC-10 | ZIL/SUG./001 /APFC-10 | OFF Season | 2026-05-20 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 350 | Internal | Mr A. Varma / Mr V.Singh
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | OFF Season | 2022-07-07 |  |  | Control valve actuator o-ring leakage . AFR, Positioner & IP are healthy. | Replace O-ring with new. After overhauling Proper cleaning & painting work done. | 100 | Internal | Mr Anuj / Mr V.Singh
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | OFF Season | 2023-08-06 |  |  | Control valve Seat found scaled and rusty. Found AFR Gauge & Filter Damage. Positioner found healty | Replace AFR gauge & filter work done. After overhauling Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | OFF Season | 2024-06-06 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 200 | Internal | Mr Anuj / Mr V.Singh
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | OFF Season | 2025-06-14 |  |  | Control valve Seat & Body found rusty .AFR filter and filterwornout Positioner found Healthy. | Control Valve Proper cleaning & overhalling work done flter and filter holderriplace. | 900 | Internal | Mr Anuj / Mr V.Singh
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Season | 2025-11-12 |  |  | Body & Tail pipe Temp. not working | TT Replaced with new 2no | 2002 | Internal | Mr Anuj / Mr V.Singh
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | Season | 2025-02-15 |  |  | Signal malfunctioning problem,wiring problem | Check many time but interanl wiring problem & mulfuctioning signal |  | Internal | Mr Anuj / Mr V.Singh
626316f2c996 | Pan-1-23 :: ZIL/SUG./001 /APFC-11 | ZIL/SUG./001 /APFC-11 | OFF Season | 2026-05-21 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 350 | Internal | Mr A. Varma / Mr V.Singh
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | OFF Season | 2022-07-06 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 200 | Internal | Mr Anuj / Mr V.Singh
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | OFF Season | 2023-06-12 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | OFF Season | 2024-05-28 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy.Found positioner gauge damage. | Control Valve Proper cleaning & overhauling work done. | 350 | Internal | Mr Anuj / Mr V.Singh
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | OFF Season | 2025-06-13 |  |  | Control valve Seat, Body found rusty. IP & Positioner Found healty.electrot cuplar wornout | Proper cleaning , lubriaction work done. Electrod cuplar riplace | 500 | Internal | Mr Anuj / Mr V.Singh
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | Season | 2025-11-04 |  |  | Rotary Not working | Replaced with new | 550 | Internal | Mr Anuj / Mr V.Singh
d35d3744d1a1 | Pan-1-23 :: ZIL/SUG./001 /APFC-12 | ZIL/SUG./001 /APFC-12 | OFF Season | 2026-05-21 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 350 | Internal | Mr A. Varma / Mr V.Singh
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | OFF Season | 2022-07-06 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 100 | Internal | Mr Anuj / Mr V.Singh
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | OFF Season | 2023-06-12 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | OFF Season | 2024-06-07 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 200 | Internal | Mr Anuj / Mr V.Singh
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | OFF Season | 23/06/2025 01/07/2025 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | Season | 2025-11-14 |  |  | Timer not working | Replaced with new | 4920 | Internal | Mr Anuj / Mr V.Singh
1e66a0a9e65e | Pan-1-23 :: ZIL/SUG./001/APFC-13A | ZIL/SUG./001/APFC-13A | OFF Season | 2026-05-23 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 250 | Internal | Mr. Anirudh / Mr V.Singh
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | OFF Season | 2022-07-07 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 100 | Internal | Mr Anuj / Mr V.Singh
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | OFF Season | 2023-06-13 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | OFF Season | 2024-06-07 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 200 | Internal | Mr Anuj / Mr V.Singh
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | OFF Season | 23/06/2025 01/07/2025 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
e7e34ef15d20 | Pan-1-23 :: ZIL/SUG./001/APFC-13B | ZIL/SUG./001/APFC-13B | OFF Season | 2026-05-23 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 250 | Internal | Mr. Anirudh / Mr V.Singh
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | OFF Season | 2022-07-07 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 100 | Internal | Mr Anuj / Mr V.Singh
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | OFF Season | 2023-06-13 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | OFF Season | 2024-06-08 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 200 | Internal | Mr Anuj / Mr V.Singh
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | OFF Season | 23/06/2025 01/07/2025 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
3aa694fe15f5 | Pan-1-23 :: ZIL/SUG./001/APFC-13C | ZIL/SUG./001/APFC-13C | OFF Season | 2026-05-25 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 250 | Internal | Mr. Anirudh / Mr V.Singh
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | OFF Season | 2022-07-07 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 100 | Internal | Mr Anuj / Mr V.Singh
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | OFF Season | 2023-06-13 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | OFF Season | 2024-06-08 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 200 | Internal | Mr Anuj / Mr V.Singh
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | OFF Season | 23/06/2025 01/07/2025 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
fa2230fcc4ee | Pan-1-23 :: ZIL/SUG./001/APFC-13D | ZIL/SUG./001/APFC-13D | OFF Season | 2026-05-25 |  |  | Control valve Seat, Body found rusty. IP & Positioner,electrode Found healty. | Proper dismentling ,cleaning & overhauling seat painting work are done. | 250 | Internal | Mr. Anirudh / Mr V.Singh
fe351a48a563 | Pan-1-23 :: ZIL/SUG./001/VB-01 | ZIL/SUG./001/VB-01 | OFF Season | 2025-06-10 |  |  | Control valve found scaled and rusty. | Proper cleaning work done. | 150 | Internal | Mr Anuj / Mr V.Singh
61943b9b1ba8 | Pan-1-23 :: ZIL/SUG./001/VB-02 | ZIL/SUG./001/VB-02 | OFF Season | 2025-06-10 |  |  | Control valve found scaled and rusty. | Proper cleaning work done. | 150 | Internal | Mr Anuj / Mr V.Singh
cd4bb3efe536 | Pan-1-23 :: ZIL/SUG./001/VB-03 | ZIL/SUG./001/VB-03 | OFF Season | 2025-06-10 |  |  | Control valve found scaled and rusty. | Proper cleaning work done. | 150 | Internal | Mr Anuj / Mr V.Singh
f968f06fea01 | Pan-1-23 :: ZIL/SUG./001/VB-08 | ZIL/SUG./001/VB-08 | OFF Season | 2025-06-10 |  |  | Control valve found scaled and rusty. | Proper cleaning work done. | 150 | Internal | Mr Anuj / Mr V.Singh
a2b8465e1110 | Pan-1-23 :: ZIL/SUG./001/VB-10 | ZIL/SUG./001/VB-10 | OFF Season | 2025-06-10 |  |  | Control valve found scaled and rusty. | Proper cleaning work done. | 150 | Internal | Mr Anuj / Mr V.Singh
cdfe835c318c | Pan-1-23 :: ZIL/SUG./001/VB-11 | ZIL/SUG./001/VB-11 | OFF Season | 2025-06-14 |  |  | Control valve found scaled and rusty. | Proper cleaning work done. | 150 | Internal | Mr Anuj / Mr V.Singh
d2001f5aa802 | Pan-1-23 :: ZIL/SUG./001/VB-12 | ZIL/SUG./001/VB-12 | OFF Season | 2025-06-13 |  |  | Control valve found scaled and rusty. | Proper cleaning work done. | 150 | Internal | Mr Anuj / Mr V.Singh
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | OFF Season | 2022-06-15 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | OFF Season | 2023-06-10 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | OFF Season | 2024-07-01 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
887ae1f6ae33 | VRL 24-53 :: ZIL/SUG./001 /PSV201 | ZIL/SUG./001 /PSV201 | OFF Season | 2025-05-01 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | OFF Season | 2022-06-15 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | OFF Season | 2023-06-10 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | OFF Season | 2024-06-28 |  |  | Control valve found scaled and rusty. Yoke ChukNut worn-out. | Proper cleaning & painting work done. Yoke Chuknut reopair in workshop. | 500 | Internal | Mr Anuj / Mr V.Singh
f4c4ed140b10 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(i) | ZIL/SUG./001/ TCV-201(i) | OFF Season | 03/05/2025 to 02/06/2025 |  |  | Control valve found scaled and rusty.yoke nut thrudwas damaged . | Proper cleaning & painting work done.a new nut was made in workshop and fitted | 1000 | Internal | Mr Anuj / Mr V.Singh
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | OFF Season | 2022-06-16 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | OFF Season | 2023-06-11 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | OFF Season | 2024-06-28 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
427ebac0a020 | VRL 24-53 :: ZIL/SUG./001/ TCV-201(ii) | ZIL/SUG./001/ TCV-201(ii) | OFF Season | 2025-05-02 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | OFF Season | 2022-06-16 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | OFF Season | 2023-06-11 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | OFF Season | 2024-05-31 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | OFF Season | 2025-07-02 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
c6d1668e078d | VRL 24-53 :: ZIL/SUG./001/TCV-203 | ZIL/SUG./001/TCV-203 | OFF Season | 2025-08-12 |  |  | Duering Calibration found Relay Not working | Replaced with new Relay valve Calibration work Done. | 4510 | Internal | Mr Anuj / Mr V.Singh
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | OFF Season | 2022-06-16 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | OFF Season | 2023-06-11 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | OFF Season | 2024-05-31 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
900cdbffa416 | VRL 24-53 :: ZIL/SUG./001/TCV-202E | ZIL/SUG./001/TCV-202E | OFF Season | 2025-07-04 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | OFF Season |  |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | OFF Season |  |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | OFF Season |  |  |  | Control valve found scaled and rusty. Spring seat of the filter regulator was wornout | Proper cleaning & Overhauling work done. AFR Spring seat replace with new. | 250 | Internal | Mr Anuj / Mr V.Singh
e8d420266467 | VRL 24-53 :: ZIL/SUG./001 /TCV203D | ZIL/SUG./001 /TCV203D | OFF Season |  |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | OFF Season | 17/06/2022 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | OFF Season | 2023-06-12 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | OFF Season | 2024-05-15 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found Healthy . | Control Valve Proper cleaning & lubrication work done. | 120 | Internal | Mr Anuj / Mr V.Singh
b235c3640469 | VRL 24-53 :: ZIL/SUG./001/TCV-203A | ZIL/SUG./001/TCV-203A | OFF Season | 2025-06-19 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found Healthy .AFR gauge wornout | Control Valve Proper cleaning & lubrication work done.AFR gauge riplace | 400 | Internal | Mr Anuj / Mr V.Singh
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | OFF Season | 17/06/2022 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | OFF Season | 2023-06-12 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | OFF Season | 2024-05-16 |  |  | Control valve Seat & Body found rusty .Positioner found Healthy but its inlet gauge wornout. AFR intenal Plastic wornout. | AFR Filtor replace with new. Control Valve Proper cleaning & lubrication work done. | 350 | Internal | Mr Anuj / Mr V.Singh
78233573e360 | VRL 24-53 :: ZIL/SUG./001 /TCV-203B | ZIL/SUG./001 /TCV-203B | OFF Season | 2025-06-19 |  |  | Control valve Seat & Body found rusty . Positioner found Healthy. AFR gauge wornout | Control Valve Proper cleaning & painting work done. | 400 | Internal | Mr Anuj / Mr V.Singh
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | OFF Season | 17/06/2022 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | OFF Season | 20/06/2023 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | OFF Season | 2024-05-16 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found Healthy . | Control Valve Proper cleaning & lubrication work done. | 120 | Internal | Mr Anuj / Mr V.Singh
dd5f44a6aeea | VRL 24-53 :: ZIL/SUG./001/TCV203-C | ZIL/SUG./001/TCV203-C | OFF Season | 2025-06-28 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found Healthy . | Control Valve Proper cleaning & lubrication work done. | 250 | Internal | Mr Anuj / Mr V.Singh
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | OFF Season | 18/06/2022 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | OFF Season | 22/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | OFF Season | 2024-05-20 |  |  | Control valve Seat & Body found rusty. AFR & Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done. | 120 | Internal | Mr Anuj / Mr V.Singh
7b31872bcb82 | VRL 24-53 :: ZIL/SUG./001/TCV204 | ZIL/SUG./001/TCV204 | OFF Season | 2025-06-30 |  |  | Control valve Seat & Body found rusty. AFR & Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | OFF Season | 2022-06-19 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | OFF Season | 2023-06-12 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | OFF Season | 2024-05-21 |  |  | Control valve Seat & Body found rusty. AFR & Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done. | 120 | Internal | Mr Anuj / Mr V.Singh
59fbb9226a80 | VRL 24-53 :: ZIL/SUG./001/TCV-205 | ZIL/SUG./001/TCV-205 | OFF Season | 2025-06-30 |  |  | Control valve Seat & Body found rusty. Positioner found Healthy. AFR wornout 1nos | Control Valve Proper cleaning & ovrhauling work done.AFR riplace 1nos | 400 | Internal | Mr Anuj / Mr V.Singh
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | OFF Season | 2022-06-19 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | OFF Season | 2023-06-12 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | OFF Season | 2024-05-21 |  |  | Control valve Seat & Body found rusty. AFR & Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done. | 120 | Internal | Mr Anuj / Mr V.Singh
67d4939ac651 | VRL 24-53 :: ZIL/SUG./001/TCV-206 | ZIL/SUG./001/TCV-206 | OFF Season | 2025-06-28 |  |  | Control valve Seat & Body found rusty. AFR & Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | OFF Season | 2022-06-20 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | OFF Season | 2023-06-11 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | OFF Season | 2024-05-20 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done. | 120 | Internal | Mr Anuj / Mr V.Singh
246f47a0663c | VRL 24-53 :: ZIL/SUG./001/TCV-207 | ZIL/SUG./001/TCV-207 | OFF Season | 2025-06-26 |  |  | Control valve Seat & Body found rusty .AFR and dran wornout Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done.AFR dran rplace | 750 | Internal | Mr Anuj / Mr V.Singh
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | OFF Season | 2022-06-02 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | OFF Season | 2023-06-04 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | OFF Season | 2024-05-18 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done. | 120 | Internal | Mr Anuj / Mr V.Singh
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | OFF Season | 2024-05-18 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done. | 120 | Internal | Mr Anuj / Mr V.Singh
694c45876510 | VRL 24-53 :: ZIL/SUG./001/TCV-208 | ZIL/SUG./001/TCV-208 | OFF Season | 2025-06-27 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | OFF Season | 2022-06-02 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | OFF Season | 2023-06-04 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | OFF Season | 2024-05-18 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done. | 120 | Internal | Mr Anuj / Mr V.Singh
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | OFF Season | 2025-06-27 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
50013bc177da | VRL 24-53 :: ZIL/SUG./001/TCV-209 | ZIL/SUG./001/TCV-209 | OFF Season | 2025-08-12 |  |  | Duering Calibration found Relay Not working | Replaced with new Relay valve Calibration work Done. | 4510 | Internal | Mr Anuj / Mr V.Singh
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | OFF Season | 2022-06-03 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | OFF Season | 2023-06-05 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | OFF Season | 2024-07-03 |  |  | Control valve Seat & Body found rusty . AFR pressure gauge damage & Positioner found Healthy. | Control Valve Proper cleaning & overhauling work done. Afr Gauge replace with new spare. | 250 | Internal | Mr Anuj / Mr V.Singh
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | OFF Season | 2025-07-03 |  |  | Control valve Seat & Body found rusty .AFR & sov found Healthy. | Control Valve Proper cleaning work done. | 250 | Internal | Mr Anuj / Mr V.Singh
6706b19850b5 | VRL 24-53 :: ZIL/SUG./001/TCV-OVERHEAD | ZIL/SUG./001/TCV-OVERHEAD | OFF Season | 2026-05-09 |  |  | Control valve Seat & Body found rusty .AFR & sov found Healthy. | Control Valve dismentale cleaning overhauling work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | OFF Season | 2022-06-03 |  |  | Control valve Seat & Body found rusty .AFR & sov found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | OFF Season | 2023-06-05 |  |  | Control valve Seat & Body found rusty .AFR & sov found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | OFF Season | 2024-09-18 |  |  | Control valve Seat & Body found rusty . AFR pressure gauge damage & sov found Healthy. | Control Valve Proper cleaning & overhauling work done. Afr Gauge replace with new spare. | 250 | Internal | Mr Anuj / Mr V.Singh
c308418c135d | VRL 24-53 :: ZIL/SUG./001/B_MOLASSES_CV | ZIL/SUG./001/B_MOLASSES_CV | OFF Season | 2025-07-08 |  |  | Control valve Seat & Body found rusty .AFR & sov found Healthy. | Control Valve Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | OFF Season | 2022-06-04 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | OFF Season | 2023-06-06 |  |  | Control valve Body & Seat worn-out. Postioner , IP & AFR Are Good Condition. | Replace seat with new & cleaning work done. |  | Internal | Mr Anuj / Mr V.Singh
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | OFF Season | 2024-05-16 |  |  | Control valve Body & Seat found ok . Postioner , IP & AFR Are Good Condition. | Control Valve Proper cleaning & ovrhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | OFF Season | 2025-06-27 |  |  | Control valve Body & Seat found ok . Postioner , IP & AFR Are Good Condition.seat bodi wornout 50% | Control Valve Proper cleaning & ovrhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
6f5787014b99 | VRL 24-53 :: ZIL/SUG./001 FCV-205 | ZIL/SUG./001 FCV-205 | OFF Season | 2026-05-13 |  |  | Control valve Seat, Body won-out-100% found rusty. IP & Positioner healthy | Actuator dismentling ,cleaning & overhauling with Valve body repalced with new work are done. | 250 | Internal | Mr. Anirudh / Mr V.Singh
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | OFF Season | 2022-06-05 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | OFF Season | 2023-08-07 |  |  | Control valve found scaled and rusty. | Proper cleaning & overhauling work done. |  | Internal | Mr Anuj / Mr V.Singh
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | OFF Season | 2024-05-06 |  |  | Control valve Body & Seat found ok. Postioner,IP & AFR Are Good Condition. | Control Valve Proper cleaning & ovrhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | OFF Season | 2025-06-26 |  |  | Control valve Body Postioner,IP & AFR Are Good Condition.seat body wor-nout 70 % | Control Valve Proper cleaning & ovrhauling work done. New set body replace | 16500 | Internal | Mr Anuj / Mr V.Singh
a033258467d5 | VRL 24-53 :: ZIL/SUG./001 05FCVB01 | ZIL/SUG./001 05FCVB01 | OFF Season | 2026-05-14 |  |  | Control valve Seat, Body found rusty. IP & Positioner healthy | Actuator,seat dismentling ,cleaning & overhauling work are done. | 250 | Internal | Mr. Anirudh / Mr V.Singh
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | OFF Season | 2022-06-05 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | OFF Season | 2023-08-07 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | OFF Season | 2024-05-17 |  |  | Control valve found scaled and rusty. | Control Valve Proper cleaning & ovrhauling work done. | 100 | Internal | Mr Anuj / Mr V.Singh | Droped leakage
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | OFF Season | 2025-06-26 |  |  | Control valve Body Postioner,IP & AFR Are Good Condition. PTFE seat wornout leak in water trail | Control Valve Proper cleaning & ovrhauling work done. PTFE seat riplace . | 6000 | Internal | Mr Anuj / Mr V.Singh
76d8be18192e | VRL 24-53 :: ZIL/SUG./001/FCV-203 | ZIL/SUG./001/FCV-203 | OFF Season | 2026-05-16 |  |  | Control valve Seat, Body found rusty. IP & Positioner healthy | Actuator,seat dismentling ,cleaning & overhauling work are done. | 250 | Internal | Mr. Anirudh / Mr V.Singh
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | OFF Season | 2022-06-05 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | OFF Season | 2023-08-07 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | OFF Season | 2024-07-13 |  |  | Control valve found scaled and rusty.stem bolt born out | Proper cleaningand stem bolt remove with new | 300 | Internal | Mr Anuj / Mr V.Singh
9ec178bfc889 | VRL 24-53 :: ZIL/SUG./001 /TCV-400 | ZIL/SUG./001 /TCV-400 | OFF Season | 2025-07-04 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 400 | Internal | Mr Anuj / Mr V.Singh
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | OFF Season | 2022-06-05 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | OFF Season | 2023-08-07 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | OFF Season | 2024-07-09 |  |  | Control valve found scaled and rusty. Positioner Gauge wornout. | Control Valve Proper cleaning & ovrhauling work done. Positioner gauge replace with new. | 250 | Internal | Mr Anuj / Mr V.Singh
7748877dd6ba | VRL 24-53 :: ZIL/SUG./001/MOL-CV | ZIL/SUG./001/MOL-CV | OFF Season | 2025-07-04 |  |  | Control valve found scaled and rusty.AFR gauge wornout 2nos | Proper cleaning & painting work done.gauge replace 2nos | 850 | Internal | Mr Anuj / Mr V.Singh
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | OFF Season | 2022-06-06 |  |  | Control valve diaphragm found leakage. Positioner , IP & AFR are healthy. | Repair diaphargm . After overhauling Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | OFF Season | 2023-10-06 |  |  | Control valve diaphragm found worn-out. Positioner , IP & AFR are healthy. | Replace new diaphargm . After overhauling Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | OFF Season | 2024-07-08 |  |  | Control valve tention Spring found worn-out. Positioner, IP healthy. AFR plastic parts worn-out. | Replace old Spare spring . After overhauling Proper cleaning & overhaulilng work done. | 2500 | Internal | Mr Anuj / Mr V.Singh
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | OFF Season | 2025-07-03 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Control Valve Proper cleaning & ovrhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
26bf36a6aff8 | VRL 24-53 :: ZIL/SUG./001 TCV-702 | ZIL/SUG./001 TCV-702 | OFF Season | 2025-04-21 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning & overhauling with checking work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | OFF Season | 2022-07-05 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | OFF Season | 2023-07-20 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | OFF Season | 2024-05-17 |  |  | Control valve found scaled and rusty.Afr Nobe Wornout . | Proper cleaning & Overhauling work done. Afr Knobe replace with spare. | 310 | Internal | Mr Anuj / Mr V.Singh
9975fc2df93f | VRL 24-53 :: ZIL/SUG./001/ FCV_204 | ZIL/SUG./001/ FCV_204 | OFF Season | 2025-07-01 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | OFF Season | 2022-08-05 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | OFF Season | 2023-07-20 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | OFF Season | 2024-05-17 |  |  | Control valve found scaled and rusty. | Proper cleaning & overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
2e8b9febffd0 | VRL 24-53 :: ZIL/SUG./001/VC-CV | ZIL/SUG./001/VC-CV | OFF Season | 2025-07-01 |  |  | Control valve Body Postioner,IP & AFR Are Good Condition. | Control Valve Proper cleaning & ovrhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | OFF Season | 2022-08-06 |  |  | Control valve seat found worn-out. Positioner ,AFR, & IP are healthy position. | Replace seat with new. Proper cleaning & painting work done. | 7000 | Internal | Mr Anuj / Mr V.Singh
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | OFF Season | 19/07/2023 |  |  | Control valve seal retainer found worn-out. Positioner ,AFR, & IP are healthy position. | Seal retainer proper welding & Machining work donee. After overhauling Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | OFF Season | 2024-05-18 |  |  | Control valve seat found worn-out.diaphgram air passing Positioner ,AFR, & IP are healthy position. | Replace seat with Diaphgram . Proper cleaning overhaulin with painting work done. | 15000 | Internal | Mr Anuj / Mr V.Singh
7e56f4827698 | VRL 24-53 :: ZIL/SUG./001 FCV-203 | ZIL/SUG./001 FCV-203 | OFF Season | 2025-07-01 |  |  | Control valve seat Positioner ,AFR, & IP are healthy position. | Control Valve Proper cleaning & ovrhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | OFF Season | 2022-08-07 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | OFF Season | 2023-07-18 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | OFF Season | 2024-05-14 |  |  | Control valve found scaled and rusty. | Proper cleaning & overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | OFF Season | 2025-06-21 |  |  | Control valve found scaled and rusty. | Proper cleaning & overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
51467edc85fe | VRL 24-53 :: ZIL/SUG./001/ SY_B_MOLASSES | ZIL/SUG./001/ SY_B_MOLASSES | OFF Season | 2026-04-22 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning & overhauling with checking work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | OFF Season | 2022-08-08 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | OFF Season | 2023-07-17 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | OFF Season | 2024-07-08 |  |  | Control valve found scaled and rusty. | Proper cleaning & overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | OFF Season | 2025-07-02 |  |  | Control valve found scaled and rusty. | Proper cleaning & overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
f85198df25c9 | VRL 24-53 :: ZIL/SUG./001/E-BOILER-CV | ZIL/SUG./001/E-BOILER-CV | OFF Season | 2026-05-25 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning & overhauling work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | OFF Season | 2022-08-08 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | OFF Season | 2023-07-17 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | OFF Season | 2024-05-15 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | OFF Season | 2025-06-20 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
7a4dbee41d12 | VRL 24-53 :: ZIL/SUG./001/SYRUP-LCV | ZIL/SUG./001/SYRUP-LCV | OFF Season | /05/2026 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning & overhauling work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | OFF Season | 2022-09-06 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  |  | Mr Anuj / Mr V.Singh
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | OFF Season | 22/052023 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  |  | Mr Anuj / Mr V.Singh
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | OFF Season | 2024-05-03 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | OFF Season | 2025-07-10 |  |  | Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | Season | 2026-02-09 |  |  | Control valve not oprated | SOV Set Replaced with new | 1849 | Internal | Mr Anuj / Mr V.Singh
d9e12e66a845 | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV1 | ZIL/SUG./001/SYRUP-CV1 | OFF Season | 2026-05-11 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning overhauling with checking work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | OFF Season | 2022-09-06 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  |  | Mr Anuj / Mr V.Singh
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | OFF Season | 2023-05-22 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  |  | Mr Anuj / Mr V.Singh
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | OFF Season | 2024-05-04 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | OFF Season | 2025-07-10 |  |  | Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
9c36e42133ae | Weingh-54-65 :: ZIL/SUG./001/SYRUP-CV2 | ZIL/SUG./001/SYRUP-CV2 | OFF Season | 2026-05-11 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning overhauling with checking work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | OFF Season | 08/062022 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  |  | Mr Anuj / Mr V.Singh
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | OFF Season | 2023-05-18 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  |  | Mr Anuj / Mr V.Singh
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | OFF Season | 2024-05-03 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning overhauling & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | OFF Season | 2025-07-07 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
f67abe0068a9 | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV1 | ZIL/SUG./001/B-HEAVY-CV1 | OFF Season | 2026-05-12 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning overhauling with checking work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | OFF Season | 2022-08-06 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | OFF Season | 2023-05-19 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | OFF Season | 2024-05-06 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. Found Actuator 1 side tention spring wornout . | Replace 5 Nos actuator tention spring. Control Valve Proper cleaning & overhauling work done. | 3000 | Internal | Mr Anuj / Mr V.Singh
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | OFF Season | 2025-07-09 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. Doom Swetch soft wor-nout. | Control Valve Proper cleaning & painting work done.Doom switch soft replace | 500 | Internal | Mr Anuj / Mr V.Singh
204045dddced | Weingh-54-65 :: ZIL/SUG./001/B-HEAVY-CV2 | ZIL/SUG./001/B-HEAVY-CV2 | OFF Season | 2026-05-12 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning overhauling with checking work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | OFF Season | 2022-09-06 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  |  | Mr Anuj / Mr V.Singh
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | OFF Season | 22/052023 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  |  | Mr Anuj / Mr V.Singh
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | OFF Season | 2024-05-03 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | OFF Season | 2025-07-10 |  |  | Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | Season | 2026-02-09 |  |  | Control valve not oprated | SOV Set Replaced with new | 1849 | Internal | Mr Anuj / Mr V.Singh
d76d3e71fd2e | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV1 | ZIL/SUG./001/C-HEAVY-CV1 | OFF Season | 2026-05-11 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning overhauling with checking work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | OFF Season | 2022-09-06 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  |  | Mr Anuj / Mr V.Singh
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | OFF Season | 22/052023 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  |  | Mr Anuj / Mr V.Singh
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | OFF Season | 2024-05-03 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | OFF Season | 2025-07-10 |  |  | Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | Season | 2026-02-09 |  |  | Control valve not oprated | SOV Set Replaced with new | 1849 | Internal | Mr Anuj / Mr V.Singh
7089d2944e2d | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV2 | ZIL/SUG./001/C-HEAVY-CV2 | OFF Season | 2026-05-11 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning overhauling with checking work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | OFF Season | 2022-08-06 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | OFF Season | 2023-05-19 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. | Control Valve Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | OFF Season | 2024-05-06 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. Found Actuator 1 side tention spring wornout . | Replace 5 Nos actuator tention spring. Control Valve Proper cleaning & overhauling work done. | 3000 | Internal | Mr Anuj / Mr V.Singh
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | OFF Season | 2025-07-09 |  |  | Control valve Seat & Body found rusty .AFR & Dome Switch found Healthy. Doom Swetch soft wor-nout. | Control Valve Proper cleaning & painting work done.Doom switch soft replace | 500 | Internal | Mr Anuj / Mr V.Singh
b562ab37e218 | Weingh-54-65 :: ZIL/SUG./001/C-HEAVY-CV3 | ZIL/SUG./001/C-HEAVY-CV3 | OFF Season | 2026-05-12 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning overhauling with checking work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | OFF Season | 2022-05-16 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | OFF Season | 2023-06-18 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | OFF Season | 22/072024 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
106efa60c6a7 | Transient Heater 66-73 :: ZIL/SUG./001/C.CFM-01 | ZIL/SUG./001/C.CFM-01 | OFF Season | 2025-07-16 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | OFF Season | 2022-05-16 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | OFF Season | 2023-06-18 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | OFF Season | 22/072024 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
4cf80560f098 | Transient Heater 66-73 :: ZIL/SUG./002/C.CFM-02 | ZIL/SUG./002/C.CFM-02 | OFF Season | 2025-07-16 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | OFF Season | 2022-05-16 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | OFF Season | 2023-06-18 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | OFF Season | 22/072024 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
e3012d82779e | Transient Heater 66-73 :: ZIL/SUG./003/C.CFM-03 | ZIL/SUG./003/C.CFM-03 | OFF Season | 2025-07-16 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | OFF Season | 2022-05-16 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | OFF Season | 2023-06-18 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | OFF Season | 22/072024 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
206559743ac0 | Transient Heater 66-73 :: ZIL/SUG./004/C1.CFM-04 | ZIL/SUG./004/C1.CFM-04 | OFF Season | 2025-07-18 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | OFF Season | 2022-05-26 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | OFF Season | 2023-06-10 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | OFF Season | 19/072024 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
a070470bf94e | Transient Heater 66-73 :: ZIL/SUG./005/C1.CFM-05 | ZIL/SUG./005/C1.CFM-05 | OFF Season | 2025-07-18 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
40579c9b934c | Transient Heater 66-73 :: ZIL/SUG./006/C.CFM-06 | ZIL/SUG./006/C.CFM-06 | OFF Season | 2025-07-17 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | OFF Season | 2022-05-26 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | OFF Season | 2023-06-10 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | OFF Season | 19/072024 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | OFF Season | 2025-07-18 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 300 | Internal | Mr Anuj / Mr V.Singh
1482438a94b5 | Transient Heater 66-73 :: ZIL/SUG./007/IJP-1 | ZIL/SUG./007/IJP-1 | OFF Season | 2026-05-22 |  |  | Control valve found scaled and rusty. | Control valve seat ,AFR SOV Proper cleaning & overhauling work done. | 350 | Internal | Mr Anuj / Mr V.Singh
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | OFF Season | 2022-05-26 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | OFF Season | 2023-06-10 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | OFF Season | 2024-07-19 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
4601d338f802 | Transient Heater 66-73 :: ZIL/SUG./008 | ZIL/SUG./008 | OFF Season | 2025-06-18 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | OFF Season | 2022-05-21 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | OFF Season | 2023-06-11 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 150 | Internal | Mr Anuj / Mr V.Singh
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | OFF Season | 13/072024 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
c4c2eefab033 | Transient Heater 66-73 :: ZIL/SUG./001 /TCV | ZIL/SUG./001 /TCV | OFF Season | 2025-07-08 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. | 250 | Internal | Mr Anuj / Mr V.Singh
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | OFF Season | 2022-06-23 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | OFF Season | 2023-07-20 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | OFF Season | 2024-07-25 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
af899fc65ee8 | DS Flow Meter-31 :: ZIL/SUG./01/FT_201A | ZIL/SUG./01/FT_201A | OFF Season | 2025-07-16 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | OFF Season | 2022-06-23 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | OFF Season | 2023-07-20 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | OFF Season | 2024-07-26 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
ffbe763f258c | DS Flow Meter-31 :: ZIL/SUG./01/FT_204 | ZIL/SUG./01/FT_204 | OFF Season | 2025-07-15 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | OFF Season | 2022-06-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | OFF Season | 2022-07-21 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | OFF Season | 2024-07-26 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
85491c06d1fb | DS Flow Meter-31 :: ZIL/SUG./01/FT_205 | ZIL/SUG./01/FT_205 | OFF Season | 2025-07-12 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | OFF Season | 2022-06-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | OFF Season | 2023-07-21 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | OFF Season | 2024-07-25 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
c88545950e1c | DS Flow Meter-31 :: ZIL/SUG./01/FT_601 | ZIL/SUG./01/FT_601 | OFF Season | 2025-07-13 |  |  | OK | Transmitter cleaning, manifold checking & flusing work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | OFF Season | 2022-06-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | OFF Season | 2023-07-21 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | OFF Season | 2024-07-25 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
25522698de7b | DS Flow Meter-31 :: ZIL/SUG./01/FT-206 | ZIL/SUG./01/FT-206 | OFF Season | 2025-07-17 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | OFF Season | 2022-06-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | OFF Season | 2023-07-21 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | OFF Season | 2024-07-22 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
09140bce6549 | DS Flow Meter-31 :: ZIL/SUG./01/FT-207 | ZIL/SUG./01/FT-207 | OFF Season | 2024-07-17 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | OFF Season | 2022-06-25 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | OFF Season | 2023-07-22 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | OFF Season | 2024-07-22 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
1d899fefa475 | DS Flow Meter-31 :: ZIL/SUG./Vacuum-FM-2 | ZIL/SUG./Vacuum-FM-2 | OFF Season | 2025-07-19 |  |  | teflon liner crack found one siderepaired with araldide | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | OFF Season | 2022-06-25 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | OFF Season | 2023-07-22 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | OFF Season | 2024-07-18 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
e13c55910104 | DS Flow Meter-31 :: ZIL/SUG./01/COND.-FM | ZIL/SUG./01/COND.-FM | OFF Season | 2025-07-15 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | OFF Season | 2022-06-25 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | OFF Season | 2023-07-22 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | OFF Season | 2024-07-20 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
d301d63c057c | DS Flow Meter-31 :: ZIL/SUG./01/B-HEAVY-FM | ZIL/SUG./01/B-HEAVY-FM | OFF Season | 2025-07-14 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | OFF Season | 2022-06-25 |  |  | OK | flow tube cleaning work done | 100 | Internal | Mr Anuj / Mr V.Singh
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | OFF Season | 2023-07-22 |  |  | OK | flow tube cleaning work done | 100 | Internal | Mr Anuj / Mr V.Singh
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | OFF Season | 2024-07-19 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
010c97204f9c | DS Flow Meter-31 :: ZIL/SUG./01/ETP-SPRAY-O/L | ZIL/SUG./01/ETP-SPRAY-O/L | OFF Season | 2025-07-17 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | OFF Season | 2022-06-25 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | OFF Season | 2023-07-22 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | OFF Season | 2024-07-20 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
614469c06d4b | DS Flow Meter-31 :: ZIL/SUG./01/OVER-HEAD/SPRAY-FM | ZIL/SUG./01/OVER-HEAD/SPRAY-FM | OFF Season | 2025-07-21 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | OFF Season | 2022-06-26 |  |  | OK | flow tube cleaning work done | 100 | Internal | Mr Anuj / Mr V.Singh
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | OFF Season | 2023-07-23 |  |  | OK | flow tube cleaning work done | 100 | Internal | Mr Anuj / Mr V.Singh
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | OFF Season | 2024-07-23 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
078132aed9f9 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-REF-CTFM | ZIL/SUG./01/ETP-O/L-REF-CTFM | OFF Season | 2025-07-17 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | OFF Season | 2022-06-26 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | OFF Season | 2023-07-23 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | OFF Season | 2024-07-23 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | OFF Season | 2025-05-02 |  |  | The display was turned off onchecking the power supplycard was found to be faulty | Transmitter & flow tube cleaning work, electronic card was replaced with repired transmitter | 5000 | external | Mr Anuj / Mr V.Singh
35e024b60280 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-I/L-FM | ZIL/SUG./01/ETP-I/L-FM | OFF Season | 2025-07-19 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work are completed. | 100 | Internal | Mr Anuj / Mr V.Singh
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | OFF Season | 2022-06-26 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | OFF Season | 2023-07-23 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | OFF Season | 2024-07-20 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
63bac132e48d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-O/L-FM | ZIL/SUG./01/ETP-O/L-FM | OFF Season | 2025-07-21 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | OFF Season | 2022-06-26 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | OFF Season | 2023-07-23 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | OFF Season | 2024-07-21 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
b6ba0b086fba | DS Flow Meter-31 :: ZIL/SUG./01/ETP-B-VER-FM | ZIL/SUG./01/ETP-B-VER-FM | OFF Season | 2025-07-21 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | OFF Season | 2022-06-26 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | OFF Season | 2023-07-23 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
ca56812f6c79 | DS Flow Meter-31 :: ZIL/SUG./01/ETP-HYDRO-FM | ZIL/SUG./01/ETP-HYDRO-FM | OFF Season | 2024-07-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | OFF Season | 2022-06-27 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | OFF Season | 2023-07-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | OFF Season | 2024-07-23 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
f8d36da8154c | DS Flow Meter-31 :: ZIL/SUG./01/CT-FM | ZIL/SUG./01/CT-FM | OFF Season | 2025-07-22 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | OFF Season | 2022-06-27 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | OFF Season | 2023-07-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | OFF Season | 2024-07-29 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
31fc811e7d98 | DS Flow Meter-31 :: ZIL/SUG./01/SURUP-MASS | ZIL/SUG./01/SURUP-MASS | OFF Season | 08 to 22/07/2025 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 250 | Internal | Mr Anuj / Mr V.Singh | Inside tube 3MM syrup Layer
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | OFF Season | 2022-06-27 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | OFF Season | 2023-07-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | OFF Season | 2024-07-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
7f8f018f4d99 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-1 | ZIL/SUG./01/B.CONT.PAN-FM-1 | OFF Season | 2025-07-19 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | OFF Season | 2022-06-27 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | OFF Season | 2023-07-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | OFF Season | 2024-07-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
039a284eb2db | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-2 | ZIL/SUG./01/B.CONT.PAN-FM-2 | OFF Season | 2025-07-18 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | OFF Season | 2022-06-27 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | OFF Season | 2023-07-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | OFF Season | 2024-07-29 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
90f6c0ce2d60 | DS Flow Meter-31 :: ZIL/SUG./01/B.CONT.PAN-FM-3 | ZIL/SUG./01/B.CONT.PAN-FM-3 | OFF Season | 2025-07-19 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | OFF Season
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | OFF Season
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | OFF Season
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | OFF Season
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | OFF Season
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | OFF Season
c40b1cbeacec | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.020.01 | ZIL/SUG./01/75.FT.020.01 | OFF Season
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | OFF Season
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | OFF Season
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | OFF Season
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | OFF Season
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | OFF Season
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | OFF Season
eeef619dc388 | DS Flow Meter-31 :: ZIL/SUG./01/75.FT.035.01. | ZIL/SUG./01/75.FT.035.01. | OFF Season
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | OFF Season
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | OFF Season
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | OFF Season
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | OFF Season
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | OFF Season
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | OFF Season
1692889d20f9 | DS Flow Meter-31 :: ZIL/SUG./01/Centric-01-FM | ZIL/SUG./01/Centric-01-FM | OFF Season
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | OFF Season
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | OFF Season
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | OFF Season
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | OFF Season
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | OFF Season
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | OFF Season
16c61e481883 | DS Flow Meter-31 :: ZIL/SUG./01//Centric-02-FM | ZIL/SUG./01//Centric-02-FM | OFF Season
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | OFF Season
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | OFF Season
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | OFF Season
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | OFF Season
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | OFF Season
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | OFF Season
8f72e7e40ccc | DS Flow Meter-31 :: ZIL/SUG./Decanter-HWFM | ZIL/SUG./Decanter-HWFM | OFF Season
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | OFF Season | 2024-05-24 |  |  | Duering checking SOV 2 nos & pressure switch found OK | SOV & Pressure switch cleaning & Overhauling work are done | 250 | Internal | Mr Anuj / Mr V.Singh
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | OFF Season | 2025-04-14 |  |  | Duering checking SOV 2 nos & pressure switch found OK | SOV & Pressure switch cleaning & Overhauling work are done | 100 | Internal | Mr Anuj / Mr V.Singh
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | OFF Season | 2025-11-29 |  |  | Duering checking SOV 2 nos & pressure switch found OK with NRV not working | SOV & Pressure switch cleaning & Overhauling work are done with 04 nos NRV Replaced | 4000 | Internal | Mr Anuj / Mr V.Singh
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | OFF Season | 2026-02-06 |  |  | Duering checking SOV 2 nos & pressure switch found oil Pump not working | SOV & Pressure switch cleaning & Overhauling work are done oil pump replace with new | 21500 | Internal | Mr Anuj / Mr V.Singh
611ec01c83dd | SEDL14 :: ZIL/SUG./001/ACCUM | ZIL/SUG./001/ACCUM | OFF Season | 2026-06-04 |  |  | Duering checking SOV 2 no & pressure switch found OK | SOV & Pressure switch cleaning & Overhauling work are done | 200 | Internal | Mr A. Varma / Mr V.Singh
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | OFF Season | 2024-05-24 |  |  | Duering checking found spare damage.Flat seal 16no,Doom nut 16 Doom nut o-ring 16 no, no SOV 2 no Do nozzle jet nozzle 1 no wornout | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed.DO,DC, Jet nozzle,NRV checking, cleaning & Overhauling work are completed. Flat seal ,doomnut ,doomnut o-ring profile gaskit & Do nozzle replaced with new. | 3322 | Internal | Mr Anuj / Mr V.Singh
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | OFF Season | 2025-04-14 |  |  | Duering checking found spare damage.Flat seal 16no,Doom nut 16 Doom nut o-ring 16 no, SOV 2 no Do nozzle 1 no Jet nozzle 1no wornout | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed.DO,DC, Jet nozzle,NRV checking, cleaning & Overhauling work are completed. Flat seal ,doom nut ,doom nut o-ring profile gasket & Do nozzle 'jet nozzle replaced with new. | 7394 | Internal | Mr Anuj / Mr V.Singh
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | Season | 2025-11-29 |  |  | Vacuum increasing in quad | dome nut-06,Flate seal-06 & Oring-06 replaced with new | 450 | Internal | Mr Anuj / Mr V.Singh
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | Season | 2026-02-06 |  |  | Vacuum increasing in quad | Jet nozil 2 Dome nut-12,Flate seal-12 & Oring-12 replaced with new | 2900 | Internal | Mr Anuj / Mr V.Singh
4edea75d6371 | SEDL14 :: ZIL/SUG./001/EVP- A SET | ZIL/SUG./001/EVP- A SET | OFF Season | 2026-06-04 |  |  | Duering Overhauling checking found damage.Flat seal 05 nos,Doom nut 03 nos. & NRV Zet nozzle 01 nos. | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. jet NRV nozzle replaced with new. | 1200 | Internal | Mr A. Varma / Mr V.Singh
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | OFF Season | 2024-05-31 |  |  | Duering checking found spare damage.Flat seal 17 no,Doom nut 7 Doom nut oring 7 no,lock nut 4 no sov 1no profile gaskit 4no hosepipe2 meter jet nozzle 5 no wornout | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. Flat seal ,doomnut ,doomnut o-ring profile gaskit hosepipe & jet nozzle replaced with new. | 8570 | Internal | Mr Anuj / Mr V.Singh
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | OFF Season | 2025-04-15 |  |  | Duering checking found spare damage.Flat seal 6 no,Doom nut 6Doom nut oring 6 no, sov 1no Do nzzle 2 no wornout Nrv nozzle 1no | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. Flat seal ,doomnut ,doomnut o-ring Do nozzle nrv nozzle sov replaced with new. | 5800 | Internal | Mr Anuj / Mr V.Singh
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | Season | 2025-11-19 |  |  | Vacuum increasing in quad | Zet-04 flat seal-04,dome nut-04,domnut oring-04 replaced with new | 4300 | Internal | Mr Anuj / Mr V.Singh
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | Season | 2025-12-10 |  |  | Vacuum increasing in quad | Zet-03,flat seal-06,dome nut-06,domnut oring-06 replaced with new | 3450 | Internal | Mr Anuj / Mr V.Singh
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | Season | 2026-02-14 |  |  | Vacuum increasing in quad | Zet-02,DC -01 DO-02 flat seal-12,dome nut-12,domnut oring-12 replaced with new | 4900 | Internal | Mr Anuj / Mr V.Singh
70b4794bb0de | SEDL14 :: ZIL/SUG./001/ EVP- B SET | ZIL/SUG./001/ EVP- B SET | OFF Season | 2026-06-04 |  |  | Duering Overhauling checking found damage.Flat seal 05 nos,Doom nut 03 nos. hosepipe 1/2 mtr. & DC nozzle 01 nos. | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. DC nozzle replaced with new. | 1500 | Internal | Mr A. Varma / Mr V.Singh
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | OFF Season | 2024-05-23 |  |  | Duering checking found spare damage.Flat seal 14 no,doomnut 10 doomnut o-ring 10 no, locknut 4 no sov 1 no profile gaskit 8 no hose pipe 2 meter jet nozzle 2 no wornout | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. Flat seal ,doomnut ,doomnut o-ring profile gaskit hosepipe & jet nozzle replaced with new. | 4126 | Internal | Mr Anuj / Mr V.Singh
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | OFF Season | 2025-04-12 |  |  | Duering checking found spare damage.Flat seal 08 no,doomnut 08 doomnut o-ring 08 no, locknut 1 sov fitting nut 1 no sov 1 no jet nozzle 3 no wornout dc nozzle 1no sov 1no | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. Flat seal ,doomnut ,doomnut o-ring lock nut sov fitting nut jet nozzle dc nozzil replaced with new. | 5067 | Internal | Mr Anuj / Mr V.Singh
dd636e16205b | SEDL14 :: ZIL/SUG./001/DS EVP- C SET | ZIL/SUG./001/DS EVP- C SET | OFF Season | 2026-06-03 |  |  | Duering Overhauling checking found damage.Flat seal 03 nos,Doom nut 05 nos. | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. Flat seal & ndome nut replaced with new. | 400 | Internal | Mr A. Varma / Mr V.Singh
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | OFF Season | 2024-05-20 |  |  | Duering checking found spare damage.Flat seal 10 no,doomnut 8 no,Flat seal oring 8 no wornout. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. flat seal ,doomnut ,flat o-ring replaced with new. | 650 | Internal | Mr Anuj / Mr V.Singh
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | OFF Season | 2025-04-18 |  |  | Duering checking found spare damage.sov 2 nos DO-01 nos ,NRV Cyl-01 nos , 3 Mtr hosepipe,PVC-T 02 nos,doomnut-15 ,flat seal-15 nos ,oring 15 locknut-02,profile gaisket-02 found damage. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed.SOV-02 nos DO-01 nos ,NRV Cyl-01 nos , 3 Mtr hosepipe,PVC-T 02 nos,doomnut-05 ,flat seal-14 nos ,locknut-02,profile gaisket-02 replace with new | 9220 | Internal | Mr Anuj / Mr V.Singh
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | Season | 2025-11-20 |  |  | Vacuum increasing in Pan | DO-01 & Tube 02 Mtr replaced with new | 1700 | Internal | Mr Anuj / Mr V.Singh
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | Season | 2025-12-16 |  |  | Vacuum increasing in Pan | Tube-3/8 03 Mtr. replaced with new | 950 | Internal | Mr Anuj / Mr V.Singh
6ffb952cc49e | SEDL14 :: ZIL/SUG./001/Pan-1 | ZIL/SUG./001/Pan-1 | OFF Season | 2026-05-29 |  |  | Duering Overhauling checking found damage.Hosepipe-1/2 mtr.Doom nut 05 nos , DO Nozzle 02 nos, & Jet 02 Nozzle nos | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. Flat seal & dome nut with nozzle replaced with new. | 4000 | Internal | Mr A. Varma / Mr V.Singh
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | OFF Season | 2024-05-21 |  |  | Duering checking found spare damage.Flat seal 14 nos, doomnut 11 nos, doomnut o-ring 11 nos ,locknut 8 nos wornout. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. flat seal ,doomnut ,doomnut o-ring & locknut replaced with new. | 1664 | Internal | Mr Anuj / Mr V.Singh
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | OFF Season | 2025-04-17 |  |  | Duering checking found spare damage. DO relay-01nos,SOV-01 nos,housepipe-03 Mtr flatseal-20 nos,doomnut & Oring-20 nos profile gaisket-05 | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed DO relay-01nos,SOV-01 nos,housepipe-03 Mtr flatseal-20 nos,doomnut & Oring-20 nos profile gaisket-05 nos replace with new | 5896 | Internal | Mr Anuj / Mr V.Singh
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | Season | 2025-11-05 |  |  | Vacuum increasing in Pan | Zet-02 & DC Nazzal 1no,flat seal-02,dome nut-02 with O ring-02 replaced with new | 3150 | Internal | Mr Anuj / Mr V.Singh
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | Season | 2025-12-07 |  |  | Vacuum increasing in Pan | Zet-02 flat seal-06,dome nut-06 with O ring-06 replaced with new | 2450 | Internal | Mr Anuj / Mr V.Singh
f527c311e5cd | SEDL14 :: ZIL/SUG./001/Pan-2 | ZIL/SUG./001/Pan-2 | OFF Season | 2026-05-30 |  |  | Duering Overhauling checking found damage.Hosepipe-1/2 mtr.Doom nut 05 nos , DO Nozzle 02 nos, & Jet 02 Nozzle nos | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. Flat seal & dome nut with nozzle replaced with new. | 4000 | Internal | Mr A. Varma / Mr V.Singh
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | OFF Season | 2024-05-22 |  |  | Flat seal 4 nos, doomnut 8 nos doomnut o-ring 8 nos, DO nozzle 2 nos wornout. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. flat seal ,doomnut ,doomnut o-ring & DO replaced with new. | 2334 | Internal | Mr Anuj / Mr V.Singh
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | OFF Season | 2025-04-16 |  |  | Duering checking found spare damage Do relay-02 nos, housepipe-02 Mtr flatseal-14 nos,doomnut & Oring-14 nos profile gaisket-02 nos | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed DO relay-02 nos, housepipe-02 Mtr flatseal-14 nos,doomnut & Oring-14 nos profile gaisket-02 nos replace with new | 2882 | Internal | Mr Anuj / Mr V.Singh
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | Season | 2025-12-03 |  |  | Vacuum increasing in Pan | SOV plunger-02 replaced with new | 650 | Internal | Mr Anuj / Mr V.Singh
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | Season | 2025-12-22 |  |  | Vacuum increasing in Pan | DO-01 & Zet-03 flat seal-08,dome nut-08 with O ring-08 replaced with new | 4600 | Internal | Mr Anuj / Mr V.Singh
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | Season | 2025-01-22 |  |  | Vacuum increasing in Pan | SOV plunger-02 replaced with new | 1400 | Internal | Mr Anuj / Mr V.Singh
ba09f15b928b | SEDL14 :: ZIL/SUG./001/Pan-4 | ZIL/SUG./001/Pan-4 | OFF Season | 2026-06-01 |  |  | Duering Overhauling checking found damage.Hosepipe-1/2 mtr.Doom nut 05 nos , DC Nozzle 01 nos, & Jet 01 Nozzle nos | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. Flat seal & dome nut with nozzle replaced with new. | 2400 | Internal | Mr A. Varma / Mr V.Singh
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | OFF Season | 2024-05-22 |  |  | Flat seal 4 nos, doomnut 8 nos, doomnut o-ring 8 nos, DO nozzle 2 nos wornout. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. flat seal ,doomnut ,doomnut o-ring & DO replaced with new. | 2334 | Internal | Mr Anuj / Mr V.Singh
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | OFF Season | 2025-04-19 |  |  | Duering checking found spare damage.Jet relay-02 nos, housepipe-01 Mtr ,Jet nozzle-01 nos , flatseal-10 nos,doomnut & Oring-10 nos profile gaisket-05 nos.NRV broken | DO,DC, Jet nozzle,NRV riplace with new cleaning & overhauling work are completed DO relay-02 nos, housepipe-01 Mtr ,Jet nozzle-01 nos , flatseal-10 nos,doomnut & Oring-10 nos profile gaisket-05 nos replace with new | 8478 | Internal | Mr Anuj / Mr V.Singh
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | Season | 2025-12-17 |  |  | Vacuum increasing in Pan | Zet Nozzle-04,flat seal-13,dome nut-13,domnut oring-13 replaced with new | 4975 | Internal | Mr Anuj / Mr V.Singh
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | Season | 2025-12-18 |  |  | Vacuum increasing in Pan | DO Nozzle-01,flat seal-06,dome nut-06,domnut oring-06 replaced with new | 1450 | Internal | Mr Anuj / Mr V.Singh
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | Season | 2026-01-03 |  |  | Vacuum increasing in Pan | DO Nozzle-02,flat seal-08,dome nut-06,domnut oring-06 replaced with new | 2500 | Internal | Mr Anuj / Mr V.Singh
5eb44c927ceb | SEDL14 :: ZIL/SUG./001/Pan-6 | ZIL/SUG./001/Pan-6 | OFF Season | 2026-06-08 |  |  | Duering Overhauling checking found damage.Hosepipe-1/2 mtr.Doom nut 05 nos benjo bolt 01 nos , DO Nozzle 01 nos, & Jet 01 Nozzle nos | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. Flat seal & dome nut with nozzle replaced with new. | 2500 | Internal | Mr A. Varma / Mr V.Singh
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | OFF Season | 2024-06-15 |  |  | Flat seal 10 nos, doomnut 10 nos, doomnut o-ring 10 nos,locknut 06 nos,tee 05 nos DO nozzle 6 nos,DC nozzle 01 no,Jet nozzle 2 nos & hosepipe 1meter wornout. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. flat seal ,doomnut ,doomnut o-ring ,tee,locknut, DO ,DC,Jet nozzle & hoseipe replaced with new. | 9778 | Internal | Mr Anuj / Mr V.Singh
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | OFF Season | 2025-04-21 |  |  | Duering checking found spare damage.DO relay-02 nos, housepipe-01 Mtr Tee-12 Nos, flatseal-06 nos,doomnut & Oring-06 nos ,lock nut-02 nos profile gaisket-03 nos. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed DO relay-02 nos, housepipe-01 Mtr Tee-12 Nos, flatseal-06 nos,doomnut & Oring-06 nos ,lock nut-02 nos profile gaisket-03 nos replace with new | 2452 | Internal | Mr Anuj / Mr V.Singh
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | Season | 2026-01-02 |  |  | Vacuum increasing in Pan | Zet-02,flat seal-02,dome nut-06,domnut oring-06 replaced with new | 2350 | Internal | Mr Anuj / Mr V.Singh
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | Season | 2026-02-06 |  |  | Vacuum increasing in Pan | Zet-03,flat seal-03,dome nut-06,domnut oring-06 replaced with new | 3375 | Internal | Mr Anuj / Mr V.Singh
bc495932d540 | SEDL14 :: ZIL/SUG./001/Pan-7 | ZIL/SUG./001/Pan-7 | OFF Season | 2026-06-09 |  |  | Duering Overhauling checking found damage.Hosepipe-1/2 mtr.Doom nut 05 nos O ring 05 nos , DO Nozzle 01 nos, & Jet 01 Nozzle nos | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. Flat seal & dome nut with nozzle replaced with new. | 2700 | Internal | Mr A. Varma / Mr V.Singh
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | OFF Season | 2024-07-18 |  |  | Flat seal 6 nos, doomnut 6 nos, doomnut o-ring 6 nos, DO nozzle 6 nos,DC nozzle 01 no & Jet nozzle 3 nos wornout. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. flat seal ,doomnut ,doomnut o-ring , DO ,DC & Jet nozzle replaced with new. | 9702 | Internal | Mr Anuj / Mr V.Singh
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | OFF Season | 2025-04-22 |  |  | Duering checking found spare damage.DO nozzle-03 nos, housepipe-01 Mtr Tee-02 Nos, flatseal-12 nos,doomnut 12 & Oring-12 nos ,lock nut-06 nos profile gaisket-02 nos | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed DO nozzle-03 nos, housepipe-01 Mtr Tee-02 Nos, flatseal-12 nos,doomnut & Oring-12 nos ,lock nut-06 nos profile gaisket-02 nos replace with new | 4500 | Internal | Mr Anuj / Mr V.Singh
edb78c39280b | SEDL14 :: ZIL/SUG./001/Pan-8 | ZIL/SUG./001/Pan-8 | OFF Season | 2026-06-10 |  |  | Duering Overhauling checking found damage.flat seal 05 nos. Doom nut 05 nos O ring 05 nos , DO Nozzle 01 nos, & Jet 01 Nozzle nos | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. Flat seal & dome nut with nozzle replaced with new. | 2400 | Internal | Mr A. Varma / Mr V.Singh
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | OFF Season | 2024-06-17 |  |  | Flat seal 12 nos, doomnut 12 nos, doomnut o-ring 12 nos,DO nozzle-02 nos , Jet nozzle 2 nos 2 meter hosepipe wornout. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. flat seal ,doomnut ,doomnut o-ring , DO ,DC & Jet nozzle replaced with new. | 5072 | Internal | Mr Anuj / Mr V.Singh
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | OFF Season | 2025-04-25 |  |  | Duering checking found spare damage. Jet nozzle-01 nos, nrv cylinder 2 housepipe-01 Mtr , flatseal-14 nos,doomnut & Oring-14 nos ,lock nut-04 nos | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed Jet nozzle-01 nos, housepipe-01 Mtr , flatseal-14 nos,doomnut & Oring-14 nos ,lock nut-04 nos replace with new. | 4600 | Internal | Mr Anuj / Mr V.Singh
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | Season | 2025-11-07 |  |  | Vaccuam tx reading error. faced | Tx. replaced with new | 12695 | Internal | Mr Anuj / Mr V.Singh
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | Season | 2025-12-05 |  |  | Nozzal Piston closing problem faced | DO-02,Zet-02 & SOV plunger-02 replaced with new | 5400 | Internal | Mr Anuj / Mr V.Singh
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | Season | 2026-01-02 |  |  | Nozzal Piston closing problem faced | Zet-03,flat seal-03,dome nut-03,domnut oring replaced with new | 3225 | Internal | Mr Anuj / Mr V.Singh
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | Season | 2026-01-29 |  |  | Vacuum increasing in Pan | Zet-04,flat seal-04,dome nut-04,Lock nut1 SOV Plunger 1replaced with new | 5000 | Internal | Mr Anuj / Mr V.Singh
b58d9fe6d056 | SEDL14 :: ZIL/SUG./001/Pan-9 | ZIL/SUG./001/Pan-9 | OFF Season | 2026-06-13 |  |  | Duering Overhauling checking found damage.flat seal 12 nos. Doom nut 12 nos O ring 12 nos & Jet 02 Nozzle nos | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. Flat seal & dome nut with nozzle replaced with new. | 3500 | Internal | Mr A. Varma / Mr V.Singh
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | OFF Season | 2024-07-18 |  |  | Flat seal 04 nos, doomnut 04 nos, doomnut o-ring 04 nos,DO nozzle-01 nos , DC nozzle 1 no Jet nozzle 1 nos ,SOV plunger nos 02 wornout. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. flat seal ,doomnut ,doomnut o-ring , DO ,DC & Jet nozzle SOV plunger replaced with new. | 4545 | Internal | Mr Anuj / Mr V.Singh
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | OFF Season | 2025-04-23 |  |  | Duering checking found spare damage.DO nozzle-01 nos,SOV-01 nos, housepipe-02 Mtr Tee-02 Nos, flatseal-16 nos,doomnut & Oring-16 nos ,lock nut-04 nos. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed DO nozzle-01 nos,SOV-01 nos, housepipe-02 Mtr Tee-02 Nos, flatseal-16 nos,doomnut & Oring-16 nos ,lock nut-04 nos. replace with new | 5360 | Internal | Mr Anuj / Mr V.Singh
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | Season | 2025-12-15 |  |  | Vacuum increasing in Pan | Tube-3/8 02 Mtr. replaced with new | 634 | Internal | Mr Anuj / Mr V.Singh
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | Season | 2025-12-22 |  |  | Vacuum increasing in Pan | DO Nazzal-02& Zet-04,flat seal-12,dome nut-12,Lock nut with O ring-12 replaced with new | 6900
f2537d4a3330 | SEDL14 :: ZIL/SUG./001/Pan-10 | ZIL/SUG./001/Pan-10 | OFF Season | 2026-06-11 |  |  | Duering Overhauling checking found damage.flat seal 07 nos. Doom nut 07,benjo bolt 01 nos. & hosepipe 1/2 mtr. | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. Flat seal & dome nut with nozzle replaced with new. | 800 | Internal | Mr A. Varma / Mr V.Singh
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | OFF Season | 2024-07-20 |  |  | Flat seal 15 nos, doomnut 15 nos, doomnut o-ring 15 nos,locknut 08 nos ,DO nozzle-03 nos ,DC nozzle 03 nos Jet nozzle 3 nos,ball valve 3/8'',SOV fitting wornout. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. flat seal ,doomnut ,doomnut o-ring ,locknut, DO ,DC & Jet nozzle replaced with new. | 13079 | Internal | Mr Anuj / Mr V.Singh | Work is not completed due to vapor line cut
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | OFF Season | 2025-04-29 |  |  | Duering checking found spare damage.DC nozzle-02 nos,Jet Nozzle-06 nos,SOV-01 nos, housepipe-02 Mtr Tee-05 Nos, flatseal-20 nos,doomnut & Oring-20 nos ,lock nut-06 nos. profile gaiskit-02 | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed DC nozzle-02 nos,Jet Nozzle-06 nos,SOV-01 nos, housepipe-02 Mtr Tee-05 Nos, flatseal-20 nos,doomnut & Oring-20 nos ,lock nut-06 nos. profile gaiskit-02 replace with new | 12275 | Internal | Mr Anuj / Mr V.Singh
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | Season | 25.12.2025 |  |  | Vacuum increasing in Pan | DO Nozzal-1 With Dome nut -08 nos Replaced with new. |  | Internal | Mr Anuj / Mr V.Singh
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | Season | 2026-01-16 |  |  | Vacuum increasing in Pan | DO Nozzle-01,flat seal-04,dome nut-04,domnut oring-04 replaced with new |  | Internal | Mr Anuj / Mr V.Singh
14cdf83b5c38 | SEDL14 :: ZIL/SUG./001/Pan-11 | ZIL/SUG./001/Pan-11 | OFF Season | 16/17 /06/2026 |  |  | Duering Overhauling checking found damage.flat seal 07 nos. Doom nut 10,lock nut-03 nos. DO-01,DC-01 ,Jet-01 nozzle dfound damage. | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. Flat seal & dome nut with nozzle replaced with new. | 3500 | Internal | Mr A. Varma / Mr V.Singh
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | OFF Season | 2024-06-20 |  |  | Flat seal 12 nos, doomnut 40 nos, doomnut o-ring 40 nos,DO nozzle-03 nos ,DC nozzle 03 nos Jet nozzle 3 nos wornout. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. flat seal ,doomnut ,doomnut o-ring , DO ,DC & Jet nozzle replaced with new. | 10551 | Internal | Mr Anuj / Mr V.Singh
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | OFF Season | 25/04/2025 to 27/07 2025 |  |  | Duering checking found spare damage. DC nozzle-01 nos,DO nozzle-01 nos ,Jet Nozzle-03 nos, housepipe-01 Mtr Tee-05 Nos, flatseal-20 nos,doomnut & Oring-20 nos ,lock nut-04 nos.NRV broken | DO,DC, Jet nozzle,NRV riplace with new, cleaning & overhauling work are completed DC nozzle-01 nos,DO nozzle-01 nos ,Jet Nozzle-03 nos, housepipe-01 Mtr Tee-05 Nos, flatseal-20 nos,doomnut & Oring-20 nos ,lock nut-04 nos. replace with new | 11950 | Internal | Mr Anuj / Mr V.Singh
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | Season | 2025-11-15 |  |  | Vaccuam Up/dowen | DO Nozzle-03,flat seal-10,dome nut-10,domnut oring-10 replaced with new | 3750 | Internal | Mr Anuj / Mr V.Singh
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | Season | 2026-01-03 |  |  | Vacuum increasing in Pan | Jet nozil-6eal-12,dome nut-12,domnut oring-12 replaced with new | 6900 | Internal | Mr Anuj / Mr V.Singh
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | Season | 2026-02-01 |  |  | Vacuum increasing in Pan | DC Nozzle-01,Zet-03 & DO 02 flat seal-09,dome nut-09,domnut oring-09 replaced with new | 3675 | Internal | Mr Anuj / Mr V.Singh
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | Season | 2026-02-14 |  |  | Vacuum increasing in Pan | DC Nozzle-01,Zet-03 & DO 02 flat seal-09,dome nut-09,domnut oring-09 replaced with new | 6675
b559d63183c6 | SEDL14 :: ZIL/SUG./001/Pan-12 | ZIL/SUG./001/Pan-12 | OFF Season | 2026-06-12 |  |  | Duering Overhauling checking found damage.flat seal 16 nos. Doom nut 16, O ring bolt 16 nos. & DO 02 nos. Jet 01 nos. | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. Flat seal & dome nut with nozzle replaced with new. | 4000 | Internal | Mr A. Varma / Mr V.Singh
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | OFF Season | 2024-07-19 |  |  | Flat seal 04 nos, doomnut 4 nos, doomnut o-ring 4 nos,DO nozzle-03 nos ,DC nozzle 01 nos Jet nozzle 3 nos SOV plunger 02 nos & profile gasket 1 no wornout. | DO,DC, Jet nozzle,NRV checking, cleaning & overhauling work are completed. flat seal ,doomnut ,doomnut o-ring , DO ,DC & Jet nozzle plunger & profile gasket replaced with new. | 8346 | Internal | Mr Anuj / Mr V.Singh
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | OFF Season | 2025-08-30 |  |  | Found SOV Not Proper working with Vaccuam tx. Not working | All sov Clean with proper lubricant fitted at position with replaced new tx. | 12695 | Internal | Mr Anuj / Mr V.Singh
b378778c6ab8 | SEDL14 :: ZIL/SUG./001/Pan-13 | ZIL/SUG./001/Pan-13 | OFF Season | 2026-06-18 |  |  | Duering Overhauling checking found damage. Doom nut 10, tube-1 mtr.DO 01 nos. | DO,DC, Jet nozzle,NRV & SOV overhauling cleaning & checking with fitting work are completed. Lock nut & dome nut with nozzle replaced with new. | 1500 | Internal | Mr A. Varma / Mr V.Singh
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | OFF Season | 25.05.2022 |  |  | Corse ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing | All Cylinder repair & checking Seal kit replaced of Load bucket ,Course ,fine Cylinder |  | Internal | A Varma / V Singh
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | OFF Season | 05.08.2023 |  |  | Corse ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing | Seal kit replaced of Load bucket ,Corse ,fine Cylinder & Load bucket bearing replaced |  | Internal | A Varma / V Singh
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | Season | 22.01.2024 |  |  | Corse cylinder not proper working. | Corse cylinder SOV replaced new |  | Internal | A Varma / V Singh
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | OFF Season | 05.08.2024 |  |  | Corse ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR found sugar dust | Corse,Fine S fine,Load bucket & bag clamp cylinder dismentale clean repair with checking work done.Load bucket & Corse Cylinder Seal kit replaced new | 1150 | Internal | A Varma / V Singh
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | Season | 18.01.2025 |  |  | Load Bucket Cylinder linkage | Cylinder repair it | 750 | Internal | A Varma / V Singh
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | Season | 23.02.2025 |  |  | Load Bucket Cylinder Problem | Repair it | 650 | Internal | A Varma / V Singh
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | Season | 24.01.2025 |  |  | Corse Cylinder SOV problem | Repair it | 250 | Internal | A Varma / V Singh
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | Season | 06.02.2025 |  |  | Bag Clamp Cylinder linkage | Cylinder repair it | 750 | Internal | A Varma / V Singh
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | OFF Season | 09.07.2025 |  |  | Corse ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter Found sugar dust. | All Cylinder,SOV & AFR repair & checking Seal kit replaced Load bucket 02 nos fine cylinder 01 nos,Bagclamp 01 nos.SOV screw 05 nos,FCV 01nos. | 3000 | Internal | Mr.Anuj / Mr. V Singh
3bd74d627abf | Hi-Tech :: ZIL/SUG./001/M1-SWM | ZIL/SUG./001/M1-SWM | Season | 2025-11-24 |  |  | Controller 03 error | Proxy replaced with new | 1250 | Internal | Mr.Anuj / Mr. V Singh
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | OFF Season | 23.05.2022 |  |  | Course ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing | All Cylinder repair & checking Seal kit replaced of Load bucket ,Course ,fine Cylinder |  | Internal | A Varma / V Singh
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | OFF Season | 06.08.2023 |  |  | Course ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing | All Cylinder repair & checking Seal kit replaced of Load bucket ,Course ,fine Cylinder |  | Internal | A Varma / V Singh
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | Season | 24.01.2024 |  |  | Weight varation at running time | Load cell replaced with new | 8500 | Internal | Anuj / V Singh
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | OFF Season | 09.07.2024 |  |  | Course ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR found sugar dust. | All Cylinder repair & checking Bag clamp Cylinder seal kit replaced | 650 | Internal | A Varma / V Singh
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | Season | 22.02.2025 |  |  | Weight varation at running time | Load cell replaced with new | 8500 | Internal | Anuj / V Singh
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | Season | 01.03.2025 |  |  | Proxy Problem | Replaced with new | 250 | Internal | Anuj / V Singh
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | Season | 01.03.2025 |  |  | Controller zero Problem faced | Replaced with spare controller | 60000 | Internal | Anuj / V Singh
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | Season | 02.03.2025 |  |  | Zero Stable Problem | Load cell Card Replaced | 20000 | Internal | Anuj / V Singh
ab356bfdc2ff | Hi-Tech :: ZIL/SUG./01/M2-SWM | ZIL/SUG./01/M2-SWM | OFF Season | 07.07.2025 |  |  | Corse ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter Found sugar dust. | All Cylinder,SOV & AFR repair & checking Seal kit replaced Load bucket 02 nos,AFR drain 01 nos.FCV 02 nos. | 2000 | Internal | Mr.Anuj / Mr. V Singh
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | OFF Season | 26.05.2022 |  |  | Corse ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing Checking | All Cylinder,SOV & AFR repair & checking Seal kit replaced of Load bucket & fine Cylinder with new. |  | Internal | Mr.A Varma /Mr. V Singh
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | OFF Season | 06.08.2023 |  |  | Corse ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing | All Cylinder,SOV & AFR repair & checking Seal kit replaced of Load bucket bearing with flapper new. |  | Internal | Mr.A Varma /Mr. V Singh
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | OFF Season | 08.07.2024 |  |  | Corse ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter Found sugar dust. | All Cylinder,SOV & AFR repair & checking Seal kit replaced Load bucket cylinder. | 650 | Internal | Mr.A Varma /Mr. V Singh
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | Season | 29.12.2024 |  |  | Bag Clamp Cylinder Problem | Repair it take in line | 650 | Internal | Mr.A Varma /Mr. V Singh
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | Season | 07.01.2025 |  |  | Proxy Problem | Replaced with new | 350 | Internal | Mr.A Varma /Mr. V Singh
26a43b7dfa80 | Hi-Tech :: ZIL/SUG./01/S-SWM | ZIL/SUG./01/S-SWM | OFF Season | 05.07.2025 |  |  | Corse ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter Found sugar dust. | All Cylinder,SOV & AFR repair & checking Seal kit replaced Load bucket 01 nos cylinder,SOV seal kit & screw 01,02 nos | 1100 | Internal | Mr.Anuj / Mr. V Singh
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | OFF Season | 25.05.2022 |  |  | Found Course ,fine S fine, Load bucket ,Bag clamp Cylinder & Limit itch sutter at sugar dust.load bucket & bag clamp cylinder seal kit air liekage. | Corse ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing repair with checking work done.Seal kit replaced of Load bucket ,Bag clamp Cylinder replaced with new |  | Internal | A Varma / V Singh
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | OFF Season | 03.05.2023 |  |  | Course ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing | Seal kit replaced of Load bucket ,Course ,fine Cylinder & Load bucket bearing replaced |  | Internal | A Varma / V Singh
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | OFF Season | 15.07.2024 |  |  | Course ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter , load bucket bearing | All Cylinder repair & checking Seal kit replaced of Load bucket Cylinder | 650 | Internal | A Varma / V Singh
6fafe505f018 | Hi-Tech :: ZIL/SUG./01/L-SWM | ZIL/SUG./01/L-SWM | OFF Season | 10.07.2025 |  |  | Corse ,fine S fine, Load bucket ,Bag clamp Cylinder & SOV , AFR ,Limit switch sutter Found sugar dust. | All Cylinder,SOV & AFR repair & checking Seal kit replaced Load bucket,bag clamp 02 nos cylinder,SOV seal kit 02 nos & FCV 02 nos. | 1200 | Internal | Mr.Anuj / Mr. V Singh
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | OFF Season | 2022-04-06 |  |  | Control valve Seat & body found rusty. AFR & positioner Gauge found ok. | Proper cleaning, Painting & Lubrication work done. Damage part change with new. |  |  | Mr. Ritesh / Mr. V singh
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | OFF Season | 2023-06-12 |  |  | Control valve Seat & body found rusty. AFR Filter & positioner Gauge found broken. | Proper cleaning, Painting & Lubrication work done. Damage part change with new. |  |  | Mr. Gaurav / Mr. V singh
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | OFF Season | 2024-06-20 |  |  | Control valve Seat found leaky & body rusty. AFR Filter & positioner Gauge found ok. | Control valve seat replace with new spare. Proper cleaning & Lubrication work done. | 18200 | Internal | Mr. Gaurav / Mr. V singh
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | OFF Season | 2025-05-05 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling ,Painting & Lubrication work with checking workdone. | 250 | Internal | Mr. Anuj Kr / Mr. V singh
7a3eb383c90c | D.B.F 14 :: ZIL/SUG./001 ( 40FCV101) | ZIL/SUG./001 ( 40FCV101) | OFF Season | 2026-04-25 |  |  | Control valve Seat & body found rusty. | SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling & Lubrication work with checking workdone. | 250 | Internal | Mr. Anuj kr / Mr. V singh
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | OFF Season | 2022-04-06 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found damage. | Proper cleaning, Painting & Lubrication work done. Damage part change with new. |  |  | Mr. Ritesh / Mr. V singh
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | OFF Season | 2023-06-12 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found damage. | Proper cleaning, Painting & Lubrication work done. Damage part change with new. |  |  | Mr. Gaurav / Mr. V singh
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | OFF Season | 2024-05-06 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 200 | Internal | Mr. Gaurav / Mr. V singh
05ec9f5bc726 | D.B.F 14 :: ZIL/SUG./001 (40XV102) | ZIL/SUG./001 (40XV102) | OFF Season | 2026-04-25 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling ,Painting & Lubrication work with checking workdone. | 250 | Internal | Mr. Anuj kr / Mr. V singh
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | OFF Season | 2022-04-06 |  |  | Control valve Seat & body found rusty. AFR & Dome switch found healty | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | OFF Season | 2023-06-12 |  |  | Control valve Seat & body found rusty. AFR & Dome switch found healty | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | OFF Season | 2024-05-04 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | OFF Season | 2025-05-05 |  |  | Control valve Seat & body found rusty. Actuator soft leak surface worn-out with O ring set damage. | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 1600 | Internal | Mr. Anuj Kr / Mr. V singh
11dcd9c3da64 | D.B.F 14 :: ZIL/SUG./001 (40XV103) | ZIL/SUG./001 (40XV103) | OFF Season | 2026-04-23 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling & Lubrication work with checking workdone.Joint seat replace. | 250 | Internal | Mr. Anuj kr / Mr. V singh
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | OFF Season | 2022-04-06 |  |  | Control valve Seat & body found rusty. AFR & Dome switch found healty | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | OFF Season | 2023-06-12 |  |  | Control valve Seat & body found rusty. AFR & Dome switch found healty | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | OFF Season | 2024-05-06 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | OFF Season | 2025-05-06 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
c90105591ef7 | D.B.F 14 :: ZIL/SUG./001 (40XV105) | ZIL/SUG./001 (40XV105) | OFF Season | 2026-04-24 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling & Lubrication work with checking workdone.Joint seat replace. | 250 | Internal | Mr. Anuj kr / Mr. V singh
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | OFF Season | 2022-05-06 |  |  | Control valve Body found rusty and Valve seat worn-out. AFR or Dome Switch found healty. | Proper cleaning, Painting & Seat replace with new work done |  |  | Mr. Ritesh / Mr. V singh
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | OFF Season | 2023-06-13 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | OFF Season | 2024-05-06 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | OFF Season | 2025-05-06 |  |  | Control valve Seat & body found rusty. Valve handle missing | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 250 | Internal | Mr. Anuj Kr / Mr. V singh
c5c251e5e479 | D.B.F 14 :: ZIL/SUG./001 (40XV106) | ZIL/SUG./001 (40XV106) | OFF Season | 2026-04-24 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling & Lubrication work with checking workdone.Joint seat replace. | 250 | Internal | Mr. Anuj kr / Mr. V singh
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | OFF Season | 2022-05-06 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | OFF Season | 2023-06-13 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | OFF Season | 2024-05-04 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | OFF Season | 2025-05-06 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 250 | Internal | Mr. Anuj Kr / Mr. V singh
b5a7a06c42c2 | D.B.F 14 :: ZIL/SUG./001 (40XV107) | ZIL/SUG./001 (40XV107) | OFF Season | 2026-04-24 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling & Lubrication work with checking workdone.Joint seat replace. | 250 | Internal | Mr. Anuj kr / Mr. V singh
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | OFF Season | 2022-05-06 |  |  | Control valve Seat & body found and rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | OFF Season | 2023-06-13 |  |  | Control valve Seat & body found and rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Season | 2023-12-20 |  |  | Actuator Leakage. | New 'O' Ring set replace & ok |  |  | Mr. Gaurav / Mr. V singh
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | OFF Season | 2024-05-04 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | Season | 2025-02-11 |  |  | Positioner problem | Proper cleaning, warm-up & checking work done. |  | Internal | Mr. Sushil / Mr. V singh
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | OFF Season | 2025-05-06 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 250 | Internal | Mr. Anuj Kr / Mr. V singh
1a298040c9ea | D.B.F 14 :: ZIL/SUG./001 (40XV108) | ZIL/SUG./001 (40XV108) | OFF Season | 2026-04-24 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling & Lubrication work with checking workdone.Joint seat replace. | 250 | Internal | Mr. Anuj kr / Mr. V singh
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | OFF Season | 2022-05-06 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | OFF Season | 2023-06-13 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | OFF Season | 2024-05-07 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | OFF Season | 2025-05-06 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 250 | Internal | Mr. Anuj Kr / Mr. V singh
f17e9f0ef77c | D.B.F 14 :: ZIL/SUG./001 (40XV202) | ZIL/SUG./001 (40XV202) | OFF Season | 2026-04-23 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling ,Lubrication work with checking workdone.joint seat replace. | 250 | Internal | Mr. Anuj kr / Mr. V singh
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | OFF Season | 2022-05-06 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | OFF Season | 14/06/2023 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | OFF Season | 2024-05-06 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | OFF Season | 2025-05-05 |  |  | Control valve Seat & body found rusty. Actuator surface worn-out with O ring set damage. | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 1600 | Internal | Mr. Anuj Kr / Mr. V singh
11fd144e2a54 | D.B.F 14 :: ZIL/SUG./001 (40XV203) | ZIL/SUG./001 (40XV203) | OFF Season | 2026-04-23 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling ,Lubrication work with checking workdone.joint seat replace. | 250 | Internal | Mr. Anuj kr / Mr. V singh
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | OFF Season | 2022-06-06 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | OFF Season | 14/06/2023 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | OFF Season | 2024-05-07 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | OFF Season | 2025-05-05 |  |  | Control valve Seat & body found rusty. Actuator gide pad damage. O ring worn-out | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 1600 | Internal | Mr. Anuj Kr / Mr. V singh
ae927933014e | D.B.F 14 :: ZIL/SUG./001 (40XV205) | ZIL/SUG./001 (40XV205) | OFF Season | 2026-04-22 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling ,Lubrication work with checking workdone.joint seat replace. | 250 | Internal | Mr. Anuj kr / Mr. V singh
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | OFF Season | 2022-06-06 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | OFF Season | 14/06/2023 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | OFF Season | 2024-05-07 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | OFF Season | 2025-05-06 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 250 | Internal | Mr. Anuj Kr / Mr. V singh
c5431b24d860 | D.B.F 14 :: ZIL/SUG./001 (40XV206) | ZIL/SUG./001 (40XV206) | OFF Season | 2026-04-22 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling ,Lubrication work with checking workdone.joint seat replace. | 250 | Internal | Mr. Anuj kr / Mr. V singh
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | OFF Season | 2022-06-07 |  |  | Control valve Seat found rusty and Actuator spring damage. AFR & dome swith is healty. | Proper cleaning, painting & Actuator spring replace with new. |  |  | Mr. Ritesh / Mr. V singh
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | OFF Season | 14/06/2023 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | OFF Season | 2024-05-07 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 75 | Internal | Mr. Gaurav / Mr. V singh
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | OFF Season | 2025-05-06 |  |  | Control valve Seat & body found rusty. Actuator gide pad damage. O ring worn-out | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 1200 | Internal | Mr. Anuj Kr / Mr. V singh
4ef27273fcae | D.B.F 14 :: ZIL/SUG./001 (40XV207) | ZIL/SUG./001 (40XV207) | OFF Season | 2026-04-22 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling ,Lubrication work with checking workdone.joint seat replace. | 250 | Internal | Mr. Anuj kr / Mr. V singh
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | OFF Season | 2022-06-06 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | OFF Season | 15/06/2023 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | OFF Season | 2024-05-07 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | OFF Season | 2025-05-06 |  |  | Control valve Seat & body found rusty. MS Flange & seat worn-out-50% | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 250 | Internal | Mr. Anuj Kr / Mr. V singh
6f0df9d5dac2 | D.B.F 14 :: ZIL/SUG./001 (40XV208) | ZIL/SUG./001 (40XV208) | OFF Season | 2026-04-22 |  |  | Control valve Seat & body found rusty. | Dome switch,SOV,Actuator ,Gear ,Valve seat Proper cleaning Overhauling ,Lubrication work with checking workdone.joint seat replace. | 250 | Internal | Mr. Anuj kr / Mr. V singh
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | OFF Season | 18/7/2022 |  |  | Control valve Seat & body found rusty. AFR & positioner found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | OFF Season | 27/07/2023 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | OFF Season | 2024-07-27 |  |  | Control valve shoft seat found 2 cut sign but no leakage found. AFR found healty. | Proper cleaning, Painting & Lubrication work done. | 180 | Internal | Mr. Gaurav / Mr. V singh
a10c85b7482a | D.B.F 14 :: ZIL/SUG./001 (40FCV003) | ZIL/SUG./001 (40FCV003) | OFF Season | 2025-05-30 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 250 | Internal | Mr. Anuj Kr / Mr. V singh
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | OFF Season | 2022-10-06 |  |  | Control valve Seat & body found rusty. AFR Filter & positioner Gauge found damage. | Proper cleaning, Painting & Lubrication work done. Damage part change with new. |  |  | Mr. Ritesh / Mr. V singh
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | OFF Season | 19/06/2023 |  |  | Control valve Seat & body found rusty. AFR Filter & positioner Gauge found damage. | Proper cleaning, Painting & Lubrication work done. Damage part change with new. |  |  | Mr. Gaurav / Mr. V singh
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | OFF Season | 2024-06-14 |  |  | Control valve Seat & body found rusty. AFR Filter & positioner Gauge found ok. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
1cb9b5ce967c | I.E.R 49 :: ZIL/SUG./001 (52 FCV 101) | ZIL/SUG./001 (52 FCV 101) | OFF Season | 2025-05-20 |  |  | Control valve Seat & body found rusty. Actuator O ring worn-out | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 1200 | Internal | Mr. Anuj Kr / Mr. V singh
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | OFF Season | 15/06/2022 |  |  | Control valve Body found rusty and valve seat worn-out. AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. Damage Seat replace with new. |  |  | Mr. Ritesh / Mr. V singh
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | OFF Season | 19/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | OFF Season | 2024-06-14 |  |  | Control valve Seat & body found rusty. AFR Filter & positioner Gauge found ok. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
d1651f38d251 | I.E.R 49 :: ZIL/SUG./001 (52 XV 102) | ZIL/SUG./001 (52 XV 102) | OFF Season | 2025-05-20 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | OFF Season | 2022-10-06 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | OFF Season | 19/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | OFF Season | 2024-06-14 |  |  | Control valve Seat & body found rusty. AFR Filter & positioner Gauge found ok. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | Season | 2025-02-03 |  |  | Postioner problem | Replaced with new | 75000 | Internal | Mr. Anirudh / Mr. V singh
cd76793a1867 | I.E.R 49 :: ZIL/SUG./001 (52 XV 103) | ZIL/SUG./001 (52 XV 103) | OFF Season | 2025-05-20 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | OFF Season | 2022-10-06 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | OFF Season | 19/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | OFF Season | 2024-06-13 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
fbbf27511e0e | I.E.R 49 :: ZIL/SUG./001 (52 XV 104) | ZIL/SUG./001 (52 XV 104) | OFF Season | 2025-05-17 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | OFF Season | 2023-03-06 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | OFF Season | 21/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | OFF Season | 2024-06-13 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
88e0c7415c60 | I.E.R 49 :: ZIL/SUG./001 (52 XV 105) | ZIL/SUG./001 (52 XV 105) | OFF Season | 2025-05-17 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | OFF Season | 2022-10-06 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | OFF Season | 21/06/2023 |  |  | Control valve found Rusty ,valve seat worn-out & actuator spring damage. | Proper cleaning, Painting & Lubrication work done. Replace with new seat & actuator spring. |  |  | Mr. Gaurav / Mr. V singh
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | OFF Season | 2024-06-13 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
63127c6882ad | I.E.R 49 :: ZIL/SUG./001 (52 XV 106) | ZIL/SUG./001 (52 XV 106) | OFF Season | 2025-05-17 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | OFF Season | 13/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | OFF Season | 21/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | OFF Season | 2024-06-13 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
e3800d2d6ba3 | I.E.R 49 :: ZIL/SUG./001 (52 XV 108) | ZIL/SUG./001 (52 XV 108) | OFF Season | 2025-05-19 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | OFF Season | 13/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | OFF Season | 21/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | OFF Season | 2024-07-03 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
2da5835fef9b | I.E.R 49 :: ZIL/SUG./001 (52 XV 110 ) | ZIL/SUG./001 (52 XV 110 ) | OFF Season | 2025-05-19 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | OFF Season | 13/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | OFF Season | 23/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | OFF Season | 2023-06-15 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | OFF Season | 2025-05-19 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV found healthy. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | Season | 2025-10-29 |  |  | Control valve Seat Leakage | Replaced with new |  | Internal | Anirudh Varma
e4c4c04b2bb1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 111) | ZIL/SUG./001 (52 XV 111) | OFF Season | 2026-04-29 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling & Lubrication work done.joint seat replace. | 150 | Internal | Mr.Sushil Singh / Mr. V singh
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | OFF Season | 13/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | OFF Season | 23/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | OFF Season | 2023-06-15 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | OFF Season | 2025-05-19 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV found healthy. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
b8849694327a | I.E.R 49 :: ZIL/SUG./001 (52 XV 118) | ZIL/SUG./001 (52 XV 118) | OFF Season | 2026-04-27 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling & Lubrication work done.joint seat replace. | 150 | Internal | Mr.Sushil Singh / Mr. V singh
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | OFF Season | 13/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | OFF Season | 23/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | OFF Season | 2024-05-10 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | OFF Season | 2025-05-19 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV found L N bolt missing | Proper cleaning, overhauling ,checking Painting & bolt fitting Lubrication work done. | 250 | Internal | Mr. Anuj Kr / Mr. V singh
0799a65b9568 | I.E.R 49 :: ZIL/SUG./001 (52 XV 119) | ZIL/SUG./001 (52 XV 119) | OFF Season | 2026-05-05 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV found L N bolt missing | Proper cleaning, overhauling ,checking Painting & bolt fitting Lubrication work done. | 250 | Internal | Mr. Sushil singh/ Mr. V singh
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | OFF Season | 13/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | OFF Season | 23/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | OFF Season | 2024-05-10 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | OFF Season | 2025-05-19 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV OK | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
a74a679cab3b | I.E.R 49 :: ZIL/SUG./001 (52 XV 120) | ZIL/SUG./001 (52 XV 120) | OFF Season | 2026-05-06 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV found L N bolt missing | Proper cleaning, overhauling ,checking & bolt fitting Lubrication work done.joint seat replace. | 250 | Internal | Mr. Sushil singh/ Mr. V singh
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | OFF Season | 15/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | OFF Season | 26/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | OFF Season | 2024-05-09 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | OFF Season | 2025-05-06 |  |  | Control valve Seat & body found rusty. Actuator air liekage. | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
b9bdd4fb67d5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 121) | ZIL/SUG./001 (52 XV 121) | OFF Season | 2026-05-06 |  |  | Control valve Seat & Body found rusty . AFR, Dome Switch & SOV found L N bolt missing | Proper cleaning, overhauling ,checking & bolt fitting Lubrication work done.joint seat replace. | 250 | Internal | Mr. Sushil singh/ Mr. V singh
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | OFF Season | 15/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | OFF Season | 26/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | OFF Season | 2024-06-11 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | Season | 2025-03-04 |  |  | Control valve Seat passing | Control valve replaced with new | 18500 | Internal | Mr. Anuj / Mr. V singh
45b3dfbc9cc9 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 201) | ZIL/SUG./001 (52 FCV 201) | OFF Season | 2025-09-15 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found healthy. | Seat Actuator ,gear Proper cleaning, overhauling with checking work are done. | 150 | Internal | Mr.Anirudh / Mr. V singh
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | OFF Season | 2022-06-15 |  |  | Control valve Body found rusty and valve seat worn-out. AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. Damage Seat replace with new. |  |  | Mr. Ritesh / Mr. V singh
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | OFF Season | 26/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | OFF Season | 2024-06-11 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | OFF Season | 2025-05-13 |  |  | Control valve Seat & body found rusty. Actuator air liekage. | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 1200 | Internal | Mr. Anuj Kr / Mr. V singh
bb218e11bff5 | I.E.R 49 :: ZIL/SUG./001 (52 XV 202) | ZIL/SUG./001 (52 XV 202) | Season | 2026-01-26 |  |  | Control valve feedback error | Dome indicator replaced it | 3500 | Internal | Mr. Anuj Kr / Mr. V singh
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | OFF Season | 15/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | OFF Season | 26/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | OFF Season | 2024-06-11 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
7f0a70fb60da | I.E.R 49 :: ZIL/SUG./001 (52 XV 203) | ZIL/SUG./001 (52 XV 203) | OFF Season | 2025-05-12 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | OFF Season | 15/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | OFF Season | 28/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | OFF Season | 2024-06-07 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
478724a411da | I.E.R 49 :: ZIL/SUG./001 (52 XV 204) | ZIL/SUG./001 (52 XV 204) | OFF Season | 2025-05-12 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | OFF Season | 15/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | OFF Season | 28/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | OFF Season | 2024-06-07 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
66fa4c0c4412 | I.E.R 49 :: ZIL/SUG./001 (52 XV 205) | ZIL/SUG./001 (52 XV 205) | OFF Season | 2025-05-12 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | OFF Season | 15/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | OFF Season | 28/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | OFF Season | 2024-06-07 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
dcad64bcb0fb | I.E.R 49 :: ZIL/SUG./001 (52 XV 206) | ZIL/SUG./001 (52 XV 206) | OFF Season | 2025-05-13 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | OFF Season | 15/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | OFF Season | 28/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 |  | Mr. Gaurav / Mr. V singh
4b60fc4973e0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 208) | ZIL/SUG./001 (52 XV 208) | OFF Season | 2024-06-07 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 150 | Internal | Mr. Gaurav / Mr. V singh
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | OFF Season | 15/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | OFF Season | 30/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | OFF Season | 2024-07-06 |  |  | Control valve Seat found wornout & Body found rusty . AFR & SOV found healthy. | Replaced control valve seat & Proper cleaning & Lubrication work done. | 18000 | Internal | Mr. Gaurav / Mr. V singh
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | OFF Season | 2025-05-14 |  |  | Control valve Seat & Body found rusty . Seat 80% worn-out | Proper cleaning,Overhauling work Painting & Lubrication work done.seat replacedcwith new | 400 | Internal | Mr. Anuj Kr / Mr. V singh
f623dac7b3dc | I.E.R 49 :: ZIL/SUG./001 (52 XV 210) | ZIL/SUG./001 (52 XV 210) | Season | 2025-11-18 |  |  | Control valve Seat worn-out | Replaced with new |  | Internal | Mr. A Varma / Mr. V singh
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | OFF Season | 16/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | OFF Season | 30/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | OFF Season | 2024-06-17 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | OFF Season | 2025-05-13 |  |  | Control valve Seat & body found rusty. seat worn-out-50% | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
59a2640f4f85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 211) | ZIL/SUG./001 (52 XV 211) | OFF Season | 2026-04-29 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Lubrication work done.Replace vave joint seat. | 200 | Internal | Mr. Sushil / Mr. V singh
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | OFF Season | 16/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | OFF Season | 30/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | OFF Season | 2024-06-17 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy.Actuator Pinion O ring out of order. | Proper cleaning & Lubrication work done.Replace Pinion O ring with new Spare. | 950 | Internal | Mr. Gaurav / Mr. V singh
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | OFF Season | 2025-05-13 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 250 | Internal | Mr. Anuj Kr / Mr. V singh
a83bf72fffa4 | I.E.R 49 :: ZIL/SUG./001 (52 XV 218) | ZIL/SUG./001 (52 XV 218) | OFF Season | 2026-04-27 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Lubrication work done.Replace vave joint seat. | 200 | Internal | Mr. Sushil / Mr. V singh
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | OFF Season | 16/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | OFF Season | 30/06/2023 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | OFF Season | 2024-05-08 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | OFF Season | 2025-05-13 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
551193369d6a | I.E.R 49 :: ZIL/SUG./001 (52 XV 219 ) | ZIL/SUG./001 (52 XV 219 ) | OFF Season | 2026-05-07 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Lubrication work done.Replace vave joint seat. | 200 | Internal | Mr. Sushil / Mr. V singh
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | OFF Season | 16/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | OFF Season | 2023-03-07 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | OFF Season | 2024-05-08 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | OFF Season | 2025-05-13 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 350 | Internal | Mr. Anuj Kr / Mr. V singh
e9619a09fee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 220) | ZIL/SUG./001 (52 XV 220) | OFF Season | 2026-05-07 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Lubrication work done.Replace vave joint seat. | 200 | Internal | Mr. Sushil / Mr. V singh
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | OFF Season | 16/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | OFF Season | 2023-03-07 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | OFF Season | 2024-05-08 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. Actuator spring found broken. | Proper cleaning, Painting & Lubrication work done.Replace new spring . | 100 | Internal | Mr. Gaurav / Mr. V singh
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | OFF Season | 2025-05-13 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
6c84ae83dee0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 221) | ZIL/SUG./001 (52 XV 221) | OFF Season | 2026-05-08 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Lubrication work done.Replace vave joint seat. | 200 | Internal | Mr. Sushil / Mr. V singh
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | OFF Season | 17/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | OFF Season | 2023-03-07 |  |  | Control valve Seat & Body found rusty . AFR Gauge & Positioner Gauge found damage. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | OFF Season | 2024-06-06 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
8d31714f6be8 | I.E.R 49 :: ZIL/SUG./001 (52 FCV 301) | ZIL/SUG./001 (52 FCV 301) | OFF Season | 2025-05-06 |  |  | Control valve Seat & body found rusty. Actuator gide pad damage. O ring worn-out | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new.04 nos L N bolt replaced | 1100 | Internal | Mr. Anuj Kr / Mr. V singh
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | OFF Season | 17/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | OFF Season | 2023-03-07 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | OFF Season | 2024-06-06 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
b47c5e17e65e | I.E.R 49 :: ZIL/SUG./001 (52 XV 302) | ZIL/SUG./001 (52 XV 302) | OFF Season | 2025-05-12 |  |  | Control valve Seat & body found rusty. Actuator inner side worn-out | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 1100 | Internal | Mr. Anuj Kr / Mr. V singh
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | OFF Season | 17/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | OFF Season | 2023-05-07 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | OFF Season | 2024-06-05 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
cdd12698eba1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 303) | ZIL/SUG./001 (52 XV 303) | OFF Season | 2025-05-09 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 250 | Internal | Mr. Anuj Kr / Mr. V singh
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | OFF Season | 17/6/2022 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | OFF Season | 2023-05-07 |  |  | Control valve seat & body found rusty.Actuator Piston pad damage. AFR & Dome switch found Healthy. | Proper cleaning, painting & replace new piston pad work done |  |  | Mr. Gaurav / Mr. V singh
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | OFF Season | 2024-06-05 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 150 | Internal | Mr. Gaurav / Mr. V singh
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | OFF Season | 2025-05-09 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
0455409d1e96 | I.E.R 49 :: ZIL/SUG./001 (52 XV 304) | ZIL/SUG./001 (52 XV 304) | OFF Season | 2026-05-16 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Lubrication work done.Joint replace with new. | 200 | Internal | Mr.Sushil singh/ Mr. V singh
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | OFF Season | 17/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | OFF Season | 2023-05-07 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | OFF Season | 2024-06-05 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 150 | Internal | Mr. Gaurav / Mr. V singh
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | OFF Season | 2025-05-09 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
d253aeb78ee7 | I.E.R 49 :: ZIL/SUG./001 (52 XV 305) | ZIL/SUG./001 (52 XV 305) | OFF Season | 2026-05-16 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Lubrication work done.Joint replace with new. | 200 | Internal | Mr.Sushil singh/ Mr. V singh
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | OFF Season | 17/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | OFF Season | 2023-05-07 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | OFF Season | 2024-06-05 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, Painting & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | OFF Season | 2025-05-09 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
87037ca13222 | I.E.R 49 :: ZIL/SUG./001 (52 XV 306) | ZIL/SUG./001 (52 XV 306) | OFF Season | 2026-05-16 |  |  | Control valve Seat was found wearout. & water leakage. Body found rusty. | Proper cleaning, overhauling ,checking Lubrication work done.Valve teflon seat replace with new. | 1500 | Internal | Mr.Sushil singh/ Mr. V singh
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | OFF Season | 17/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | OFF Season | 2023-07-07 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | OFF Season | 2024-08-16 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
d08a5b1c82b9 | I.E.R 49 :: ZIL/SUG./001 (52 XV 308) | ZIL/SUG./001 (52 XV 308) | OFF Season | 2025-09-12 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. | 250 | Internal | Mr. Anuj / Mr. V singh
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | OFF Season | 17/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  | Internal | Mr. Ritesh / Mr. V singh
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | OFF Season | 2023-07-07 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  | Internal | Mr. Gaurav / Mr. V singh
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | OFF Season | 2024-07-04 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
a12747901927 | I.E.R 49 :: ZIL/SUG./001 (52 XV 310) | ZIL/SUG./001 (52 XV 310) | OFF Season | 2025-05-14 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | OFF Season | 18/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | OFF Season | 2023-07-07 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | OFF Season | 2024-06-17 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | OFF Season | 2025-05-15 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy.1 spring is damage | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 600 | Internal | Mr. Anuj Kr / Mr. V singh
dec00ba465cb | I.E.R 49 :: ZIL/SUG./001 (52 XV 311) | ZIL/SUG./001 (52 XV 311) | OFF Season | 2026-05-04 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Lubrication work done.Replace vave joint seat. | 200 | Internal | Mr. Sushil / Mr. V singh
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | OFF Season | 18/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | OFF Season | 2023-07-07 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | OFF Season | 2024-06-17 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | OFF Season | 2025-05-10 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
6dc309fdc4d0 | I.E.R 49 :: ZIL/SUG./001 (52 XV 318) | ZIL/SUG./001 (52 XV 318) | OFF Season | 2026-05-04 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Lubrication work done.joint seat replace with new. | 200 | Internal | Mr.Sushil Singh / Mr. V singh
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | OFF Season | 2023-08-06 |  |  | Control valve seat & body found rusty and actuator spring damage. AFR,Sov & Dome swith found healthy . | Proper cleaning & spring replace with new work done. |  |  | Mr. Ritesh / Mr. V singh
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | OFF Season | 2023-08-07 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | OFF Season | 2024-05-09 |  |  | Control valve Seat & Body found rusty. AFR , SOV Dome switch found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | OFF Season | 2025-05-09 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | Season | 2025-11-05 |  |  | Control valve Actuator not working | found actuator seal kit worn-out replaced with new take in line. | 800 | Internal | Mr. Anuj Kr / Mr. V singh
4ef7a370c829 | I.E.R 49 :: ZIL/SUG./001 (52 XV 319) | ZIL/SUG./001 (52 XV 319) | OFF Season | 2026-05-08 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Lubrication work done.joint seat replace with new. | 200 | Internal | Mr.Sushil Singh / Mr. V singh
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | OFF Season | 18/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | OFF Season | 2023-08-07 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | OFF Season | 2024-05-09 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning & Lubrication work done. | 80 | Internal | Mr. Gaurav / Mr. V singh
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | OFF Season | 2025-05-11 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
0c4d5ee8dec8 | I.E.R 49 :: ZIL/SUG./001 (52 XV 320) | ZIL/SUG./001 (52 XV 320) | OFF Season | 2026-05-09 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Lubrication work done.joint seat replace with new. | 200 | Internal | Mr.Sushil Singh / Mr. V singh
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | OFF Season | 18/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | OFF Season | 2023-08-07 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | OFF Season | 2024-05-09 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning & Lubrication work done. | 80 | Internal | Mr. Gaurav / Mr. V singh
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | OFF Season | 2025-05-11 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
371b7cdefdcf | I.E.R 49 :: ZIL/SUG./001 (52 XV 321) | ZIL/SUG./001 (52 XV 321) | OFF Season | 2026-05-08 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Lubrication work done.joint seat replace with new. | 200 | Internal | Mr.Sushil Singh / Mr. V singh
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | OFF Season | 18/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | OFF Season | 2023-11-07 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | OFF Season | 2024-06-28 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. | 80 | Internal | Mr. Gaurav / Mr. V singh
5327e9dcefbd | I.E.R 49 :: ZIL/SUG./001 (52 XV005) | ZIL/SUG./001 (52 XV005) | OFF Season | 2025-05-24 |  |  | Control valve Seat & body found rusty. Seat worn-out | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 17000 | Internal | Mr. Anuj Kr / Mr. V singh
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | OFF Season | 18/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | OFF Season | 2023-11-07 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | OFF Season | 2024-06-28 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. | 80 | Internal | Mr. Gaurav / Mr. V singh
727e6f6de9ff | I.E.R 49 :: ZIL/SUG./001 (52 XV 006) | ZIL/SUG./001 (52 XV 006) | OFF Season | 2025-05-25 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | OFF Season | 18/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | OFF Season | 2023-11-07 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | OFF Season | 2024-06-28 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. | 80 | Internal | Mr. Gaurav / Mr. V singh
21241bcb069b | I.E.R 49 :: ZIL/SUG./001 (52 XV 007 ) | ZIL/SUG./001 (52 XV 007 ) | OFF Season | 2025-05-24 |  |  | Control valve Seat & body found rusty. Seat worn-out | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 17000 | Internal | Mr. Anuj Kr / Mr. V singh
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | OFF Season | 19/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | OFF Season | 2023-07-11 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | OFF Season | 2024-06-22 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  | Internal | Mr. Gaurav / Mr. V singh
5c7f61e1426a | I.E.R 49 :: ZIL/SUG./001 (52 XV 003) | ZIL/SUG./001 (52 XV 003) | OFF Season | 2025-05-26 |  |  | Control valve Seat & Body found rusty . AFR & SOV found healthy. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 200 | Internal | Mr. Anuj Kr / Mr. V singh
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | OFF Season | 19/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | OFF Season | 13/7/2023 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | OFF Season | 2024-06-22 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. Actuator Pinion O ring Out of order. | Proper cleaning & Lubrication work done.Replace O ring with spare . | 700 | Internal | Mr. Gaurav / Mr. V singh
bb33dc7b7b85 | I.E.R 49 :: ZIL/SUG./001 (52 XV 002 ) | ZIL/SUG./001 (52 XV 002 ) | OFF Season | 2025-05-19 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | OFF Season | 19/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | OFF Season | 13/7/2023 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | OFF Season | 2024-06-26 |  |  | Control valve Seat found leakage & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning & Lubrication work done. Replaced its soft seat with new spare. | 5800 | Internal | Mr. Gaurav / Mr. V singh
d6dd30c6388f | I.E.R 49 :: ZIL/SUG./001 (25 TCV 029 ) | ZIL/SUG./001 (25 TCV 029 ) | OFF Season | 2025-05-23 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | OFF Season | 19/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | OFF Season | 13/7/2023 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | OFF Season | 2024-06-26 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
bafef7605571 | I.E.R 49 :: ZIL/SUG./001 (52 XV 036) | ZIL/SUG./001 (52 XV 036) | OFF Season | 2025-05-22 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | OFF Season | 19/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | OFF Season | 15/7/2023 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | OFF Season | 2024-06-26 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
f5f0a13a5636 | I.E.R 49 :: ZIL/SUG./001 (52 XV 032) | ZIL/SUG./001 (52 XV 032) | OFF Season | 2025-05-23 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. Anuj Kr / Mr. V singh
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | OFF Season | 19/6/2022 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | OFF Season | 15/7/2023 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | OFF Season | 2024-07-20 |  |  | Control valve Seat & Body found rusty . Actuator Pinion Both side O ring found worn out. SOV & Dome switch terminal found worn-out. | Repair its Dome Switch & SOV. Proper cleaning, Checking & Lubrication work done. | 650 | Internal | Mr. Gaurav / Mr. V singh
766dcca928c1 | I.E.R 49 :: ZIL/SUG./001 (52 XV 031) | ZIL/SUG./001 (52 XV 031) | OFF Season | 2025-08-05 |  |  | Control valve Seat & Body found rusty . AFR ,SOV Dome switch found healthy. | Proper cleaning, Painting & Lubrication work done. | 200 | Internal | Mr. Gaurav / Mr. V singh
ab4f190cbd95 | I.E.R 49 :: ZIL/SUG./001/FEED-CV-1 | ZIL/SUG./001/FEED-CV-1 | Season | 2026-03-10 |  |  | New Equipment | New equioment installation |  | External | Sushil/Mr. V.singh
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | OFF Season | 02/062022 |  |  | Control valve Seat & Body found rusty . AFR Gauge & Positioner Gauge found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | OFF Season | 29/05/2023 |  |  | Control valve Seat & Body found rusty . AFR Gauge & Positioner Gauge found damage. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | OFF Season | 2024-05-14 |  |  | Control valve Seat & Body found 30% Corresive . | Proper cleaning & Lubrication work done. | 125 | Internal | Mr. Gaurav / Mr.V singh
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | OFF Season | 2025-05-30 |  |  | Control valve Seat & Body found 30% Corresive . | Proper cleaning & Lubrication work done. | 400 | Internal | Mr.Anirudh / Mr.V singh
5993c160b9a2 | DCH Ref. 4 :: ZIL/SUG./001 (20 TCV 015) | ZIL/SUG./001 (20 TCV 015) | OFF Season | 2026-05-13 |  |  | Control valve Seat & Body found 40% Corresive . | Proper cleaning & Lubrication work done. | 400 | Internal | Mr.Sushil Singh / Mr.V singh
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | OFF Season | 2022-03-06 |  |  | Control valve Seat & Body found rusty . AFR Gauge & Positioner Gauge found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | OFF Season | 29/05/2023 |  |  | Control valve Seat found worn-out . AFR Gauge & Positioner Gauge found damage. | Proper cleaning & Lubrication work done. Replace seat with new. |  |  | Mr. Gaurav / Mr.V singh
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | OFF Season | 2024-05-14 |  |  | Control valve Seat & Body found 30% Corresive . | Proper cleaning, Painting & Lubrication work done. | 150 | Internal | Mr. Gaurav / Mr.V singh
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | OFF Season | 2025-05-23 |  |  | Control valve Seat & Body found 30% Corresive . | Proper cleaning & Lubrication work done. | 400 | Internal | Mr.Anirudh / Mr.V singh
eb4a0efd5fd7 | DCH Ref. 4 :: ZIL/SUG./001 (20FCV005) | ZIL/SUG./001 (20FCV005) | OFF Season | 2026-05-14 |  |  | Control valve Seat & Body found 40% Corresive . | Proper cleaning & Lubrication work done. | 400 | Internal | Mr.Sushil Singh / Mr.V singh
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | OFF Season | 2022-04-06 |  |  | Control valve Seat & Body found rusty . AFR Gauge & Positioner Gauge found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | OFF Season | 30/05/2023 |  |  | Control valve Seat & Body found rusty . AFR Gauge & Positioner Gauge found damage. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | OFF Season | 2024-06-25 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found ok. | Proper cleaning & Lubrication work done. | 150 | Internal | Mr. Gaurav / Mr.V singh
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | OFF Season | 2025-06-03 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. A Varma / Mr. V singh
c70872fd1a22 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV010BO1) | ZIL/SUG./001 (20TCV010BO1) | OFF Season | 2026-05-14 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling & Lubrication work done.fitted on position. | 150 | Internal | Mr. Sushil singh / Mr. V singh
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | OFF Season | 2022-04-06 |  |  | Control valve Seat & Body found rusty . AFR Gauge & Positioner Gauge found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | OFF Season | 30/05/2023 |  |  | Control valve Seat & Body found rusty . AFR Gauge & Positioner Gauge found damage. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | OFF Season | 2024-06-25 |  |  | Control valve Seat & Body found rusty . AFR & Positioner found ok. | Proper cleaning & Lubrication work done. | 150 | Internal | Mr. Gaurav / Mr.V singh
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | OFF Season | 2025-06-03 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 150 | Internal | Mr. A Varma / Mr. V singh
631763471d13 | DCH Ref. 4 :: ZIL/SUG./001 (20TCV020B01) | ZIL/SUG./001 (20TCV020B01) | OFF Season | 2026-05-14 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling & Lubrication work done.Joint seat replaceed.fitted on position. | 150 | Internal | Mr. Sushil singh / Mr. V singh
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | OFF Season | 2023-10-07 |  |  | Control valve seat & Body found rusty and Actuator spring damage. AFR filter damage. | Proper cleaning, Painting replace actuator spring & AFR filter with new. |  |  | Mr. Ritesh / Mr. V singh
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | OFF Season | 17/07/2023 |  |  | Control valve Seat & Body found rusty . AFR Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | OFF Season | 2024-05-10 |  |  | Control valve Seat & Body found rusty . AFR Dome Switch found Healthy.Found Actuator spring damage. | Proper cleaning, Painting & Lubrication work done. | 75 | Internal | Mr. Gaurav / Mr.V singh
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | OFF Season | 2025-05-28 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 300 | Internal | Mr. Anuj Kr / Mr. V singh
abc839905c17 | Ground floor 19 :: ZIL/SUG./001 (52 TCV 004) | ZIL/SUG./001 (52 TCV 004) | OFF Season | 2026-06-09 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 300 | Internal | Mr. Anirudh / Mr. V singh
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | OFF Season | 2023-10-07 |  |  | Control valve seat & Body found rusty and Actuator spring damage. AFR filter damage. | Proper cleaning, Painting replace actuator spring & AFR filter with new. |  |  | Mr. Ritesh / Mr. V singh
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | OFF Season | 17/07/2023 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | OFF Season | 2024-07-06 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. | 75 | Internal | Mr. Gaurav / Mr.V singh
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | OFF Season | 2025-05-29 |  |  | Control valve Seat & body found rusty. Seat passing & actuator O ring damage | Proper cleaning, overhauling ,checking Painting & Lubrication work done.seat replace with new | 4600 | Internal | Mr. Anuj Kr / Mr. V singh
b848afc7905c | Ground floor 19 :: ZIL/SUG./001 (52 FCV 009) | ZIL/SUG./001 (52 FCV 009) | OFF Season | 2026-06-07 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 300 | Internal | Mr. sushil / Mr. V singh
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | OFF Season | 2023-10-07 |  |  | Control valve seat & Body found rusty and Actuator spring damage. AFR filter damage. | Proper cleaning, Painting replace actuator spring & AFR filter with new. |  |  | Mr. Ritesh / Mr. V singh
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | OFF Season | 17/07/2023 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | OFF Season | 2024-07-06 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. | 75 | Internal | Mr. Gaurav / Mr.V singh
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | OFF Season | 2025-05-29 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 400 | Internal | Mr. Anuj Kr / Mr. V singh
d01294aa990d | Ground floor 19 :: ZIL/SUG./001 (52 XV 010) | ZIL/SUG./001 (52 XV 010) | OFF Season | 2026-06-07 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 300 | Internal | Mr. sushil / Mr. V singh
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | OFF Season | 2023-10-07 |  |  | Control valve seat & Body found rusty and Actuator spring damage. AFR filter damage. | Proper cleaning, Painting replace actuator spring & AFR filter with new. |  |  | Mr. Ritesh / Mr. V singh
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | OFF Season | 18/07/2023 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | OFF Season | 2024-06-26 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. Actuator end cap corner found broken. | Proper cleaning, Painting & Lubrication work done. AFR Filter replace with new. Actuator end cap fitted with warsal. | 80 | Internal | Mr. Gaurav / Mr.V singh
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | OFF Season | 2025-05-27 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 400 | Internal | Mr. Anuj Kr / Mr. V singh
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | OFF Season | 2026-06-09 |  |  | Control valve Seat & body found rusty. Nos-04 spring found broken. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 2000 | Internal | Mr. Anirudh / Mr. V singh
c4d124f8c5d8 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 011) | ZIL/SUG./001 (52 FCV 011) | OFF Season | 2026-06-09 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 300 | Internal | Mr. Anirudh / Mr. V singh
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | OFF Season | 2023-12-07 |  |  | Control valve seat & Body found rusty and Actuator spring damage. AFR filter damage. | Proper cleaning, Painting replace actuator spring & AFR filter with new. |  |  | Mr. Ritesh / Mr. V singh
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | OFF Season | 18/07/2023 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | OFF Season | 2024-06-29 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done. | 75 | Internal | Mr. Gaurav / Mr.V singh
cc7083d97c8d | Ground floor 19 :: ZIL/SUG./001 (52 XV 012) | ZIL/SUG./001 (52 XV 012) | OFF Season | 2025-05-27 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 400 | Internal | Mr. Anuj Kr / Mr. V singh
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | OFF Season | 2023-12-07 |  |  | Control valve seat & Body found rusty and Actuator spring damage. AFR filter damage. | Proper cleaning, Painting replace actuator spring & AFR filter with new. |  |  | Mr. Ritesh / Mr. V singh
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | OFF Season | 18/07/2023 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | OFF Season | 2024-06-29 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done. | 75 | Internal | Mr. Gaurav / Mr.V singh
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | OFF Season | 2025-05-27 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 400 | Internal | Mr. Anuj Kr / Mr. V singh
8ee862ebe50b | Ground floor 19 :: ZIL/SUG./001 (52 XV 025) | ZIL/SUG./001 (52 XV 025) | Season | 2025-12-12 |  |  | Caustic soda tank level transmitter diaphrgam wear-out. Not trim zero. | Level transmitter show false reading when tank is empty. Many time trim zero but show value is High alaram. |  | Internal | Anuj Srivastava. / V singh
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | OFF Season | 2023-12-07 |  |  | Control valve seat & Body found rusty and Actuator spring damage. AFR filter damage. | Proper cleaning, Painting replace actuator spring & AFR filter with new. |  |  | Mr. Ritesh / Mr. V singh
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | OFF Season | 19/07/2023 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
ad61c6278c96 | Ground floor 19 :: ZIL/SUG./001 (52 XV 026) | ZIL/SUG./001 (52 XV 026) | OFF Season | 2024-06-29 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done. | 75 | Internal | Mr. Gaurav / Mr.V singh
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | OFF Season | 2022-07-12 |  |  | Control valve seat & Body found rusty and Actuator spring damage. AFR filter damage. | Proper cleaning, Painting replace actuator spring & AFR filter with new. |  |  | Mr. Ritesh / Mr. V singh
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | OFF Season | 19/07/2023 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | OFF Season | 2024-06-28 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done. | 75 | Internal | Mr. Gaurav / Mr.V singh
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | OFF Season | 2025-05-26 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 400 | Internal | Mr. Anuj Kr / Mr. V singh
a073779ae039 | Ground floor 19 :: ZIL/SUG./001 (52 FCV 013) | ZIL/SUG./001 (52 FCV 013) | OFF Season | 2025-06-10 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 400 | Internal | Mr. Anuj Kr / Mr. V singh
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | OFF Season | 2023-12-07 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Ritesh / Mr. V singh
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | OFF Season | 19/07/2023 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | OFF Season | 2024-06-28 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done. | 75 | Internal | Mr. Gaurav / Mr.V singh
d71a9363dc58 | Ground floor 19 :: ZIL/SUG./001 (52 XV 014) | ZIL/SUG./001 (52 XV 014) | OFF Season | 2025-05-26 |  |  | Control valve Seat & body found rusty. Found 04 nos spring damage | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 1400 | Internal | Mr. Anuj Kr / Mr. V singh
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | OFF Season | 13/07/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Ritesh / Mr. V singh
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | OFF Season | 19/07/2023 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | OFF Season | 2024-06-29 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done. | 75 | Internal | Mr. Gaurav / Mr.V singh
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | OFF Season | 2025-05-30 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 400 | Internal | Mr. Anuj Kr / Mr. V singh
42f1e215b0a9 | Ground floor 19 :: ZIL/SUG./001 (52 XV 016) | ZIL/SUG./001 (52 XV 016) | OFF Season | 2026-06-09 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 400 | Internal | Mr. Anirudh / Mr. V singh
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | OFF Season | 13/07/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Ritesh / Mr. V singh
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | OFF Season | 19/07/2023 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | OFF Season | 2024-06-29 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done. | 75 | Internal | Mr. Gaurav / Mr.V singh
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | OFF Season | 2025-05-27 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 400 | Internal | Mr. Anuj Kr / Mr. V singh
ae6966e9a386 | Ground floor 19 :: ZIL/SUG./001 (15 XV 017) | ZIL/SUG./001 (15 XV 017) | OFF Season | 2026-06-09 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 400 | Internal | Mr. Anirudh / Mr. V singh
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | OFF Season | 13/07/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Ritesh / Mr. V singh
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | OFF Season | 19/07/2023 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | OFF Season | 2024-06-29 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 75 | Internal | Mr. Gaurav / Mr.V singh
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | OFF Season | 2025-05-27 |  |  | Control valve Seat & body found rusty. | Proper cleaning, overhauling ,checking Painting & Lubrication work done. | 400 | Internal | Mr. Anuj Kr / Mr. V singh
bb9c0e634560 | Ground floor 19 :: ZIL/SUG./001 (52 XV 037) | ZIL/SUG./001 (52 XV 037) | OFF Season | 2026-06-09 |  |  | Control valve Seat & Body found rusty .AFR found Healthy. | Proper cleaning, Lapping & Lubrication work done. | 300 | Internal | Mr. Anirudh / Mr.V singh
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | OFF Season | 13/07/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. AFR Filter replace with new. |  |  | Mr. Ritesh / Mr. V singh
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | OFF Season | 20/07/2023 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | OFF Season | 2024-06-29 |  |  | Control valve Seat & Body found rusty .Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 75 | Internal | Mr. Gaurav / Mr.V singh
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | OFF Season | 2025-05-30 |  |  | Control valve Seat & body found rusty. Gide pad wor-out | Proper cleaning, overhauling ,checking Painting & Lubrication work done.damage spare replace with new | 3500 | Internal | Mr. Anuj Kr / Mr. V singh
638ce12c909b | Ground floor 19 :: ZIL/SUG./001 (15 TCV 014) | ZIL/SUG./001 (15 TCV 014) | OFF Season | 2026-06-10 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Lapping & Lubrication work done. | 300 | Internal | Mr. Anirudh / Mr.V singh
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | OFF Season | 13/07/2023 |  |  | Control valve Seat & Body found rusty. AFR, SOV & Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | OFF Season | 20/07/2023 |  |  | Control valve Seat & Body found rusty. Dome Switch found Healthy. AFR Filter Damage. | Proper cleaning, Painting & Lubrication work done.AFR Filter replace with new. |  |  | Mr. Gaurav / Mr.V singh
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | OFF Season | 2024-05-10 |  |  | Control valve Seat & Body found rusty. Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | OFF Season | 2025-05-30 |  |  | Control valve Seat & Body found rusty. Found 01 spring brocken | Proper cleaning & Lubrication work done.spring & replace with new | 900 | Internal | Mr. Anuj Kumar / Mr.V singh
a28a7e94a1d3 | Ground floor 19 :: ZIL/SUG./001 (21TCV040B01) | ZIL/SUG./001 (21TCV040B01) | OFF Season | 2026-06-11 |  |  | Control valve Seat & Body found rusty .Nos-01 spring damage | Proper cleaning, Lapping & Lubrication work done. | 1000 | Internal | Mr. Anirudh / Mr.V singh
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | OFF Season | 14/07/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | OFF Season | 20/07/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | OFF Season | 2024-05-10 |  |  | Control valve Seat & Body found rusty. Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
757bff158fc7 | Ground floor 19 :: ZIL/SUG./001 (21LCV070B01) | ZIL/SUG./001 (21LCV070B01) | OFF Season | 2025-05-30 |  |  | Control valve Seat & Body found rusty. Found seat passing | Proper cleaning & Lubrication work done.seat replace with new | 17500 | Internal | Mr. Anuj Kumar / Mr.V singh
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | OFF Season | 2022-07-14 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Lapping & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | OFF Season | 2023-05-21 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Lapping & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | OFF Season | 2024-06-08 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Lapping & Lubrication work done. | 80 | Internal | Mr. Gaurav / Mr.V singh
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | OFF Season | 2025-06-04 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Lapping & Lubrication work done. | 150 | Internal | Mr. Anirudh / Mr.V singh
e4e5220db386 | Ground floor 19 :: ZIL/SUG./001/BCV_TCV_801 | ZIL/SUG./001/BCV_TCV_801 | OFF Season | 2026-06-08 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Lapping & Lubrication work done. | 300 | Internal | Mr. Anirudh / Mr.V singh
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | OFF Season | 14/07/2023 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Lapping & Lubrication work done. |  | Internal | Mr. Ritesh / Mr. V singh
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | OFF Season | 21/07/2023 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Lapping & Lubrication work done. |  | Internal | Mr. Gaurav / Mr.V singh
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | OFF Season | 2023-07-08 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Lapping & Lubrication work done. | 80 | Internal | Mr. Gaurav / Mr.V singh
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | OFF Season | 2025-06-04 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Lapping & Lubrication work done. | 150 | Internal | Mr. Anirudh / Mr.V singh
557e0f2b71c9 | Ground floor 19 :: ZIL/SUG./001/BCV_PCV_802 | ZIL/SUG./001/BCV_PCV_802 | OFF Season | 2026-06-08 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Lapping & Lubrication work done. | 300 | Internal | Mr. Anirudh / Mr.V singh
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | OFF Season | 2022-07-14 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | OFF Season | 21/07/2023 |  |  | Control valve Seat & Body found rusty .AFR diaphragm found damage & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. AFR Damage part replace with new |  |  | Mr. Gaurav / Mr.V singh
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | OFF Season | 2024-06-23 |  |  | Control valve Seat & Body found rusty .AFR diaphragm found damage & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. AFR Damage part replace with new | 150 | Internal | Mr. Gaurav / Mr.V singh
53f83b28fde1 | Ground floor 19 :: ZIL/SUG./001 (FCV-101) | ZIL/SUG./001 (FCV-101) | OFF Season | 2025-06-01 |  |  | Control valve Seat & Body found rusty .AFR diaphragm found damage & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. AFR Damage part replace with new | 200 | Internal | Mr. Gaurav / Mr.V singh
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | OFF Season | 14/07/2022 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | OFF Season | 2023-06-06 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | OFF Season | 2024-06-27 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning, Painting & Lubrication work done. | 200 | Internal | Mr. Gaurav / Mr.V singh
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | OFF Season | 2025-06-03 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning,Checking Painting & Lubrication work done. | 200 | Internal | Mr. Anirudh / Mr.V singh
084b3e862ac1 | Pan Feed Valve 3 :: ZIL/SUG./001 (11 BCV 020B01) | ZIL/SUG./001 (11 BCV 020B01) | OFF Season | 2026-05-13 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning,Checking Painting & Lubrication work done.joint seat replaced | 200 | Internal | Mr. Sushil / Mr.V singh
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | OFF Season | 2022-04-08 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | OFF Season | 2023-08-08 |  |  | Control valve Seat & Body found rusty .AFR & Positioner found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | OFF Season | 2024-05-08 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
da9ea21a639a | Ref. Condensor 57 :: ZIL/SUG./001 (022 XV 022G04) | ZIL/SUG./001 (022 XV 022G04) | OFF Season | 2025-04-21 |  |  | Control valve Seat & body found rusty. Seat found worn-out 80% | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 2500 | Internal | Mr. A Varma / Mr. V singh
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | OFF Season | 23/5/2022 |  |  | Control valve seat found rusty and actuator spring found damage. AFR Gauge found damage. | Proper cleaning & lubricaion work done . Actuator spring replace with new. |  |  | Mr. Gaurav / Mr.V singh
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | OFF Season | 16/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | OFF Season | 2024-05-11 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. Actuator Spring Found wornout. | Replace its spare .Proper cleaning & Lubrication work done. |  | Internal | Mr. Gaurav / Mr.V singh
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | OFF Season | 2025-04-21 |  |  | Control valve Seat & body found rusty. Seat found worn-out 80% | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 12500 | Internal | Mr. A Varma / Mr. V singh
42dac004a4f4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G01 ) | ZIL/SUG./001 (22XV 022 G01 ) | OFF Season | 2026-06-16 |  |  | Actuator nos-01 spring found brocken. & Valve seat found leaky. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done.Valve seat ok. Spring replace with new. | 2000 | Internal | Mr.Sushil singh / Mr. V singh
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | OFF Season | 23/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning, & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | OFF Season | 16/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | OFF Season | 2024-05-11 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | OFF Season | 2025-04-21 |  |  | Control valve Seat & body found rusty. Seat found worn-out 80% | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new.Dome switch repair work done. | 12500 | Internal | Mr. A Varma / Mr. V singh
fc6514957839 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G02 ) | ZIL/SUG./001 (22XV 022 G02 ) | OFF Season | 2026-06-17 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done.Valve seat ok. | 500 | Internal | Mr.Sushil singh / Mr. V singh
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | OFF Season | 23/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | OFF Season | 16/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | OFF Season | 2024-05-11 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | OFF Season | 2025-04-22 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 150 | Internal | Mr. A Varma / Mr.V singh
605f102ad327 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV 022 G03 ) | ZIL/SUG./001 (22XV 022 G03 ) | OFF Season | 2026-06-16 |  |  | Control valve Seat & Body found 100% worn-out .AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done.Valve seat work under process. | 500 | Internal | Mr.Sushil singh / Mr. V singh | New seat required
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | OFF Season | 24/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | OFF Season | 17/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | OFF Season | 2024-05-16 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  | Internal | Mr. Gaurav / Mr.V singh
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | OFF Season | 2025-04-25 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 150 | Internal | Mr. A Varma / Mr.V singh
4cd770d2a9d6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B03) | ZIL/SUG./001 (22XV023B03) | OFF Season | 2026-06-17 |  |  | Control valve Seat & Body found 100% worn-out .AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done.Repaired seat replaced. | 1000 | Internal | Mr.Sushil singh / Mr. V singh
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | OFF Season | 24/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication wortk done. |  |  | Mr. Gaurav / Mr.V singh
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | OFF Season | 17/05/2023 |  |  | Control valve Seat found rusty and Actuator spring damage. AFR diaphragm also damage. | Proper cleaning & Lubrication wortk done. Actuator spring & AFR diaphragm replace with new. |  |  | Mr. Gaurav / Mr.V singh
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | OFF Season | 2024-05-16 |  |  | Control valve Seat found wornout & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Replaced its seat with new spare. After Proper cleaning & Lubrication work done. |  | Internal | Mr. Gaurav / Mr.V singh
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | OFF Season | 2025-04-25 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. 02 nos cap o ring damage. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 650 | Internal | Mr. A Varma / Mr.V singh
b2d532e54e78 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B02) | ZIL/SUG./001 (22XV023B02) | OFF Season | 2026-06-18 |  |  | Control valve Seat & Body found OK.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. | 500 | Internal | Mr.Sushil singh / Mr. V singh
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | OFF Season | 24/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | OFF Season | 17/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | OFF Season | 2024-05-16 |  |  | Control valve Seat found wornout & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Replaced its seat with new spare. After Proper cleaning & Lubrication work done. | 12500 | Internal | Mr. Gaurav / Mr.V singh
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | OFF Season | 2024-04-26 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
5e14184cfee1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B04) | ZIL/SUG./001 (22XV023B04) | OFF Season | 2026-06-17 |  |  | Control valve Seat found Leakage.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done.Valve seat repaired. | 600 | Internal | Mr.Sushil singh / Mr. V singh
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | OFF Season | 24/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | OFF Season | 17/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | OFF Season | 2024-05-16 |  |  | Control valve Seat found wornout & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Replaced its seat with new spare. After Proper cleaning & Lubrication work done. | 12500 | Internal | Mr. Gaurav / Mr.V singh
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | OFF Season | 2024-04-26 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
b770b860ce1f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV023B05) | ZIL/SUG./001 (22XV023B05) | OFF Season | 2026-06-18 |  |  | Control valve Seat & Body found OK .AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. | 500 | Internal | Mr.Sushil singh / Mr. V singh
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | OFF Season | 25/5/2022 |  |  | Control valve Seat & Body found rusty . AFR, SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | OFF Season | 18/05/2023 |  |  | Control valve seat found rusty . SOV & Dome switch found healthy. Actuator spring found damage. | Proper cleaning & Lubrication work done . Actuator Spring change with new. |  |  | Mr. Gaurav / Mr.V singh
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | OFF Season | 2024-05-18 |  |  | Control valve Seat found wornout & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Replaced Control Valve seat with new spare. Proper cleaning & Lubrication work done. | 12500 | Internal | Mr. Gaurav / Mr.V singh
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | OFF Season | 2025-04-30 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
b375c53e076a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV020B04) | ZIL/SUG./001 (22XV020B04) | OFF Season | 2026-06-19 |  |  | Control valve Seat & Body found 100% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Sushil singh / Mr. V singh | New Seat
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | OFF Season | 2022-05-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | OFF Season | 2023-08-08 |  |  | Control valve Actuator found rusty and Actuator bottem pinion 'O' ring found damage .AFR & SOV found Healthy. | Actuator Proper cleaning , Lubrication & 'O' Ring kit replace with new. | 800 |  | Mr. Gaurav / Mr.V singh
9a103cf9b1fd | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G05) | ZIL/SUG./001 (22XV024G05) | OFF Season | 2025-05-02 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | OFF Season | 25/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | OFF Season | 18/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | OFF Season | 2024-05-29 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | OFF Season | 2025-05-03 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
994551843400 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G01 ) | ZIL/SUG./001 (22XV024G01 ) | OFF Season | 2026-06-20 |  |  | Control valve Seat & Body found 30% worn-out.AFR,SOV & Dome Switch found Healthy.Actuator piston o-ring Damage & Actuator inner side scratch. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done.Pistion o-ring replace with new. | 2500 | Internal | Mr.Sushil singh / Mr. V singh
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | OFF Season | 25/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | OFF Season | 18/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | OFF Season | 2024-05-29 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | OFF Season | 2025-05-03 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. Found gear pin damage. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work with gear pin replaced done. | 200 | Internal | Mr. A Varma / Mr.V singh
1263aad094e0 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G02) | ZIL/SUG./001 (22XV024G02) | OFF Season | 2026-06-20 |  |  | Control valve Seat & Body found 30% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. | 500 | Internal | Mr.Sushil singh / Mr. V singh
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | OFF Season | 25/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | OFF Season | 18/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | OFF Season | 2024-05-29 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | OFF Season | 2025-05-03 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
40d69f8d0541 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G03) | ZIL/SUG./001 (22XV024G03) | OFF Season | 2026-06-20 |  |  | Control valve Seat & Body found 20% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. | 500 | Internal | Mr.Sushil singh / Mr. V singh
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | OFF Season | 25/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | OFF Season | 18/05/2023 |  |  | Control valve seat found worn- out . AFR , SOV & Dome switch found healthy. | Proper cleaning & Lubrication work done. Valve seat replace with new. |  |  | Mr. Gaurav / Mr.V singh
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | OFF Season | 2024-05-29 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | OFF Season | 2025-05-02 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
619697b82989 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV024G04 ) | ZIL/SUG./001 (22XV024G04 ) | OFF Season | 2026-06-22 |  |  | Control valve Seat & Body found 30% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. | 500 | Internal | Mr.Sushil singh / Mr. V singh
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | OFF Season | 2022-06-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | OFF Season | 2023-09-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 |  | Mr. Gaurav / Mr.V singh
e08aa888ab59 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G04 ) | ZIL/SUG./001 (22XV025G04 ) | OFF Season | 2025-05-14 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | OFF Season | 26/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | OFF Season | 19/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | OFF Season | 2024-05-29 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. Found Actuator tention Spring wornout. | Proper cleaning & Lubrication work done. | 1000 | Internal | Mr. Gaurav / Mr.V singh
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | OFF Season | 2025-05-14 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
e04e2652c429 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G03 ) | ZIL/SUG./001 (22XV025G03 ) | OFF Season | 2026-06-20 |  |  | Control valve soft found broken.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done.Valve Seat repaired. | 1000 | Internal | Mr.Sushil singh / Mr. V singh
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | OFF Season | 26/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | OFF Season | 19/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | OFF Season | 2024-05-29 |  |  | Control valve Seat seat found worn out & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Replaced wornout seat with new spare. Proper cleaning & Lubrication work done. | 17150 | Internal | Mr. Gaurav / Mr.V singh
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | OFF Season | 2025-05-14 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
123458af3aa3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV025G02) | ZIL/SUG./001 (22XV025G02) | OFF Season | 2026-06-20 |  |  | Control valve seat worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Sushil singh / Mr. V singh | New seat
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | OFF Season | 2022-07-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | OFF Season | 2023-09-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | OFF Season | 2024-05-29 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 150 | Internal | Mr. Gaurav / Mr.V singh
69933f8b594b | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B01) | ZIL/SUG./001 (22XV035B01) | OFF Season | 2025-05-05 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | OFF Season | 26/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | OFF Season | 19/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | OFF Season | 2024-05-29 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | OFF Season | 2025-05-05 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
e881dbb65d0f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B02) | ZIL/SUG./001 (22XV035B02) | OFF Season | 2026-06-22 |  |  | Control valve seat & body found Ok.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. | 500 | Internal | Mr.Anuj Srivastava / Mr. V singh
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | OFF Season | 25/05/2023 |  |  | Control valve found scaledfull and Actuator spring damage. | Proper cleaning & replace spring with new. |  |  | Mr. Gaurav / Mr.V singh
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | OFF Season | 19/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | OFF Season | 2024-05-29 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | OFF Season | 2025-05-05 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
685c5d0f61ef | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B03) | ZIL/SUG./001 (22XV035B03) | OFF Season | 2026-06-22 |  |  | Control valve seat & body found 100% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Anuj Srivastava / Mr. V singh | New seat
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | OFF Season | 26/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | OFF Season | 22/5/2023 |  |  | Control valve seat found worn-out. AFR, Dome Switch ,Sov found healthy. | Proper cleaning & lubriction work done. Replace seat (PTFE) with new. |  |  | Mr. Gaurav / Mr.V singh
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | OFF Season | 2024-05-29 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | OFF Season | 2025-05-05 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
6578d8e773ed | Ref. Condensor 57 :: ZIL/SUG./001 (22XV035B04 ) | ZIL/SUG./001 (22XV035B04 ) | OFF Season | 2026-06-22 |  |  | Control valve seat & body found 100% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Anuj Srivastava / Mr. V singh | New seat
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | OFF Season | 13/08/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | OFF Season | 2023-10-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 |  | Mr. Gaurav / Mr.V singh
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | OFF Season | 2024-05-21 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | OFF Season | 2025-05-06 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. Found Seat & spring damage. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with replaced new seat with spring Lubrication work done. | 4500 | Internal | Mr. A Varma / Mr.V singh
b365c2364848 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B04) | ZIL/SUG./001 (22XV040B04) | OFF Season | 2026-06-20 |  |  | Control valve seat & body found 100% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Anuj Srivastava / Mr. V singh | New seat
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | OFF Season | 2022-05-27 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | OFF Season | 2023-05-22 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | OFF Season | 2024-05-29 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | OFF Season | 2025-05-06 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
419f270f6fe3 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B03) | ZIL/SUG./001 (22XV040B03) | OFF Season | 2026-06-20 |  |  | Control valve seat & body found OK.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. | 500 | Internal | Mr.Anuj Srivastava / Mr. V singh
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | OFF Season | 2022-05-27 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | OFF Season | 2023-05-22 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | OFF Season | 2024-05-29 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | OFF Season | 2025-05-06 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
a4faa312e150 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B02 ) | ZIL/SUG./001 (22XV040B02 ) | OFF Season | 2026-06-20 |  |  | Control valve seat & body found 100% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Anuj Srivastava / Mr. V singh | New seat
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | OFF Season | 27/5/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | OFF Season | 22/5/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | OFF Season | 2024-05-29 |  |  | Control valve Seat seat found worn out & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Replaced wornout seat with new spare .Proper cleaning & Lubrication work done. | 17150 | Internal | Mr. Gaurav / Mr.V singh
043e96a04bfc | Ref. Condensor 57 :: ZIL/SUG./001 (22XV040B01) | ZIL/SUG./001 (22XV040B01) | OFF Season | 2025-05-06 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | OFF Season | 2022-08-14 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 |  | Mr. Gaurav / Mr.V singh
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | OFF Season | 2023-08-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 150 |  | Mr. Gaurav / Mr.V singh
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | OFF Season | 2024-05-28 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 150 |  | Mr. Gaurav / Mr.V singh
aea32b2789c2 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B01) | ZIL/SUG./001 (22XV055B01) | OFF Season | 2025-04-30 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | OFF Season | 27/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | OFF Season | 2023-05-22 |  |  | Control valve seat found rusty & actuator spring damage. AFR , SOV, DOME Switch Found healthy. | Proper cleaning , Lubrication & Replace actuator spring with new. |  |  | Mr. Gaurav / Mr.V singh
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | OFF Season | 2023-05-18 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 150 | Internal | Mr. Gaurav / Mr.V singh
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | OFF Season | 2025-05-01 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
897673af0370 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B02) | ZIL/SUG./001 (22XV055B02) | OFF Season | 2026-06-19 |  |  | Control valve seat & body found 50% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Sushil Singh / Mr. V singh
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | OFF Season | 27/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | OFF Season | 2023-05-22 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | OFF Season | 2023-05-18 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | OFF Season | 2025-05-01 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 150 | Internal | Mr. A Varma / Mr.V singh
87f16ec4bdc4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B03) | ZIL/SUG./001 (22XV055B03) | OFF Season | 2026-06-19 |  |  | Control valve seat & body found 50% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done.Seat repaired. |  | Internal | Mr.Sushil Singh / Mr. V singh
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | OFF Season | 27/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | OFF Season | 2023-05-22 |  |  | Control valve Seat found wornout & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | OFF Season | 2024-05-18 |  |  | Control valve Seat found wornout & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Before Replacing spare PTFE Seat & Proper cleaning & Lubrication work done. | 12800 | Internal | Mr. Gaurav / Mr.V singh
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | OFF Season | 2025-05-01 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
9f30719e3bf8 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV055B04 ) | ZIL/SUG./001 (22XV055B04 ) | OFF Season | 2026-06-19 |  |  | Control valve seat & body found Ok.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done.Seat repaired. |  | Internal | Mr.Sushil Singh / Mr. V singh
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | OFF Season | 18/08/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | OFF Season | 2023-10-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | OFF Season | 2024-05-28 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
fc29bf7ede53 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B01) | ZIL/SUG./001 (22XV060B01) | OFF Season | 2025-04-27 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | OFF Season | 28/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | OFF Season | 24/5/2023 |  |  | Control valve Seat found rusty. Found actuator spring damage. | Proper cleaning, lubrication & replace actuator spring with new. |  |  | Mr. Gaurav / Mr.V singh
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | OFF Season | 2024-05-17 |  |  | Control valve Seat found rusty. AFR,SOV & Dome Switch found Healthy. | Proper cleaning, lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | OFF Season | 2025-04-27 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
c1dd23655faa | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B02) | ZIL/SUG./001 (22XV060B02) | OFF Season | 2026-06-17 |  |  | Control valve seat & body found 100% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Sushil Singh / Mr. V singh | new seat
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | OFF Season | 28/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | OFF Season | 24/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | OFF Season | 2024-05-17 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning, lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | OFF Season | 2025-04-29 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
4b9cc98c90b7 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B03) | ZIL/SUG./001 (22XV060B03) | OFF Season | 2026-06-17 |  |  | Control valve seat & body found 100% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Sushil Singh / Mr. V singh | new seat
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | OFF Season | 28/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | OFF Season | 24/5/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | OFF Season | 2024-05-17 |  |  | Control valve Seat found stem seat bolt wornout & Found actuator spring damage. | Repair seat & replace a tention spring with new. Proper cleaning, lubrication work done. | 600 | Internal | Mr. Gaurav / Mr.V singh
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | OFF Season | 2025-04-29 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
ddcebcd5f601 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV060B04 ) | ZIL/SUG./001 (22XV060B04 ) | OFF Season | 2026-06-17 |  |  | Control valve seat & body found 100% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Sushil Singh / Mr. V singh | new seat
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | OFF Season | 16/08/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | OFF Season | 2023-11-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | OFF Season | 2024-05-28 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
be8a090ce1a4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B01) | ZIL/SUG./001 (22XV065B01) | OFF Season | 2025-04-23 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | OFF Season | 28/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | OFF Season | 24/05/2023 |  |  | Control valve seat found worn-out. AFR,Dome switch ,Sov Found healthy. | Proper cleaning ,lubrication work done. Replace seat with new. |  |  | Mr. Gaurav / Mr.V singh
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | OFF Season | 2024-05-11 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | OFF Season | 2025-04-25 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. Found gear pin damage | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done & gear pin replaced | 200 | Internal | Mr. A Varma / Mr.V singh
44f4e38d8346 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B02) | ZIL/SUG./001 (22XV065B02) | OFF Season | 2026-06-17 |  |  | Control valve seat & body found 50% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Sushil Singh / Mr. V singh
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | OFF Season | 30/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | OFF Season | 25/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | OFF Season | 2024-05-11 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | OFF Season | 2025-04-25 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. Dome switch not working | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done.dome repair work are done. | 200 | Internal | Mr. A Varma / Mr.V singh
b0105263b96f | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B03) | ZIL/SUG./001 (22XV065B03) | OFF Season | 2026-06-16 |  |  | Control valve seat & body found 50% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Sushil Singh / Mr. V singh
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | OFF Season | 30/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | OFF Season | 25/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | OFF Season | 2024-05-11 |  |  | Control valve Seat found rusty. Found actuator spring damage. | Proper cleaning, lubrication & replace actuator spring with new. | 600 | Internal | Mr. Gaurav / Mr.V singh
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | OFF Season | 2025-04-25 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 150 | Internal | Mr. A Varma / Mr.V singh
5565bb63c995 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV065B04 ) | ZIL/SUG./001 (22XV065B04 ) | OFF Season | 2026-06-16 |  |  | Control valve seat & body found 20% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Sushil Singh / Mr. V singh
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | OFF Season | 2022-07-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | OFF Season | 2023-11-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | OFF Season | 2024-05-27 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
b1fbf73ae090 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B01) | ZIL/SUG./001 (22XV070B01) | OFF Season | 2025-05-03 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | OFF Season | 30/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | OFF Season | 26/05/2023 |  |  | Control valve Seat found worn-out. AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. Seat replace with new. |  |  | Mr. Gaurav / Mr.V singh
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | OFF Season | 2024-06-01 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | OFF Season | 2025-05-03 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
8da9f9df239a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B02) | ZIL/SUG./001 (22XV070B02) | OFF Season | 2026-06-20 |  |  | Control valve seat & body found 20% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Aunj Srivastava / Mr. V singh
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | OFF Season | 30/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | OFF Season | 26/05/2023 |  |  | Control valve seat found rusty . Found Actuator spring damage. AFR ,SOV, Dome Switch healthy. | Proper cleaning & Lubrication . Replace actuator spring with new. |  |  | Mr. Gaurav / Mr.V singh
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | OFF Season | 2024-06-01 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | OFF Season | 2025-05-02 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
6c66b1aad269 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B03) | ZIL/SUG./001 (22XV070B03) | OFF Season | 2026-06-20 |  |  | Control valve seat & body found 100% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Aunj Srivastava / Mr. V singh
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | OFF Season | 30/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | OFF Season | 26/05/2023 |  |  | Control valve found scaledfull and control valve seat worn-out. | Proper cleaning & replace seat with new. |  |  | Mr. Gaurav / Mr.V singh
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | OFF Season | 2024-06-01 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | OFF Season | 2025-05-02 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 150 | Internal | Mr. A Varma / Mr.V singh
e7a8515694d5 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV070B04 ) | ZIL/SUG./001 (22XV070B04 ) | OFF Season | 2026-06-20 |  |  | Control valve seat & body found 20% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Aunj Srivastava / Mr. V singh
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | OFF Season | 14/08/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | OFF Season | 2023-11-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | OFF Season | 2024-06-01 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
a38efd3909f6 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B01 ) | ZIL/SUG./001 (22XV045B01 ) | OFF Season | 2025-05-08 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 150 | Internal | Mr. A Varma / Mr.V singh
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | OFF Season | 31/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | OFF Season | 26/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | OFF Season | 2024-06-03 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | OFF Season | 2025-05-09 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
e9e63e1171f1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B02 ) | ZIL/SUG./001 (22XV045B02 ) | OFF Season | 2026-06-19 |  |  | Control valve seat & body found 30% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Aunj Srivastava / Mr. V singh
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | OFF Season | 31/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | OFF Season | 26/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | OFF Season | 2024-06-03 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | OFF Season | 2025-05-09 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
4f49fa96e155 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B03) | ZIL/SUG./001 (22XV045B03) | OFF Season | 2026-06-20 |  |  | Control valve seat & body found 50% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Aunj Srivastava / Mr. V singh
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | OFF Season | 31/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | OFF Season | 26/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | OFF Season | 2024-06-03 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | OFF Season | 2025-05-09 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
de442ebe8ae1 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B04) | ZIL/SUG./001 (22XV045B04) | OFF Season | 2026-06-20 |  |  | Control valve seat & body found 30% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Aunj Srivastava / Mr. V singh
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | OFF Season | 31/05/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | OFF Season | 27/05/2023 |  |  | Control valve Seat found rusty .AFR,SOV & Dome Switch found Healthy. Actuator Spring found damage. | Proper cleaning & Lubrication work done. Replace actuator spring with new. |  |  | Mr. Gaurav / Mr.V singh
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | OFF Season | 2024-06-03 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | OFF Season | 2025-05-10 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | Season | 2026-01-21 |  |  | Control valve Seat found leakage | Replaced with new |  | Internal | Mr. Anuj Kr. / Mr.V singh
9d56fabe49bb | Ref. Condensor 57 :: ZIL/SUG./001 (22XV045B05 ) | ZIL/SUG./001 (22XV045B05 ) | OFF Season | 2026-06-20 |  |  | Control valve seat & body found ok.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Aunj Srivastava / Mr. V singh
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | OFF Season | 13/08/2022 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | OFF Season | 2023-11-08 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | OFF Season | 2024-06-03 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
5dad742f24de | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B01) | ZIL/SUG./001 (22XV050B01) | OFF Season | 2025-05-07 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | OFF Season | 2022-01-06 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | OFF Season | 27/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | OFF Season | 2024-06-04 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | OFF Season | 2025-05-07 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
8da93aa17979 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B02 ) | ZIL/SUG./001 (22XV050B02 ) | OFF Season | 2026-06-19 |  |  | Control valve seat & body found 60% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Aunj Srivastava / Mr. V singh
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | OFF Season | 2022-01-06 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | OFF Season | 27/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | OFF Season | 2024-06-04 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | OFF Season | 2025-05-07 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
dfae3c9e283a | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B03) | ZIL/SUG./001 (22XV050B03) | OFF Season | 2026-06-19 |  |  | Control valve seat & body found 50% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Aunj Srivastava / Mr. V singh
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | OFF Season | 2022-01-06 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | OFF Season | 27/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | OFF Season | 2024-06-04 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | OFF Season | 2025-05-08 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 100 | Internal | Mr. A Varma / Mr.V singh
f9f11926a2e9 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B04) | ZIL/SUG./001 (22XV050B04) | OFF Season | 2026-06-19 |  |  | Control valve seat & body found 50% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Aunj Srivastava / Mr. V singh
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | OFF Season | 2022-01-06 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | OFF Season | 27/05/2023 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | OFF Season | 2024-06-04 |  |  | Control valve Seat & Body found rusty .AFR,SOV & Dome Switch found Healthy. | Proper cleaning & Lubrication work done. | 100 | Internal | Mr. Gaurav / Mr.V singh
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | OFF Season | 2025-05-08 |  |  | Control valve Seat & Body found rusty .AFR & SOV found Healthy. | Actuator ,Spring ,seat Proper cleaning & SOV overhauling with Lubrication work done. | 200 | Internal | Mr. A Varma / Mr.V singh
edfa40e24fb4 | Ref. Condensor 57 :: ZIL/SUG./001 (22XV050B05 ) | ZIL/SUG./001 (22XV050B05 ) | OFF Season | 2026-06-19 |  |  | Control valve seat & body found 50% worn-out.AFR,SOV & Dome Switch found Healthy. | Actuator,gear-box,afr,Dome switch dismantle,cleaning & overhauling & assembling work done. |  | Internal | Mr.Aunj Srivastava / Mr. V singh
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | OFF Season | 2022-01-07 |  |  | Power Cylender Body found rusty . AFR & SOV found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | OFF Season | 2023-05-24 |  |  | Power Cylender Body found rusty . AFR & SOV found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | OFF Season | 2024-07-19 |  |  | Power Cylender found leakage through the Inlet conector. AFR & SOV found Healthy. | Replace kit with spare part .Proper cleaning,Checking & Lubrication work done. | 6100 | Internal | Mr. Gaurav / Mr.V singh
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Season | 2024-12-11 |  |  | Sov problem | Replaced with new | 900 | Internal | Mr. Anuj / Mr.V singh
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Season | 2025-01-03 |  |  | Power Cylinder Linkage the O/L Conector. | Replaced kit take in line | 6100 | Internal | Mr. Anirudh / Mr.V singh
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | OFF Season | 2025-06-05 |  |  | Power Cylender Body found rusty . AFR & SOV found Healthy.found lenk bolt Damage & rotary valve not work | Proper cleaning, Painting & Lubrication work done.len bolt & rotary replace with new | 1500 | Internal | Mr. Anirudh / Mr.V singh
ec3241fc59ff | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO1) | ZIL/SUG./001 (18 LCV 20 BO1) | Season | 2025-11-18 |  |  | Power cylinder manual mode not working | Rotary valve replaced it take in line. | 600 | Internal | Mr. Anuj Kr. / Mr.V singh
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | OFF Season | 2022-02-07 |  |  | Power Cylender Body found rusty . AFR & SOV found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | ON Season | 2023-10-02 |  |  | Power cylender found leakage. | Gland packing replace with new . |  |  | Mr. Gaurav / Mr.V singh
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | OFF Season | 2023-08-02 |  |  | Power Cylender Body found rusty . AFR & SOV found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | OFF Season | 2024-07-18 |  |  | Power Cylender Body ok . AFR & SOV found Healthy. | Proper cleaning, Painting & Lubrication work done. | 250 | Internal | Mr. Gaurav / Mr.V singh
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Season | 2025-02-12 |  |  | SOV problem | Repair it take line | 250 | Internal | Mr. Sushil Mr.V singh
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | OFF Season | 2025-06-05 |  |  | Power Cylender Body found rusty . AFR found damage. | Proper cleaning, overhauling & Lubrication work done. | 250 | Internal | Mr. Anirudh / Mr.V singh
040f80bbc08a | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO2) | ZIL/SUG./001 (18 LCV 20 BO2) | Season | 2025-11-19 |  |  | Power Cylender SOV Not working | Repair it take line | 1800 | Internal | Mr. Anuj Kr./ Mr.V singh
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | OFF Season | 2022-04-07 |  |  | Power Cylender Body found rusty . AFR & SOV found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Ritesh / Mr. V singh
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | OFF Season | 2023-08-03 |  |  | Power Cylender Body found rusty . AFR & SOV found Healthy. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr.V singh
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | OFF Season | 2024-07-18 |  |  | Power Cylender Body ok . AFR & SOV found Healthy. | Proper cleaning, Checking & Lubrication work done. | 250 | Internal | Mr. Gaurav / Mr.V singh
66297fc4d293 | Crystillizer03 :: ZIL/SUG./001 (18 LCV 20 BO3) | ZIL/SUG./001 (18 LCV 20 BO3) | OFF Season | 2025-06-06 |  |  | Power Cylender Body found rusty . AFR & SOV found Healthy. | Proper cleaning, Overhauling work done. | 500 | Internal | Mr. Anirudh / Mr.V singh
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | OFF Season | 2023-06-26 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | OFF Season | 2024-07-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
94b8925ee290 | Ref Flow Meter h :: ZIL/SUG./01/16_FT_130_B01 | ZIL/SUG./01/16_FT_130_B01 | OFF Season | 2025-06-13 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | OFF Season | 2023-06-26 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | OFF Season | 2024-07-30 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
e7f1f3e6a995 | Ref Flow Meter h :: ZIL/SUG./01/15FT027 | ZIL/SUG./01/15FT027 | OFF Season | 2025-06-13 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | OFF Season | 2023-06-26 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | OFF Season | 2024-07-30 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
2072c1fbc922 | Ref Flow Meter h :: ZIL/SUG./01/20FT005 | ZIL/SUG./01/20FT005 | OFF Season | 2025-06-14 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | OFF Season | 2023-06-26 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | OFF Season | 2024-07-30 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
0155572917de | Ref Flow Meter h :: ZIL/SUG./01/40FT003 | ZIL/SUG./01/40FT003 | OFF Season | 2025-06-14 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | OFF Season | 2023-06-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | OFF Season | 2024-07-31 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
1fd6a2e688fc | Ref Flow Meter h :: ZIL/SUG./01/40FT101 | ZIL/SUG./01/40FT101 | OFF Season | 2025-06-14 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | OFF Season | 2023-06-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | OFF Season | 2024-07-31 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
cb893e239628 | Ref Flow Meter h :: ZIL/SUG./01/40FT201 | ZIL/SUG./01/40FT201 | OFF Season | 2025-06-18 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | OFF Season | 2023-06-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | OFF Season | 2024-07-29 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
2c380a6b658e | Ref Flow Meter h :: ZIL/SUG./01/52FT009 | ZIL/SUG./01/52FT009 | OFF Season | 2025-06-14 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | OFF Season | 2023-06-27 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | OFF Season | 2024-07-30 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
a950c822dcf4 | Ref Flow Meter h :: ZIL/SUG./01/52FT011 | ZIL/SUG./01/52FT011 | OFF Season | 2025-06-14 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | OFF Season | 2023-06-28 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | OFF Season | 2024-07-29 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
5835d3ce44c2 | Ref Flow Meter h :: ZIL/SUG./01/52FT013 | ZIL/SUG./01/52FT013 | OFF Season | 2025-06-14 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | OFF Season | 2023-06-28 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | OFF Season | 2024-07-31 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
1c3773dcdaec | Ref Flow Meter h :: ZIL/SUG./01/52FT101 | ZIL/SUG./01/52FT101 | OFF Season | 2025-06-17 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | OFF Season | 2023-06-28 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | OFF Season | 2024-07-31 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
a1a8aa3809ce | Ref Flow Meter h :: ZIL/SUG./01/52FT201 | ZIL/SUG./01/52FT201 | OFF Season | 2025-06-18 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | OFF Season | 2023-06-28 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | OFF Season | 2024-07-31 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | OFF Season | 2025-06-18 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
79215e3dac44 | Ref Flow Meter h :: ZIL/SUG./52FT301 | ZIL/SUG./52FT301 | OFF Season | 2026-05-18 |  |  | Flow meter flow tube found sugar scalling. | Cleaend Sensor | 100 | Internal | Mr. Sushil Singh/ Mr.V singh
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | OFF Season | 2023-06-29 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | OFF Season | 2024-08-07 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
2971b643188c | Ref Flow Meter h :: ZIL/SUG./01/FT-101 | ZIL/SUG./01/FT-101 | OFF Season | 2025-06-20 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | OFF Season | 2023-06-29 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | OFF Season | 2024-08-07 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
9b58b5d21863 | Ref Flow Meter h :: ZIL/SUG./01/FT-102 | ZIL/SUG./01/FT-102 | OFF Season | 2025-06-20 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | OFF Season | 2023-06-29 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | OFF Season | 2024-08-08 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
5fe3890252f6 | Ref Flow Meter h :: ZIL/SUG./01/FT-202 | ZIL/SUG./01/FT-202 | OFF Season | 2025-06-20 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | OFF Season | 2023-06-30 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | OFF Season | 2024-08-08 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
2bb5d3c2977c | Ref Flow Meter h :: ZIL/SUG./01/FT-301 | ZIL/SUG./01/FT-301 | OFF Season | 2025-06-19 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | OFF Season | 2023-06-30 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | OFF Season | 2024-08-08 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
22e44c5a04db | Ref Flow Meter h :: ZIL/SUG./01/FT-302 | ZIL/SUG./01/FT-302 | OFF Season | 2025-06-19 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | OFF Season | 2023-06-30 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Ritesh / Mr.V singh
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | OFF Season | 2024-08-08 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Gaurav / Mr.V singh
253224e49b3f | Ref Flow Meter h :: ZIL/SUG./01/FT-303 | ZIL/SUG./01/FT-303 | OFF Season | 2025-06-19 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh / Mr.V singh
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | OFF Season | 2023-05-24 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | OFF Season | 2024-09-21 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | OFF Season | 2024-09-22 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | OFF Season | 2025-04-01 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a32dcd230a83 | conntroller - :: ZIL/GSM/C-1/01 | ZIL/GSM/C-1/01 | OFF Season | 2026-04-13 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | OFF Season | 2023-05-24 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | OFF Season | 2024-09-21 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | OFF Season | 2024-09-22 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | OFF Season | 2025-04-01 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | OFF Season | 2026-04-07 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
eadbc93a4fe8 | conntroller - :: ZIL/GSM/C-2/02 | ZIL/GSM/C-2/02 | OFF Season | 2026-04-13 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | OFF Season | 2023-05-24 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | OFF Season | 2024-04-19 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | OFF Season | 2024-09-21 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | OFF Season | 2025-03-31 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
c66da537a3f4 | conntroller - :: ZIL/GSM/C-3/03 | ZIL/GSM/C-3/03 | OFF Season | 2026-04-07 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | OFF Season | 2023-05-24 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | OFF Season | 2024-04-21 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | OFF Season | 2024-08-05 |  |  | Found PSU-2 output supply failed. | SMPS replace with new one | 6232 | Internal | Sushil Singh/MR. V. Singh
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | OFF Season | 2024-09-22 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | OFF Season | 2025-03-31 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d2b830397ff3 | conntroller - :: ZIL/GSM/C-4/04 | ZIL/GSM/C-4/04 | OFF Season | 2026-04-11 |  |  | Controller,communication module ,external battery,SMPS, ACON converter found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | OFF Season | 2024-08-23 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | OFF Season | 2024-08-26 |  |  | All loop test found ok | Marshaling to field JB loop checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | OFF Season | 2024-09-30 |  |  | All euipment found helthy. | Check all transmitter ,motor rpm & load found ok. |  | Internal | Sushil Singh/MR. V. Singh
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | OFF Season | 2025-04-02 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | OFF Season | 2025-07-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | OFF Season | 2025-08-04 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
ce05f2903868 | conntroller - :: ZIL/GSM/C-1/PANEL-1 | ZIL/GSM/C-1/PANEL-1 | OFF Season | 2026-04-13 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | OFF Season | 2024-08-23 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | OFF Season | 2024-08-26 |  |  | All loop test found ok | Marshaling to field JB loop checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | OFF Season | 2024-09-28 |  |  | All euipment found helthy. | Check all transmitter ,motor rpm & load found ok. |  | Internal | Sushil Singh/MR. V. Singh
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | OFF Season | 2025-04-02 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | OFF Season | 2025-07-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | OFF Season | 2025-08-04 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
21720f1a39ef | conntroller - :: ZIL/GSM/C-1/PANEL-2 | ZIL/GSM/C-1/PANEL-2 | OFF Season | 2026-04-13 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | OFF Season | 2024-08-23 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | OFF Season | 2024-09-28 |  |  | All euipment found helthy. | Check all motor ,control valve,postioner,limit switch feedback are found ok. |  | Internal | Sushil Singh/MR. V. Singh
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | OFF Season | 2025-04-02 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | OFF Season | 2025-07-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | OFF Season | 2025-08-04 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
734e1015a686 | conntroller - :: ZIL/GSM/C-1/PANEL-3 | ZIL/GSM/C-1/PANEL-3 | OFF Season | 2026-04-13 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | OFF Season | 2024-08-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | OFF Season | 2024-09-28 |  |  | All euipment found helthy. | Check all motor ,control valve,postioner,limit switch feedback are found ok. |  | Internal | Sushil Singh/MR. V. Singh
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | OFF Season | 2025-04-04 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | OFF Season | 2025-07-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | OFF Season | 2025-08-05 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
e226e3801516 | conntroller - :: ZIL/GSM/C-1/PANEL-4 | ZIL/GSM/C-1/PANEL-4 | OFF Season | 2026-04-13 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | OFF Season | 2024-08-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | OFF Season | 2024-09-28 |  |  | All euipment found helthy. | Check all motor ,control valve,postioner,limit switch feedback are found ok. |  | Internal | Sushil Singh/MR. V. Singh
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | OFF Season | 2025-04-04 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | OFF Season | 2025-07-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | OFF Season | 2025-08-13 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
f7af7c819c63 | conntroller - :: ZIL/GSM/C-1/PANEL-5 | ZIL/GSM/C-1/PANEL-5 | OFF Season | 2026-04-13 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | OFF Season | 2024-08-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | OFF Season | 2024-09-28 |  |  | All euipment found helthy. | Check all motor ,control valve,postioner,SOV command are found ok. |  | Internal | Sushil Singh/MR. V. Singh
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | OFF Season | 2025-04-04 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | OFF Season | 2025-07-22 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | OFF Season | 2025-08-13 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
2e78e356479d | conntroller - :: ZIL/GSM/C-1/PANEL-6 | ZIL/GSM/C-1/PANEL-6 | OFF Season | 2026-04-13 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | OFF Season | 2024-08-25 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | OFF Season | 2024-09-28 |  |  | All euipment found helthy. | Check all motor ,control valve,postioner,SOV command are found ok. |  | Internal | Sushil Singh/MR. V. Singh
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | OFF Season | 2025-04-04 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | OFF Season | 2025-07-22 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | OFF Season | 2025-08-14 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
1a91ce41fc0e | conntroller - :: ZIL/GSM/C-1/PANEL-7 | ZIL/GSM/C-1/PANEL-7 | OFF Season | 2026-04-13 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | OFF Season | 2024-08-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | OFF Season | 2024-10-18 |  |  | All euipment found helthy. | Check all transmitter ,motor rpm & load found ok. |  | Internal | Sushil Singh/MR. V. Singh
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | OFF Season | 2025-04-02 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | OFF Season | 2025-07-23 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | OFF Season | 2025-08-06 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
df07c42cffe6 | conntroller - :: ZIL/GSM/C-2/PANEL-1 | ZIL/GSM/C-2/PANEL-1 | OFF Season | 2026-04-14 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | OFF Season | 2024-08-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | OFF Season | 2024-09-30 |  |  | All euipment found helthy. | Check all transmitter ,motor rpm & load found ok. |  | Internal | Sushil Singh/MR. V. Singh
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | OFF Season | 2025-04-02 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | OFF Season | 2025-07-23 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | OFF Season | 2025-08-06 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
8af012e10964 | conntroller - :: ZIL/GSM/C-2/PANEL-2 | ZIL/GSM/C-2/PANEL-2 | OFF Season | 2026-04-14 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | OFF Season | 2024-08-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | OFF Season | 2024-09-29 |  |  | All euipment found helthy. | Check all motor & control valve feedback found ok. |  | Internal | Sushil Singh/MR. V. Singh
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | OFF Season | 2025-04-02 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | OFF Season | 2025-07-23 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | OFF Season | 2025-08-06 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
66eb3a3cc50d | conntroller - :: ZIL/GSM/C-2/PANEL-3 | ZIL/GSM/C-2/PANEL-3 | OFF Season | 2026-04-14 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | OFF Season | 2024-08-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | OFF Season | 2024-09-29 |  |  | All euipment found helthy. | Check all motor & control valve feedback found ok. |  | Internal | Sushil Singh/MR. V. Singh
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | OFF Season | 2025-04-02 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | OFF Season | 2025-07-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | OFF Season | 2025-08-07 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
8f7328846fe0 | conntroller - :: ZIL/GSM/C-2/PANEL-4 | ZIL/GSM/C-2/PANEL-4 | OFF Season | 2026-04-14 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | OFF Season | 2024-08-22 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | OFF Season | 2024-09-29 |  |  | All euipment found helthy. | Check all motor & control valve command found ok. |  | Internal | Sushil Singh/MR. V. Singh
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | OFF Season | 2025-04-04 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | OFF Season | 2025-07-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | OFF Season | 2025-08-07 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
a6f4aab960b2 | conntroller - :: ZIL/GSM/C-2/PANEL-5 | ZIL/GSM/C-2/PANEL-5 | OFF Season | 2026-04-14 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | OFF Season | 2024-08-22 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | OFF Season | 2024-09-29 |  |  | All euipment found helthy. | Check all motor & control valve command found ok. |  | Internal | Sushil Singh/MR. V. Singh
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | OFF Season | 2025-04-04 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | OFF Season | 2025-07-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | OFF Season | 2025-08-07 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
1b902e56fe02 | conntroller - :: ZIL/GSM/C-2/PANEL-6 | ZIL/GSM/C-2/PANEL-6 | OFF Season | 2026-04-14 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | OFF Season | 2023-05-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Gaurav/MR. V. Singh
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | OFF Season | 2024-04-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | OFF Season | 2024-08-22 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | OFF Season | 2024-09-21 |  |  | All loop test found ok | Marshaling to field JB loop checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | OFF Season | 2024-09-29 |  |  | All euipment found helthy. | Check all motor & control valve command found ok. |  | Internal | Sushil Singh/MR. V. Singh
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | OFF Season | 2025-04-04 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | OFF Season | 2025-07-24 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | OFF Season | 2025-08-08 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
ad6cda468b78 | conntroller - :: ZIL/GSM/C-2/PANEL-7 | ZIL/GSM/C-2/PANEL-7 | OFF Season | 2026-04-14 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | OFF Season | 2023-05-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness check work are completed. |  | Internal | Sushil Singh/MR. V. Singh
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | OFF Season | 2024-04-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | OFF Season | 2024-08-13 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | OFF Season | 2024-09-21 |  |  | All loop test found ok | Marshaling to field JB loop checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | OFF Season | 2024-10-18 |  |  | All euipment found helthy. | Check all transmitter motor & control valve live value found ok. |  | Internal | Sushil Singh/MR. V. Singh
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | Season | 2025-02-10 |  |  | AI Module channel malfunctioning | Check & Replace AI Card With new. Problem reactify. | 38540 | Internal | MR. V. Singh
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | OFF Season | 2025-03-31 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | OFF Season | 2025-07-17 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed.& mill bearing temp. sensor ferrul & lug punching work are completed. |  | Internal | Sushil Singh/MR. V. Singh
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | OFF Season | 2025-07-29 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
6da378442da1 | conntroller - :: ZIL/GSM/C-3/PANEL-1 | ZIL/GSM/C-3/PANEL-1 | OFF Season | 2026-04-07 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | OFF Season | 2023-05-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness check work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | OFF Season | 2024-04-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | OFF Season | 2024-08-14 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | OFF Season | 2024-10-18 |  |  | All euipment found helthy. | Check all motor & control valve feedback found ok. |  | Internal | Sushil Singh/MR. V. Singh
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | OFF Season | 2025-04-04 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | OFF Season | 2025-03-31 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | OFF Season | 2025-07-17 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | OFF Season | 2025-07-29 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
a747f65eadc3 | conntroller - :: ZIL/GSM/C-3/PANEL-2 | ZIL/GSM/C-3/PANEL-2 | OFF Season | 2026-04-07 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | OFF Season | 2023-05-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | OFF Season | 2024-04-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | OFF Season | 2024-08-15 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | OFF Season | 2024-08-17 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | OFF Season | 2024-10-01 |  |  | All euipment found helthy. | Check all motor & control valve command found ok. |  | Internal | Sushil Singh/MR. V. Singh
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | OFF Season | 2025-03-31 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | OFF Season | 2025-07-18 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | OFF Season | 2025-07-30 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
b7258927d4e1 | conntroller - :: ZIL/GSM/C-3/PANEL-3 | ZIL/GSM/C-3/PANEL-3 | OFF Season | 2026-04-07 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | OFF Season | 2023-05-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | OFF Season | 2024-04-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | OFF Season | 2024-08-17 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | OFF Season | 2024-10-01 |  |  | All euipment found helthy. | Check all transmitter motor & control valve live value found ok. |  | Internal | Sushil Singh/MR. V. Singh
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | OFF Season | 2025-04-02 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | OFF Season | 2025-07-26 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | OFF Season | 2025-08-18 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
4d6ef1105f70 | conntroller - :: ZIL/GSM/C-4/PANEL-1 | ZIL/GSM/C-4/PANEL-1 | OFF Season | 2026-04-11 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | OFF Season | 2023-05-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | OFF Season | 2024-04-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | OFF Season | 2024-08-20 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | OFF Season | 2024-09-30 |  |  | All euipment found helthy. | Check all motor & control valve feedback found ok. |  | Internal | Sushil Singh/MR. V. Singh
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | OFF Season | 2025-04-02 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | OFF Season | 2025-07-26 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | OFF Season | 2025-08-18 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
d66d1b71b9f4 | conntroller - :: ZIL/GSM/C-4/PANEL-2 | ZIL/GSM/C-4/PANEL-2 | OFF Season | 2026-04-11 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | OFF Season | 2023-05-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | OFF Season | 2024-04-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | OFF Season | 2024-08-20 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | OFF Season | 2024-09-30 |  |  | All euipment found helthy. | Check all motor & control valve feedback found ok. |  | Internal | Sushil Singh/MR. V. Singh
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | OFF Season | 2025-04-03 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | OFF Season | 2025-07-26 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | OFF Season | 2025-08-19 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
63e563bfb640 | conntroller - :: ZIL/GSM/C-4/PANEL-3 | ZIL/GSM/C-4/PANEL-3 | OFF Season | 2026-04-11 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | OFF Season | 2023-05-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | OFF Season | 2024-04-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | OFF Season | 2024-08-20 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | OFF Season | 2024-09-30 |  |  | All euipment found helthy. | Check all motor & control valve command found ok. |  | Internal | Sushil Singh/MR. V. Singh
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | OFF Season | 2025-04-03 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | OFF Season | 2025-07-28 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | OFF Season | 2025-08-19 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
d6689fb09412 | conntroller - :: ZIL/GSM/C-4/PANEL-4 | ZIL/GSM/C-4/PANEL-4 | OFF Season | 2026-04-11 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | OFF Season | 2023-05-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | OFF Season | 2024-04-19 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | OFF Season | 2024-08-21 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | OFF Season | 2024-09-30 |  |  | All euipment found helthy. | Check all motor & control valve command found ok. |  | Internal | Sushil Singh/MR. V. Singh
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | OFF Season | 2025-04-03 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | OFF Season | 2025-07-28 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | OFF Season | 2025-08-20 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
65fe634cebfb | conntroller - :: ZIL/GSM/C-4/PANEL-5 | ZIL/GSM/C-4/PANEL-5 | OFF Season | 2026-04-11 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | OFF Season | 2023-05-22 |  |  | Controller & All module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Mr. Gaurav/MR. V. Singh
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | OFF Season | 2024-04-24 |  |  | All module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | OFF Season | 2024-09-30 |  |  | Controller & All module found healthy. | Proper checking, cleaning & Panel TB module connection tightness checking work are completed. All Fuse inserted TB in panel. |  | Internal | Sushil Singh/MR. V. Singh
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | OFF Season | 2025-04-03 |  |  | Controller & All module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | OFF Season | 2025-07-28 |  |  | All cluster & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
1f7a39c51ee3 | conntroller - :: ZIL/GSM/BRS | ZIL/GSM/BRS | OFF Season | 2026-04-11 |  |  | All module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | OFF Season | 2023-05-19 |  |  | All euipment found helthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | OFF Season | 2024-04-23 |  |  | Controller & module found healthy. | Proper checking, cleaning & safely shutdown work are completed. |  | Internal | Sushil Singh/MR. V. Singh
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | OFF Season | 2024-08-06 |  |  | All euipment found helthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. Start the panel. |  | Internal | Sushil Singh/MR. V. Singh
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | OFF Season | 2025-04-03 |  |  | Controller & module found healthy. | Proper checking, cleaning & safely shutdown work are completed. |  | Internal | Sushil Singh/MR. V. Singh
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | OFF Season | 2025-07-29 |  |  | All euipment found helthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | OFF Season | 2025-08-20 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | OFF Season | 2025-09-20 |  |  | SMPS was found unhealthy.Not ON | SMPS was replace with new. | 6500 | Internal | Sushil Singh/MR. V. Singh
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | OFF Season | 2025-09-20 |  |  | Controlller internal communication card not support.field process value not show graphic | Controller replace with new. Program restored in new controller.now ok | 192727 | Internal/online support | Sushil Singh/MR. V. Singh
9c6075df4678 | conntroller - :: ZIL/GSM/SEDL | ZIL/GSM/SEDL | OFF Season | 2026-04-11 |  |  | Controller & module found healthy. | Proper checking, cleaning & safely shutdown work are completed. |  | Internal | Sushil Singh/MR. V. Singh
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | OFF Season | 2023-05-21 |  |  | Controller & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Mr. Gaurav/MR. V. Singh
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | OFF Season | 2024-04-22 |  |  | Controller & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | OFF Season | 2024-09-05 |  |  | Controller & module found healthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | OFF Season | 2024-09-26 |  |  | All euipment found helthy. | Check all motor & control valve command found ok. |  | Internal | Sushil Singh/MR. V. Singh
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | OFF Season | 2025-04-03 |  |  | Controller & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | OFF Season | 2025-07-29 |  |  | All euipment found helthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | OFF Season | 2025-08-02 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
45f06d18b66d | conntroller - :: ZIL/GSM/MCS/PANEL | ZIL/GSM/MCS/PANEL | OFF Season | 2026-04-13 |  |  | Controller & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | OFF Season | 2023-05-19 |  |  | Controller & All module found healthy. | Proper checking, cleaning & connection tightness checking work are completed. |  | Internal | Mr. Gaurav/MR. V. Singh
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | OFF Season | 2024-04-22 |  |  | Controoler & all module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed.only CPU MCB on & other MCB off. |  | Internal | Sushil Singh/MR. V. Singh
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | OFF Season | 2024-08-28 |  |  | ALL channel loop found healthy. | Proper checking, cleaning & Panel TB module connection tightness checking & loop test work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | OFF Season | 2024-09-30 |  |  | Controller & All module found healthy. | Proper checking, cleaning & fuse insert TB work are completed. Taken line |  | Internal | Sushil Singh/MR. V. Singh
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | OFF Season | 2025-04-03 |  |  | Controller & All module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | OFF Season | 2025-07-30 |  |  | All euipment found helthy. | Proper checking, cleaning & marshaling TB module connection tightness checking work are completed. |  | Internal | Sushil Singh/MR. V. Singh
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | OFF Season | 2025-08-23 |  |  | All loop found ok. | JB to Marshaling TB Loop checking work are completed |  | Internal | Sushil Singh/MR. V. Singh
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | Season | 2025-11-07 |  |  | Faulty RAM (memory issue) & PLC hangd. | B & C Continuouse Pan operator system & PLC Restart. System healthy & comununicate with PLC Found OK.with the help of Online support. |  | Internal | Sushil Singh/Mr.Service engineer
8eb79ccf6d67 | conntroller - :: ZIL/GSM/B&C Conti. | ZIL/GSM/B&C Conti. | OFF Season | 2026-04-07 |  |  | Controller & module found healthy. | Proper checking, cleaning & marshaling TB fuse open work are completed. |  | Internal | Sushil Singh/MR. V. Singh
ebc2e4d34893 | conntroller - :: ZIL/SUG/PLC-1 | ZIL/SUG/PLC-1 | Season | 2025-12-15 |  |  | New Equipment | New decanter panel commissioning work |  | External | Mr. Anirudh Verma/Mr. V. Singh
9c35534a604f | conntroller - :: ZIL/SUG/PLC-2 | ZIL/SUG/PLC-2 | Season | 2025-12-15 |  |  | New Equipment | New decanter panel commissioning work |  | External | Mr. Anirudh Verma/Mr. V. Singh
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | OFF-SEASON | 2024-04-18 |  |  | Server,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | OFF-SEASON | 2024-09-21 |  |  | Server,Monitor,Mouse ,Keyboard found ok. | Server Up-gration work | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
d08de2e083c9 | Work stations :: ZIL/GSM/Server-1 | ZIL/GSM/Server-1 | OFF-SEASON | 2025-04-05 |  |  | Server,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | OFF-SEASON | 2024-04-18 |  |  | Server,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | OFF-SEASON | 2024-09-21 |  |  | Server,Monitor,Mouse ,Keyboard found ok. | Server Up-gration work | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
270cd60ab099 | Work stations :: ZIL/GSM/Server-2 | ZIL/GSM/Server-2 | OFF-SEASON | 2025-04-05 |  |  | Server,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | OFF-SEASON | 2024-09-21 |  |  | Server,Monitor,Mouse ,Keyboard found ok. | New historien server installation work | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
d599279ca67b | Work stations :: ZIL/GSM/Server-3 | ZIL/GSM/Server-3 | OFF-SEASON | 2025-04-05 |  |  | Server,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | OFF-SEASON | 2024-04-20 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | OFF-SEASON | 2024-09-21 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Engineering system Up-gration work | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | OFF-SEASON | 2025-04-06 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
2de1d33c5501 | Work stations :: ZIL/GSM/ENGG.ES-1 | ZIL/GSM/ENGG.ES-1 | OFF-SEASON | 2026-04-13 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OFF-SEASON | 2024-04-18 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OFF-SEASON | 2024-09-21 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Engineering system Up-gration work | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OFF-SEASON | 2025-04-06 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
05e40c302e77 | Work stations :: ZIL/GSM/OS-1 | ZIL/GSM/OS-1 | OFF-SEASON | 2026-04-06 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OFF-SEASON | 2024-04-23 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OFF-SEASON | 2024-09-21 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Operator system Up-gration work | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OFF-SEASON | 2025-04-06 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
7b248c5b7f01 | Work stations :: ZIL/GSM/OS-2 | ZIL/GSM/OS-2 | OFF-SEASON | 2026-04-06 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OFF-SEASON | 2024-04-23 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OFF-SEASON | 2024-09-21 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Operator system Up-gration work | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OFF-SEASON | 2025-04-02 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
b16171a22e95 | Work stations :: ZIL/GSM/OS-3 | ZIL/GSM/OS-3 | OFF-SEASON | 2026-04-10 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OFF-SEASON | 2024-04-22 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OFF-SEASON | 2024-09-21 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Operator system Up-gration work | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OFF-SEASON | 2025-04-02 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
84bd3c7347c4 | Work stations :: ZIL/GSM/OS-4 | ZIL/GSM/OS-4 | OFF-SEASON | 2026-04-10 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OFF-SEASON | 2024-04-18 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OFF-SEASON | 2024-09-21 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Operator system Up-gration work | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OFF-SEASON | 2025-04-02 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
c8fbaa610800 | Work stations :: ZIL/GSM/OS-5 | ZIL/GSM/OS-5 | OFF-SEASON | 2026-04-10 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OFF-SEASON | 2024-04-20 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OFF-SEASON | 2024-09-21 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Operator system Up-gration work | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OFF-SEASON | 2025-03-30 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.system kept in mill dcs control room & start OS |  | Internal | Sushil Singh/MR. V. Singh
86c66511a674 | Work stations :: ZIL/GSM/OS-6 | ZIL/GSM/OS-6 | OFF-SEASON | 2026-04-07 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OFF-SEASON | 2024-04-20 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OFF-SEASON | 2024-09-21 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Operator system Up-gration work | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OFF-SEASON | 2025-03-30 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.system kept in mill dcs control room & start OS |  | Internal | Sushil Singh/MR. V. Singh
3d21a2eb194e | Work stations :: ZIL/GSM/OS-7 | ZIL/GSM/OS-7 | OFF-SEASON | 2026-04-07 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OFF-SEASON | 2024-04-24 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OFF-SEASON | 2024-09-21 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Operator system Up-gration work | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OFF-SEASON | 2025-04-07 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.system kept in mill dcs control room & start OS |  | Internal | Sushil Singh/MR. V. Singh
b1930c60688e | Work stations :: ZIL/GSM/OS-8 | ZIL/GSM/OS-8 | OFF-SEASON | 2026-04-13 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OFF-SEASON | 2024-09-21 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | New operator system use as spare | Up-gradation pakage 1.2 cr. | External | Sushil Singh/MR. V. Singh
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OFF-SEASON | 2025-04-07 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.system kept in mill dcs control room & start OS |  | Internal | Sushil Singh/MR. V. Singh
d12cd381cec6 | Work stations :: ZIL/GSM/SPARE | ZIL/GSM/SPARE | OFF-SEASON | 2026-04-13 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | OFF-SEASON | 2024-04-22 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | OFF-SEASON | 2024-09-27 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.Installed at own place. | 0 | Internal | Sushil Singh/MR. V. Singh
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | OFF-SEASON | 2025-03-07 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.system kept in mill dcs control room & start OS |  | Internal | Sushil Singh/MR. V. Singh
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | OFF-SEASON | 2025-04-01 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.system kept in Raw dcs control room |  | Internal | Sushil Singh/MR. V. Singh
237799de980f | Work stations :: ZIL/GSM/OS-B&C | ZIL/GSM/OS-B&C | OFF-SEASON | 2026-04-07 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | OFF-SEASON | 2024-04-22 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.kept in dcs room | 0 | Internal | Sushil Singh/MR. V. Singh
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | OFF-SEASON | 2024-09-26 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.Installed at own place. | 0 | Internal | Sushil Singh/MR. V. Singh
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | OFF-SEASON | 2025-04-01 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.system kept in Raw dcs control room |  | Internal | Sushil Singh/MR. V. Singh
d874f39f176a | Work stations :: ZIL/GSM/CLIENT-1 | ZIL/GSM/CLIENT-1 | OFF-SEASON | 2026-04-11 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | OFF-SEASON | 2024-04-22 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.kept in dcs room | 0 | Internal | Sushil Singh/MR. V. Singh
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | OFF-SEASON | 2024-09-26 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.Installed at own place. | 0 | Internal | Sushil Singh/MR. V. Singh
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | OFF-SEASON | 2025-04-07 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.system kept in Raw dcs control room |  | Internal | Sushil Singh/MR. V. Singh
3293ed79696b | Work stations :: ZIL/GSM/CLIENT-2 | ZIL/GSM/CLIENT-2 | OFF-SEASON | 2026-04-11 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OFF-SEASON | 2024-04-23 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OFF-SEASON | 2024-08-06 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.Installed at postion. | 0 | Internal | Sushil Singh/MR. V. Singh
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OFF-SEASON | 2025-04-07 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed.system kept in Raw dcs control room |  | Internal | Sushil Singh/MR. V. Singh
ad1b56012e2b | Work stations :: ZIL/GSM/OS-SEDL | ZIL/GSM/OS-SEDL | OFF-SEASON | 2026-04-11 |  |  | CPU,Monitor,Mouse ,Keyboard found ok. | Proper checking, cleaning & sytem healthyness checking work are completed. | 0 | Internal | Sushil Singh/MR. V. Singh
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | SEASON | 2023-11-23 |  |  | Fire alarm solution (GST Make) equipment’s panel are not worked. | Fire alarm solution (GST Make) equipment’s installation with testing work is completed.All MCP and loop SDR working are OK | 52152 | External | Sushil Singh/MR. V. Singh
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | SEASON | 2024-01-10 |  |  | All equipment found healthy & runing condition | fire alarm equipment’s testing work are completed.All MCP and loop SDR working are OK. | 0 | Internal | Sushil Singh/MR. V. Singh
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | SEASON | 2024-02-07 |  |  | All equipment found healthy & runing condition | fire alarm equipment’s testing work are completed.All MCP and loop SDR working are OK. | 0 | Internal | Sushil Singh/MR. V. Singh
8938859f7f9d | Fire control panel :: ZIL/GSM/FA-01 | ZIL/GSM/FA-01 | OFF-SEASON | 2025-07-17 |  |  | All equipment found healthy & runing condition | Panel cleaning work is completed | 0 | Internal | Sushil Singh/MR. V. Singh
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | SEASON | 2023-11-23 |  |  | All equipment found healthy & runing condition | fire alarm equipment’s testing work are completed.All MCP and loop SDR working are OK. | 0 | Internal | Sushil Singh/MR. V. Singh
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | SEASON | 2024-01-10 |  |  | All equipment found healthy & runing condition | fire alarm equipment’s testing work are completed.All MCP and loop SDR working are OK. | 0 | Internal | Sushil Singh/MR. V. Singh
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | SEASON | 2024-02-07 |  |  | All equipment found healthy & runing condition | fire alarm equipment’s testing work are completed.All MCP and loop SDR working are OK. | 0 | Internal | Sushil Singh/MR. V. Singh
76748315eff8 | Fire control panel :: ZIL/GSM/FA-02 | ZIL/GSM/FA-02 | OFF-SEASON | 2025-07-23 |  |  | All equipment found healthy & runing condition | Panel cleaning work is completed | 0 | Internal | Sushil Singh/MR. V. Singh
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | SEASON | 2024-02-26 |  |  | MCC1 nos-01 smoke detector & nos-02 SDR & MCC2 nos-01 found warnout. | Fire alarm solution (GST Make) equipment’s installation with testing work is completed.All MCP and loop SDR working are OK | 52152 | External | Sushil Singh/MR. V. Singh
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | OFF-SEASON | 2025-07-26 |  |  | All equipment found healthy. | Panel cleaning work is completed | 0 | Internal | Sushil Singh/MR. V. Singh
cc7fd480dc3e | Fire control panel :: ZIL/GSM/FA-03 | ZIL/GSM/FA-03 | SEASON | 2025-11-15 |  |  | MCC1 cable celler nos-02 smoke detector & nos-01 transformer room found warn-out | Panel cleaning work is completed | 7500 | External | Sushil Singh/MR. V. Singh
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | OFF Season | 25.05.2022 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing & painting work done. |  | Internal | A Varma / V singh
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | OFF Season | 05.08.2023 |  |  | Control valve found C light scaling and rusty.Electrode o-ring,seat damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode o ring,seat replaced with new | 250 | Internal | A Varma / V singh
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | OFF Season | 05.08.2024 |  |  | Control valve found C light scaling and rusty.Electrode cylinder seal kit damage. | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work done.electrode cylinder seal kit replaced with new | 685 | Internal | A Varma / V singh
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | OFF Season | 05.06.2025 |  |  | Control valve found C light scaling and rustry | Actuator,body,positioner,valve seat checking,AFR cleaning repairing work are. | 250 | Internal | A Varma / V singh
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | OFF Season | 11.09.2025 |  |  | Brick transmitter with electrode replaced with new | Spare Sensor absulit in market | 81500 | External | A Varma / V singh
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | OFF Season | 22.04.2026 |  |  | Control valve found C light scaling and rusty. | Actuator,body,positioner,valve seat checking,AFR ,Electrode cleaning repairing work done. | 250 | Internal | Anuj kr./ V singh
70ee7410612a | B COUNTI.PAN 27-65 :: ZIL/SUG./B.COMP-CT-05 | ZIL/SUG./B.COMP-CT-05 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | OFF Season | 2023-06-10 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | OFF Season | 2024-08-28 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | OFF Season | 2025-06-21 |  |  | Flow tube found Scale full . | Clean its Liner & Sensor. | 100 | Internal | Mr. Anirudh Varma
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 4
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 5
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 6
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | 7
3370e96b2811 | FLOW METER :: ZIL/SUG./01/16.FT.075.B01 | ZIL/SUG./01/16.FT.075.B01 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | OFF Season | 2022-08-07 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | OFF Season | 2023-07-18 |  |  | Control valve found scaled and rusty. | Proper cleaning & painting work done. |  | Internal | Mr Anuj / Mr V.Singh
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | OFF Season | 2024-05-14 |  |  | Control valve found scaled and rusty. | Proper cleaning & overhauling work done. | 150 | Internal | Mr Anuj / Mr V.Singh
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | OFF Season | 2025-06-20 |  |  | Control valve found scaled and rusty. | Proper cleaning & Overhauling work done. | 250 | Internal | Mr Anuj / Mr V.Singh
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | OFF Season | 2026-04-23 |  |  | Control valve found scaled and rusty. | Valve dismentling cleaning & overhauling with checking work done. | 250 | Internal | Mr A. Varma / Mr V.Singh
969d52681150 | VRL 24-53 :: ZIL/SUG./001/SY_B_MOL_CV2 | ZIL/SUG./001/SY_B_MOL_CV2 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | OFF Season | 2022-06-24 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | OFF Season | 2023-07-21 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | OFF Season | 2024-07-22 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | OFF Season | 2025-07-18 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 150 | Internal | Mr Anuj / Mr V.Singh
09d54898090a | DS Flow Meter-31 :: ZIL/SUG./01/Vacuum-FM-01 | ZIL/SUG./01/Vacuum-FM-01 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | OFF Season | 2022-06-28 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | OFF Season | 2022-07-25 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | OFF Season | 2024-08-29 |  |  | OK | Transmitter & flow tube cleaning work, electronic card physical checking work is completed. | 100 | Internal | Mr Anuj / Mr V.Singh
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | OFF Season
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | OFF Season
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | OFF Season
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | OFF Season
910c1c18dcc0 | DS Flow Meter-31 :: ZIL/SUG./01/DIST.-TWFM-2 | ZIL/SUG./01/DIST.-TWFM-2 | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | OFF Season
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | OFF Season
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | OFF Season
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | OFF Season
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | OFF Season
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | OFF Season
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | OFF Season
7b6e4014649d | DS Flow Meter-31 :: ZIL/SUG./01/ETP-DECANTER-FM | ZIL/SUG./01/ETP-DECANTER-FM | Technician |  |  |  | Sec .Engineer |  |  |  | HOD
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | OFF Season | 2022-05-06 |  |  | Control valve Body found rusty and valve seat worn-out.AFR & Positioner Gauge found Damage. | Proper cleaning, Painting , valve seat & gauge replace with new. |  |  | Mr. Ritesh / Mr. V singh
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | OFF Season | 2023-06-13 |  |  | Control valve Seat & body found rusty. AFR & Dome Switch found healty. | Proper cleaning, Painting & Lubrication work done. |  |  | Mr. Gaurav / Mr. V singh
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | OFF Season | 2024-05-06 |  |  | Control valve Seat & body found rusty. AFR Filter & Gauge found ok. | Proper cleaning, & Lubrication work done. Dome Switch checking work done. | 100 | Internal | Mr. Gaurav / Mr. V singh
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | OFF Season | 2025-05-05 |  |  | Control valve Seat & body found rusty. Actuator surface worn-out with O ring set damage. | Proper cleaning, overhauling ,checking Painting & Lubrication work done.Damage part change with new. | 1600 | Internal | Mr. Anuj Kr / Mr. V singh
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | OFF Season | 2026-04-23 |  |  | Control valve Seat & body found rusty. | Actuator ,Gear ,Valve seat Proper cleaning Overhauling ,Painting & Lubrication work with checking workdone. | 250 | Internal | Mr. Anuj kr / Mr. V singh
e71a9add8164 | D.B.F 14 :: ZIL/SUG./001 (40FCV201) | ZIL/SUG./001 (40FCV201) | Technician |  |  |  | Sec .Engineer |  |  |  | HOD