## INDEX
Sugar Plant DS House Electrical Equipments-VFD PANEL
Sr.No. | Plant | Section | Location | Main Equipment | Sub Equipment | Department | History card Tag Nos. | History card Location
1 | SUGAR | DS HOUSE | DS House | DS VACUUM filter 14'x36' | DS VACUUM filter 14'x36' VFD PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/VFD/14'x36' | SUGAR PLANT DS HOUSE MCC ROOM-2nd
2 | SUGAR | DS HOUSE | DS House | DS VACUUM filter 14'x30' | DS VACUUM filter 14'x30' VFD PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/VFD/14'x30' | SUGAR PLANT DS HOUSE MCC ROOM-2nd
3 | SUGAR | DS HOUSE | DS House | Distillery Syrup weightment | DS Distillery Syrup weightment Pump no.1 VFD PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1 | SUGAR PLANT DS HOUSE MCC ROOM-2nd
4 | SUGAR | DS HOUSE | DS House | Distillery Syrup weightment | DS Distillery Syrup weightment Pump no.2 VFD PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2 | SUGAR PLANT DS HOUSE MCC ROOM-2nd
5 | SUGAR | DS HOUSE | DS House | DS Molten Sulphur Dosing | DS Molten Sulphur Dosing pump(E) VFD PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E) | SUGAR PLANT DS HOUSE
6 | SUGAR | DS HOUSE | DS House | DS Molten Sulphur Dosing | DS Molten Sulphur Dosing pump(W) VFD PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W) | SUGAR PLANT DS HOUSE
7 | SUGAR | DS HOUSE | DS House | DS AIR BLOWER | DS AIR BLOWER NO.3 VFD PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER | SUGAR PLANT DS HOUSE MCC ROOM-1st
8 | SUGAR | DS HOUSE | DS House | DS CLEAR JUICE PUMP | DS CLEAR JUICE PUMP-1 VFD PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1 | SUGAR PLANT DS HOUSE MCC ROOM-1st
9 | SUGAR | DS HOUSE | DS House | DS INJECTION PUMP | DS INJECTION PUMP NO.5 VFD PANEL | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5 | SUGAR PLANT DS HOUSE MCC ROOM-1st
10 | SUGAR | DS HOUSE | DS House | DS 1750 WIL MACHINE-1 | DS 1750 WIL AC VFD PANEL-1 | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1 | SUGAR PLANT DS HOUSE C/F M/C BATCH TYPE 1750
11 | SUGAR | DS HOUSE | DS House | DS 1750 NHEC MACHINE-2 | DS 1750 NHEC(DC) VFD PANEL-2 | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2 | SUGAR PLANT DS HOUSE C/F M/C BATCH TYPE 1750
12 | SUGAR | DS HOUSE | DS House | DS 1750 WIL MACHINE-3 | DS 1750 WIL AC VFD PANEL-3 | ELECTRICAL | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3 | SUGAR PLANT DS HOUSE C/F M/C BATCH TYPE 1750

## VACUUM FILTER 14'x36'
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS VACUUM filter 14'x36' VFD PANEL
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE MCC ROOM-2nd
EQUIPMENT NO : | [5 empty] | ZIL/GSM/SP/ELECT/DS/VFD/14'x36'
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | VFD Sr. No.
VFD Rating |  |  | 12A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V
Model |  |  | ACS550-01-12A-4
Feeder No.
VFD Feeder Name |  |  | OC filter 14'x36' VFD PANEL
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | DS VACUUM filter 14'x36' VFD PANEL | VFD feeder physicaly status. |  | X | X | X | X | √ | X
VFD feeder cleaning by blower.
|  | VFD and by pass control scheme checked. |  |  | X
|  | Control & power connection tightness. |  |  | X
|  | Feeder Incoming & out going bus bar tightness. |  |  | X
|  | Feeder charging status after maintenance. |  |  | X
|  | Feeder On, Off and trip indication checked. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL

## VACUUM FILTER 14'x30
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS VACUUM filter 14'x30' VFD PANEL
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE MCC ROOM-2nd
EQUIPMENT NO : | [5 empty] | ZIL/GSM/SP/ELECT/DS/VFD/14'x30'
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | VFD Sr. No.
VFD Rating |  |  | 15A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V
Model |  |  | ACS550-01-15A-4
Feeder No.
VFD Feeder Name |  |  | OC filter 14'x30' VFD PANEL
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | DS VACUUM filter 14'x30' VFD PANEL | VFD feeder physicaly status. |  | X | X | X | X | √ | X
VFD feeder cleaning by blower.
|  | VFD and by pass control scheme checked. |  |  | X
|  | Control & power connection tightness. |  |  | X
|  | Feeder Incoming & out going bus bar tightness. |  |  | X
|  | Feeder charging status after maintenance. |  |  | X
|  | Feeder On, Off and trip indication checked. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL

## Distillery W S Pump-1
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS Distillery Syrup weightment Pump no.1 VFD PANEL
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE MCC ROOM-2nd
EQUIPMENT NO : | [5 empty] | ZIL/GSM/SP/ELECT/DS/VFD/DSW-1
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | VFD Sr. No.
VFD Rating |  |  | 87A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V
Model |  |  | ACS880-01-087A-3+0J400+P944
Feeder No.
VFD Feeder Name |  |  | Distillery Syrup weightment Pump no.1 VFD
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | DS Distillery Syrup weightment Pump no.1 VFD PANEL | VFD feeder physicaly status. |  | X | X | X | X | √ | X
VFD feeder cleaning by blower.
|  | VFD and by pass control scheme checked. |  |  | X
|  | Control & power connection tightness. |  |  | X
|  | Feeder Incoming & out going bus bar tightness. |  |  | X
|  | Feeder charging status after maintenance. |  |  | X
|  | Feeder On, Off and trip indication checked. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL

## Distillery W S Pump-2
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS Distillery Syrup weightment Pump no.2 VFD PANEL
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE MCC ROOM-2nd
EQUIPMENT NO : | [5 empty] | ZIL/GSM/SP/ELECT/DS/VFD/DSW-2
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | VFD Sr. No.
VFD Rating |  |  | 87A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V
Model |  |  | ACS880-01-087A-3+0J400+P944
Feeder No.
VFD Feeder Name |  |  | Distillery Syrup weightment Pump no.2 VFD
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | DS Distillery Syrup weightment Pump no.2 VFD PANEL | VFD feeder physicaly status. |  | X | X | X | X | √ | X
VFD feeder cleaning by blower.
|  | VFD and by pass control scheme checked. |  |  | X
|  | Control & power connection tightness. |  |  | X
|  | Feeder Incoming & out going bus bar tightness. |  |  | X
|  | Feeder charging status after maintenance. |  |  | X
|  | Feeder On, Off and trip indication checked. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL

## MOLTEN SULPHUR DOSING PUMP(E)
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS Molten Sulphur Dosing pump(E) VFD PANEL
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE
EQUIPMENT NO : | [5 empty] | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(E)
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | VFD Sr. No.
VFD Rating |  |  | 6A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V
Model |  |  | ACS550-01-06A9-4
Feeder No.
VFD Feeder Name |  |  | Molten Sulphur Dosing pump(E) VFD PANEL
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | DS Molten Sulphur Dosing pump(E) VFD PANEL | VFD feeder physicaly status. |  | X | X | X | X | √ | X
VFD feeder cleaning by blower.
|  | VFD and by pass control scheme checked. |  |  | X
|  | Control & power connection tightness. |  |  | X
|  | Feeder Incoming & out going bus bar tightness. |  |  | X
|  | Feeder charging status after maintenance. |  |  | X
|  | Feeder On, Off and trip indication checked. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Season |  | 2025-26 | Control card out of order. |  | Other old VFD installed(Raw spare VFD). |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL/AKASH
Off Season |  | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL

## MOLTEN SULPHUR DOSING PUMP(W)
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS Molten Sulphur Dosing pump(W) VFD PANEL
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE
EQUIPMENT NO : | [5 empty] | ZIL/GSM/SP/ELECT/DS/VFD/MS DOSING(W)
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | VFD Sr. No.
VFD Rating |  |  | 6A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V
Model |  |  | ACS550-01-06A9-4
Feeder No.
VFD Feeder Name |  |  | Molten Sulphur Dosing pump(W) VFD PANEL
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | Molten Sulphur Dosing pump(W) VFD PANEL | VFD feeder physicaly status. |  | X | X | X | X | √ | X
VFD feeder cleaning by blower.
|  | VFD and by pass control scheme checked. |  |  | X
|  | Control & power connection tightness. |  |  | X
|  | Feeder Incoming & out going bus bar tightness. |  |  | X
|  | Feeder charging status after maintenance. |  |  | X
|  | Feeder On, Off and trip indication checked. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL

## AIR BLOWER NO.3
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS AIR BLOWER NO.3 VFD PANEL
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE MCC ROOM-1st
EQUIPMENT NO : | [5 empty] | ZIL/GSM/SP/ELECT/DS/VFD/AIR BLOWER
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | VFD Sr. No.
VFD Rating |  |  | 59A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V
Model |  |  | ACS550-01-059A-4
Feeder No.
VFD Feeder Name |  |  | AIR BLOWER NO.3 VFD PANEL
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | DS AIR BLOWER NO.3 VFD PANEL | VFD feeder physicaly status. |  | X | X | X | X | √ | X
VFD feeder cleaning by blower.
|  | VFD and by pass control scheme checked. |  |  | X
|  | Control & power connection tightness. |  |  | X
|  | Feeder Incoming & out going bus bar tightness. |  |  | X
|  | Feeder charging status after maintenance. |  |  | X
|  | Feeder On, Off and trip indication checked. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2034 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2026 |  |  |  |  | NO | NO | Akhilesh Chaudhari/charanjit

## CLEAR JUICE PUMP-1
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS CLEAR JUICE PUMP-1 VFD PANEL
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE MCC ROOM-1st
EQUIPMENT NO : | [5 empty] | ZIL/GSM/SP/ELECT/DS/VFD/CJ-1
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | VFD Sr. No.
VFD Rating |  |  | 430A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V
Model |  |  | ACS580-01-430A-4
Feeder No.
VFD Feeder Name |  |  | CLEAR JUICE PUMP-1 VFD PANEL
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | DS CLEAR JUICE PUMP-1 VFD PANEL | VFD feeder physicaly status. |  | X | X | X | X | √ | X
VFD feeder cleaning by blower.
|  | VFD and by pass control scheme checked. |  |  | X
|  | Control & power connection tightness. |  |  | X
|  | Feeder Incoming & out going bus bar tightness. |  |  | X
|  | Feeder charging status after maintenance. |  |  | X
|  | Feeder On, Off and trip indication checked. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2034 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL

## Injection Pump No.5
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS INJECTION PUMP NO.5 VFD PANEL
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE MCC ROOM-1st
EQUIPMENT NO : | [5 empty] | ZIL/GSM/SP/ELECT/DS/VFD/INJ-5
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | VFD Sr. No.
VFD Rating |  |  | 505A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V
Model |  |  | ACS580-04-505A-4+E208+E210+J400+J410
Feeder No.
VFD Feeder Name |  |  | INJECTION PUMP NO.5 VFD PANEL
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | DS INJECTION PUMP NO.5 VFD PANEL | VFD feeder physicaly status. |  | X | X | X | X | √ | X
VFD feeder cleaning by blower.
|  | VFD and by pass control scheme checked. |  |  | X
|  | Control & power connection tightness. |  |  | X
|  | Feeder Incoming & out going bus bar tightness. |  |  | X
|  | Feeder charging status after maintenance. |  |  | X
|  | Feeder On, Off and trip indication checked. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2034 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL
Off Season |  | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL

## DS 1750 WIL AC-1
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS 1750 WIL AC VFD PANEL-1
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE C/F M/C BATCH TYPE 1750
EQUIPMENT NO : | [5 empty] | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-1
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | VFD Panel Code
VFD Rating |  |  | 470A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V
Module-1 choke unit | [5 empty] | Code No.
Module-2 Line Converter unit |  |  | ACS880-104-0470A-3+C188+E205 |  |  | Code No. / SN.
Module-3 Inverter unit |  |  | ACS880-104-0640A-3+E205+P904+V112 |  |  | Code No. / SN.
Feeder No.
VFD Feeder Name |  |  | DS 1750 WIL AC VFD PANEL-1
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | DS 1750 WIL AC VFD PANEL-1 | VFD feeder physicaly status. |  | X | X | X | X | √ | X
|  | VFD feeder cleaning by blower. |  |  | X
|  | VFD and by pass control scheme checked. |  |  | X
|  | Control & power connection tightness. |  |  | X
|  | Feeder Incoming & out going bus bar tightness. |  |  | X
|  | Feeder charging status after maintenance. |  |  | X
|  | Feeder On, Off and trip indication checked. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /VIKASH
Off Season |  | 2024 | Drive tripped at fault-short ckt-2340,two phase IGBT & BGDR card faulty(During Trial). |  | Replaced with new ISU module. |  | NO | NO | VIJAY KR CHAUDHARY /VIKASH
Off Season |  | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /VIKASH
Off Season |  | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL/AKASH

## DS 1750 NHEC DC-2
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS 1750 NHEC(DC) VFD PANEL-2
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE C/F M/C BATCH TYPE 1750
EQUIPMENT NO : | [5 empty] | ZIL/GSM/SP/ELECT/DS/VFD/DC-1750-2
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | VFD Sr. No.
VFD Rating |  |  | 400A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V
Model |  |  | DCS800
Feeder No.
VFD Feeder Name |  |  | DS 1750 NHEC(DC) VFD PANEL-2
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | DS 1750 NHEC(DC) VFD PANEL-2 | VFD feeder physicaly status. |  | X | X | X | X | √ | X
VFD feeder cleaning by blower.
|  | VFD and by pass control scheme checked. |  |  | X
|  | Control & power connection tightness. |  |  | X
|  | Feeder Incoming & out going bus bar tightness. |  |  | X
|  | Feeder charging status after maintenance. |  |  | X
|  | Feeder On, Off and trip indication checked. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2023 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /VIKASH
Off Season |  | 2024 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /VIKASH
Off Season |  | 2025 | PLC out of order(During trial). |  | PLC ageing and DC drive control panel absoluted in market hence retrofitting of existing DC drive control panel into ABB Make with HMI,PLC and new control wiring. |  | NO | NO | VIJAY KR CHAUDHARY /VIKASH
Season |  | 2025-26 | Thyristor out of order. |  | Fault 502 Armature over current, so replaced with new and started. |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL/AKASH
Off Season |  | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL/AKASH

## DS 1750 WIL AC-3
EQUIPMENT LIFE HISTORY CARD
NAME OF EQUIPMENT : | [5 empty] | DS 1750 WIL AC VFD PANEL-3
LOCATION : | [5 empty] | SUGAR PLANT DS HOUSE C/F M/C BATCH TYPE 1750
EQUIPMENT NO : | [5 empty] | ZIL/GSM/SP/ELECT/DS/VFD/1750 AC-3
DATE OF COMMISSIONING :
EQUIPMENT SPECIFICATION
Make |  |  | ABB |  |  | VFD Panel Code
VFD Rating |  |  | 470A |  |  | Year of Manufacture
Rated Voltage |  |  | 415 ±10%V
Module-1 choke unit |  |  | BLCL-13-5+C183+C188+V112+V991 |  |  | Code No.
Module-2 Line Converter unit |  |  | ACS880-104-0470A-3+E205+V112 |  |  | Code No. / SN.
Module-3 Inverter unit |  |  | ACS880-104-0470A-3+E205+V112 |  |  | Code No. / SN.
Feeder No.
VFD Feeder Name |  |  | DS 1750 WIL AC VFD PANEL-3
GSM MAINTENANCE SCHEDULE
Sr.No. | Name of Equipment | Maintenance / Inspection Activities |  | Interval | [5 empty] | Remarks
|  |  |  | Weekly | Monthly | Quarterly | Half - Yearly | Yearly | 2 - Years
1 | DS 1750 WIL AC VFD PANEL-3 | VFD feeder physicaly status. |  | X | X | X | X | √ | X
|  | VFD feeder cleaning by blower. |  |  | X
|  | VFD and by pass control scheme checked. |  |  | X
|  | Control & power connection tightness. |  |  | X
|  | Feeder Incoming & out going bus bar tightness. |  |  | X
|  | Feeder charging status after maintenance. |  |  | X
|  | Feeder On, Off and trip indication checked. |  |  | X
EQUIPMENT MAINTENANCE HISTORY
Season / OFF Season |  | Year | Outage/ Observation |  | Action Taken |  | Repair Cost (Rs.) | Services (Internal / External) | Responsibility ( Engineer/ Supervision) | Remarks
Off Season |  | 2025 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /Vikash | New 1750 M/C installed - 2025
Off Season |  | 2026 |  |  |  |  | NO | NO | VIJAY KR CHAUDHARY /ABHAYLAL/AKASH